## Read me
Sustained Interruption Events, January 2025 - August 2026
Sedgewater Energy Holdings
Effective date | 2026-09-09
Purpose | Provide event-level sustained interruptions with 25.52 fields for 2025 and 2026 to date.
Coverage | See each dataset dictionary and summary. Missing numeric values are excluded, not zero.
Summary interpretation | Descriptive statistics of selected records only. Totals of percentages and adjustment values are not operating KPIs.
Introduction | Workbook of sustained interruption events from January 2025 to August 2026, extracted from the outage management system on September 9, 2026 by Reliability Engineering. Each row is one sustained interruption at transformer-fuse level or above.
Sheets | Data 1 - 2025 events (January to December).
Sheets | Data 2 - 2026 events (January to August).
Sheets | Summary - formula totals of each numeric column; totals include every class, including major events.
Classification | Every event is classified as forced, planned, outside cause or major event. Planned interruptions have at least 24 hours' notice; outside-cause interruptions start on the transmission grid or at a customer facility; momentary interruptions of five minutes or less are not in the extract. Headline indices under the Reliability Metric Definitions and Calculation Standard use forced events only and the average of monthly delivery points.
Classification | Records carry type, cause, date and start hour, duration, customers interrupted and feeder identifiers, as the interruption record rule requires.
Headline results | 2025, excluding major events: SAIDI 118.0 minutes, SAIFI 1.210, CAIDI 97.5 minutes from 4,560 forced interruptions. January to August 2026: SAIDI 84.0 minutes and SAIFI 0.830, against 83.3 minutes and 0.850 for January to August 2025.
Major events | June 11-13, 2025: 355 interruptions, 104,000 customers, 126.4 million customer minutes. May 19-22, 2026: 463 interruptions, 132,152 customers, 116.6 million customer minutes. Both met the major-event test and are flagged in the major event column.
Causes | In 2025, vegetation caused 26% of forced customer minutes, overhead equipment 22%, underground equipment 16%, lightning 10%, animals 10%, wind 9%, vehicles or public 4% and unknown 3%.
Data notes | Cause is coded Unknown for about 4% of events; crews are asked to update it when the repair is closed. Customer minutes equal customers interrupted multiplied by duration for every row.

## Summary
Dataset | Measure | Unit | Total | Mean | Records | Period start | Period end
Sustained interruption events, 2025 (Jan-Dec) | customer_minutes | customer-minutes | 211922230 | 40220.5789 | 5269 | 2025-01-01 | 2025-12-31
Sustained interruption events, 2025 (Jan-Dec) | customers_interrupted | customers | 994701 | 188.7836 | 5269 | 2025-01-01 | 2025-12-31
Sustained interruption events, 2025 (Jan-Dec) | duration_minutes | minutes | 1045435 | 198.4124 | 5269 | 2025-01-01 | 2025-12-31
Sustained interruption events, 2026 (Jan-Aug) | customer_minutes | customer-minutes | 177538997 | 46488.3469 | 3819 | 2026-01-01 | 2026-08-31
Sustained interruption events, 2026 (Jan-Aug) | customers_interrupted | customers | 743270 | 194.6242 | 3819 | 2026-01-01 | 2026-08-31
Sustained interruption events, 2026 (Jan-Aug) | duration_minutes | minutes | 820040 | 214.7264 | 3819 | 2026-01-01 | 2026-08-31

## Dictionary
Dataset | Field | Definition | Unit | Type | Reference
Sustained interruption events, 2025 (Jan-Dec) | event_id | OE-25-000001 |  | id
Sustained interruption events, 2025 (Jan-Dec) | customer_minutes | Customer minutes interrupted (derived) | customer-minutes | number
Sustained interruption events, 2025 (Jan-Dec) | customers_interrupted | Customers interrupted | customers | integer
Sustained interruption events, 2025 (Jan-Dec) | duration_minutes | Duration to restoration | minutes | integer
Sustained interruption events, 2025 (Jan-Dec) | feeder_code | Feeder (FK) |  | category
Sustained interruption events, 2025 (Jan-Dec) | district | District (copied) |  | category
Sustained interruption events, 2025 (Jan-Dec) | start_date | Start date |  | date
Sustained interruption events, 2025 (Jan-Dec) | start_hour | Start hour (local) | hour | category
Sustained interruption events, 2025 (Jan-Dec) | cause | Cause code |  | category
Sustained interruption events, 2025 (Jan-Dec) | device | Interrupting device |  | category
Sustained interruption events, 2025 (Jan-Dec) | classification | 25.52 classification |  | category
Sustained interruption events, 2025 (Jan-Dec) | major_event | Major event label |  | category
Sustained interruption events, 2026 (Jan-Aug) | event_id | OE-26-000001 |  | id
Sustained interruption events, 2026 (Jan-Aug) | customer_minutes | Customer minutes interrupted (derived) | customer-minutes | number
Sustained interruption events, 2026 (Jan-Aug) | customers_interrupted | Customers interrupted | customers | integer
Sustained interruption events, 2026 (Jan-Aug) | duration_minutes | Duration to restoration | minutes | integer
Sustained interruption events, 2026 (Jan-Aug) | feeder_code | Feeder (FK) |  | category
Sustained interruption events, 2026 (Jan-Aug) | district | District (copied) |  | category
Sustained interruption events, 2026 (Jan-Aug) | start_date | Start date |  | date
Sustained interruption events, 2026 (Jan-Aug) | start_hour | Start hour (local) | hour | category
Sustained interruption events, 2026 (Jan-Aug) | cause | Cause code |  | category
Sustained interruption events, 2026 (Jan-Aug) | device | Interrupting device |  | category
Sustained interruption events, 2026 (Jan-Aug) | classification | 25.52 classification |  | category
Sustained interruption events, 2026 (Jan-Aug) | major_event | Major event label |  | category

## Data 1
event_id | customer_minutes | customers_interrupted | duration_minutes | feeder_code | district | start_date | start_hour | cause | device | classification | major_event
OE-25-000001 | 4750 | 50 | 95 | CR-S27-02 | Crossroads | 2025-01-01 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-000002 | 2070 | 23 | 90 | BY-S11-02 | Bayou | 2025-01-01 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000003 | 1305 | 9 | 145 | BY-S03-01 | Bayou | 2025-01-01 | 8 | Animal | Transformer fuse | Forced | None
OE-25-000004 | 4104 | 36 | 114 | CR-S23-01 | Crossroads | 2025-01-01 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-000005 | 690 | 3 | 230 | BY-S05-01 | Bayou | 2025-01-01 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000006 | 2464 | 14 | 176 | BY-S16-05 | Bayou | 2025-01-02 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000007 | 4071 | 59 | 69 | BY-S21-04 | Bayou | 2025-01-02 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000008 | 19516 | 82 | 238 | BY-S13-02 | Bayou | 2025-01-02 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-25-000009 | 5712 | 56 | 102 | CR-S18-06 | Crossroads | 2025-01-02 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000010 | 1530 | 17 | 90 | CR-S31-02 | Crossroads | 2025-01-02 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000011 | 1815 | 11 | 165 | BY-S27-06 | Bayou | 2025-01-02 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000012 | 30393 | 99 | 307 | CR-S07-03 | Crossroads | 2025-01-02 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000013 | 2044 | 14 | 146 | PR-S16-05 | Prairie | 2025-01-02 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000014 | 9125 | 125 | 73 | BY-S03-03 | Bayou | 2025-01-02 | 15 | Unknown | Lateral fuse | Forced | None
OE-25-000015 | 5590 | 130 | 43 | BY-S29-03 | Bayou | 2025-01-02 | 18 | Unknown | Lateral fuse | Forced | None
OE-25-000016 | 530 | 5 | 106 | HB-S15-03 | Harbor | 2025-01-02 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-000017 | 696 | 12 | 58 | HB-S02-01 | Harbor | 2025-01-02 | 23 | Unknown | Lateral fuse | Forced | None
OE-25-000018 | 1232 | 7 | 176 | PR-S05-03 | Prairie | 2025-01-03 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000019 | 11050 | 50 | 221 | CR-S15-03 | Crossroads | 2025-01-03 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000020 | 10836 | 63 | 172 | PR-S13-03 | Prairie | 2025-01-03 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000021 | 32800 | 164 | 200 | BY-S05-02 | Bayou | 2025-01-03 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000022 | 17152 | 128 | 134 | CR-S07-05 | Crossroads | 2025-01-03 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000023 | 1495 | 13 | 115 | CR-S19-03 | Crossroads | 2025-01-03 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000024 | 13536 | 72 | 188 | PR-S14-01 | Prairie | 2025-01-03 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000025 | 1690 | 10 | 169 | HB-S14-03 | Harbor | 2025-01-03 | 18 | Animal | Transformer fuse | Forced | None
OE-25-000026 | 510 | 10 | 51 | BY-S25-05 | Bayou | 2025-01-03 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-25-000027 | 15876 | 126 | 126 | BY-S07-06 | Bayou | 2025-01-04 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000028 | 15129 | 123 | 123 | CR-S13-05 | Crossroads | 2025-01-04 | 4 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000029 | 34018 | 73 | 466 | PR-S20-01 | Prairie | 2025-01-04 | 5 | Animal | Lateral fuse | Forced | None
OE-25-000030 | 2947 | 7 | 421 | PR-S13-06 | Prairie | 2025-01-04 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000031 | 3672 | 102 | 36 | CR-S24-04 | Crossroads | 2025-01-04 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000032 | 1830 | 10 | 183 | PR-S20-02 | Prairie | 2025-01-04 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-000033 | 1673 | 7 | 239 | PR-S01-06 | Prairie | 2025-01-04 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000034 | 30628 | 403 | 76 | BY-S26-05 | Bayou | 2025-01-04 | 11 | Vehicle or public | Feeder recloser | Forced | None
OE-25-000035 | 1694 | 11 | 154 | PR-S15-02 | Prairie | 2025-01-04 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000036 | 2208 | 8 | 276 | BY-S12-03 | Bayou | 2025-01-04 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000037 | 60242 | 662 | 91 | CR-S23-05 | Crossroads | 2025-01-04 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-000038 | 7035 | 105 | 67 | CR-S08-06 | Crossroads | 2025-01-04 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000039 | 2544 | 24 | 106 | BY-S29-02 | Bayou | 2025-01-04 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000040 | 459 | 3 | 153 | BY-S19-04 | Bayou | 2025-01-05 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-25-000041 | 2150 | 10 | 215 | CR-S30-05 | Crossroads | 2025-01-05 | 7 | Animal | Transformer fuse | Forced | None
OE-25-000042 | 12054 | 49 | 246 | PR-S03-05 | Prairie | 2025-01-05 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000043 | 770 | 7 | 110 | CR-S32-04 | Crossroads | 2025-01-05 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000044 | 10164 | 66 | 154 | BY-S22-04 | Bayou | 2025-01-05 | 16 | Animal | Lateral fuse | Forced | None
OE-25-000045 | 1870 | 10 | 187 | BY-S26-03 | Bayou | 2025-01-05 | 16 | Animal | Transformer fuse | Forced | None
OE-25-000046 | 146464 | 796 | 184 | BY-S16-04 | Bayou | 2025-01-05 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-000047 | 216 | 3 | 72 | BY-S24-05 | Bayou | 2025-01-05 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000048 | 130104 | 1112 | 117 | CR-S20-02 | Crossroads | 2025-01-05 | 17 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-000049 | 23358 | 458 | 51 | BY-S18-05 | Bayou | 2025-01-05 | 18 | Weather - wind | IGSD-isolated section | Forced | None
OE-25-000050 | 1001 | 7 | 143 | HB-S03-02 | Harbor | 2025-01-05 | 19 | Animal | Transformer fuse | Forced | None
OE-25-000051 | 159941 | 3403 | 47 | HB-S09-02 | Harbor | 2025-01-05 | 22 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000052 | 54096 | 588 | 92 | CR-S01-03 | Crossroads | 2025-01-06 | 2 | Animal | Feeder recloser | Forced | None
OE-25-000053 | 2580 | 20 | 129 | CR-S28-03 | Crossroads | 2025-01-06 | 2 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000054 | 8060 | 124 | 65 | CR-S24-04 | Crossroads | 2025-01-06 | 5 | Animal | Lateral fuse | Forced | None
OE-25-000055 | 1469 | 13 | 113 | BY-S10-05 | Bayou | 2025-01-06 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-000056 | 73700 | 670 | 110 | CR-S05-06 | Crossroads | 2025-01-06 | 7 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000057 | 27264 | 142 | 192 | BY-S17-04 | Bayou | 2025-01-06 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-000058 | 355 | 5 | 71 | PR-S10-03 | Prairie | 2025-01-06 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000059 | 8712 | 121 | 72 | PR-S16-04 | Prairie | 2025-01-06 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000060 | 93786 | 957 | 98 | BY-S17-01 | Bayou | 2025-01-06 | 10 | Weather - wind | Feeder recloser | Forced | None
OE-25-000061 | 35616 | 318 | 112 | HB-S15-01 | Harbor | 2025-01-06 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-000062 | 908 | 4 | 227 | HB-S19-01 | Harbor | 2025-01-06 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-000063 | 520 | 5 | 104 | HB-S03-02 | Harbor | 2025-01-06 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000064 | 17739 | 243 | 73 | HB-S16-01 | Harbor | 2025-01-06 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000065 | 90145 | 605 | 149 | PR-S05-02 | Prairie | 2025-01-06 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000066 | 30444 | 258 | 118 | CR-S25-06 | Crossroads | 2025-01-06 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-000067 | 84245 | 581 | 145 | CR-S24-02 | Crossroads | 2025-01-06 | 22 | Animal | Feeder recloser | Forced | None
OE-25-000068 | 32718 | 861 | 38 | CR-S14-02 | Crossroads | 2025-01-07 | 8 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-000069 | 10416 | 48 | 217 | CR-S19-01 | Crossroads | 2025-01-07 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000070 | 2080 | 13 | 160 | PR-S07-04 | Prairie | 2025-01-07 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000071 | 3795 | 23 | 165 | BY-S04-01 | Bayou | 2025-01-07 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-000072 | 13414 | 38 | 353 | BY-S06-03 | Bayou | 2025-01-07 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000073 | 133 | 1 | 133 | PR-S16-05 | Prairie | 2025-01-07 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000074 | 14000 | 50 | 280 | BY-S26-02 | Bayou | 2025-01-07 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-000075 | 737 | 11 | 67 | CR-S08-02 | Crossroads | 2025-01-07 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000076 | 47952 | 333 | 144 | HB-S15-01 | Harbor | 2025-01-07 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-25-000077 | 26096 | 466 | 56 | CR-S05-03 | Crossroads | 2025-01-07 | 22 | Animal | IGSD-isolated section | Forced | None
OE-25-000078 | 10320 | 86 | 120 | CR-S16-01 | Crossroads | 2025-01-08 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000079 | 86 | 1 | 86 | BY-S23-01 | Bayou | 2025-01-08 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000080 | 7280 | 80 | 91 | HB-S16-05 | Harbor | 2025-01-08 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000081 | 1764 | 14 | 126 | CR-S23-03 | Crossroads | 2025-01-08 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000082 | 652 | 4 | 163 | BY-S16-01 | Bayou | 2025-01-08 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000083 | 23700 | 316 | 75 | BY-S20-03 | Bayou | 2025-01-08 | 8 | Animal | Feeder recloser | Forced | None
OE-25-000084 | 356 | 2 | 178 | PR-S20-01 | Prairie | 2025-01-08 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000085 | 5000 | 50 | 100 | HB-S15-02 | Harbor | 2025-01-08 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000086 | 1240 | 10 | 124 | PR-S01-04 | Prairie | 2025-01-08 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000087 | 318 | 3 | 106 | PR-S02-02 | Prairie | 2025-01-08 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000088 | 3280 | 80 | 41 | HB-S03-01 | Harbor | 2025-01-08 | 13 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000089 | 2067 | 13 | 159 | BY-S23-01 | Bayou | 2025-01-08 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-000090 | 1969 | 11 | 179 | PR-S19-02 | Prairie | 2025-01-08 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000091 | 9088 | 71 | 128 | CR-S13-05 | Crossroads | 2025-01-08 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000092 | 455 | 7 | 65 | BY-S15-02 | Bayou | 2025-01-08 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-000093 | 195220 | 860 | 227 | BY-S28-02 | Bayou | 2025-01-08 | 16 | Weather - lightning | Feeder recloser | Forced | None
OE-25-000094 | 330 | 10 | 33 | BY-S18-03 | Bayou | 2025-01-08 | 19 | Weather - wind | Transformer fuse | Forced | None
OE-25-000095 | 33495 | 145 | 231 | CR-S04-01 | Crossroads | 2025-01-09 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-000096 | 945 | 9 | 105 | HB-S08-05 | Harbor | 2025-01-09 | 0 | Animal | Transformer fuse | Forced | None
OE-25-000097 | 560 | 7 | 80 | BY-S20-02 | Bayou | 2025-01-09 | 5 | Animal | Transformer fuse | Forced | None
OE-25-000098 | 8288 | 112 | 74 | HB-S19-04 | Harbor | 2025-01-09 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000099 | 18426 | 74 | 249 | PR-S03-03 | Prairie | 2025-01-09 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000100 | 15400 | 200 | 77 | PR-S19-04 | Prairie | 2025-01-09 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-000101 | 9312 | 96 | 97 | BY-S04-01 | Bayou | 2025-01-09 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000102 | 24297 | 89 | 273 | BY-S14-02 | Bayou | 2025-01-09 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000103 | 26010 | 102 | 255 | BY-S17-04 | Bayou | 2025-01-09 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-000104 | 355 | 5 | 71 | BY-S21-02 | Bayou | 2025-01-09 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000105 | 1476 | 9 | 164 | BY-S01-02 | Bayou | 2025-01-09 | 16 | Animal | Transformer fuse | Forced | None
OE-25-000106 | 5875 | 47 | 125 | HB-S05-01 | Harbor | 2025-01-09 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-000107 | 10664 | 124 | 86 | BY-S19-02 | Bayou | 2025-01-09 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000108 | 366 | 6 | 61 | BY-S17-04 | Bayou | 2025-01-10 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-25-000109 | 20349 | 133 | 153 | BY-S26-05 | Bayou | 2025-01-10 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-000110 | 2697 | 31 | 87 | PR-S12-01 | Prairie | 2025-01-10 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000111 | 7488 | 36 | 208 | CR-S01-04 | Crossroads | 2025-01-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000112 | 4779 | 27 | 177 | HB-S10-01 | Harbor | 2025-01-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000113 | 1872 | 26 | 72 | BY-S12-02 | Bayou | 2025-01-10 | 11 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000114 | 27470 | 335 | 82 | HB-S09-02 | Harbor | 2025-01-10 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000115 | 2502 | 9 | 278 | BY-S02-02 | Bayou | 2025-01-10 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000116 | 21303 | 263 | 81 | CR-S07-06 | Crossroads | 2025-01-10 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000117 | 7752 | 76 | 102 | PR-S10-02 | Prairie | 2025-01-10 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000118 | 37170 | 885 | 42 | CR-S18-03 | Crossroads | 2025-01-10 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000119 | 4340 | 10 | 434 | PR-S13-01 | Prairie | 2025-01-10 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-000120 | 781 | 11 | 71 | PR-S15-04 | Prairie | 2025-01-10 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000121 | 10486 | 107 | 98 | BY-S10-05 | Bayou | 2025-01-11 | 12 | Animal | Lateral fuse | Forced | None
OE-25-000122 | 1474 | 11 | 134 | BY-S13-01 | Bayou | 2025-01-11 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-000123 | 28320 | 118 | 240 | BY-S15-03 | Bayou | 2025-01-11 | 14 | Animal | Lateral fuse | Forced | None
OE-25-000124 | 579 | 3 | 193 | CR-S04-06 | Crossroads | 2025-01-11 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-000125 | 10560 | 165 | 64 | BY-S15-03 | Bayou | 2025-01-11 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000126 | 2280 | 12 | 190 | CR-S23-01 | Crossroads | 2025-01-11 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-000127 | 550 | 5 | 110 | CR-S01-03 | Crossroads | 2025-01-11 | 17 | Animal | Transformer fuse | Forced | None
OE-25-000128 | 1243 | 11 | 113 | PR-S07-05 | Prairie | 2025-01-11 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000129 | 1647 | 9 | 183 | BY-S28-03 | Bayou | 2025-01-11 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000130 | 10395 | 99 | 105 | BY-S08-02 | Bayou | 2025-01-12 | 6 | Vegetation | Lateral fuse | Forced | None
OE-25-000131 | 5440 | 85 | 64 | HB-S10-03 | Harbor | 2025-01-12 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-000132 | 2664 | 37 | 72 | HB-S03-01 | Harbor | 2025-01-12 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000133 | 306 | 2 | 153 | HB-S01-05 | Harbor | 2025-01-12 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000134 | 1088 | 8 | 136 | HB-S16-03 | Harbor | 2025-01-12 | 15 | Animal | Transformer fuse | Forced | None
OE-25-000135 | 6020 | 86 | 70 | CR-S26-06 | Crossroads | 2025-01-12 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-000136 | 31900 | 638 | 50 | HB-S10-03 | Harbor | 2025-01-12 | 16 | Vehicle or public | IGSD-isolated section | Forced | None
OE-25-000137 | 96717 | 939 | 103 | CR-S28-01 | Crossroads | 2025-01-12 | 18 | Weather - wind | Feeder recloser | Forced | None
OE-25-000138 | 55510 | 610 | 91 | HB-S19-02 | Harbor | 2025-01-12 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-000139 | 1368 | 12 | 114 | BY-S09-04 | Bayou | 2025-01-12 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000140 | 2739 | 11 | 249 | PR-S20-04 | Prairie | 2025-01-12 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-000141 | 121632 | 1267 | 96 | BY-S17-04 | Bayou | 2025-01-13 | 1 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000142 | 29931 | 907 | 33 | HB-S06-04 | Harbor | 2025-01-13 | 6 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000143 | 948 | 12 | 79 | HB-S19-03 | Harbor | 2025-01-13 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-000144 | 927 | 9 | 103 | PR-S03-01 | Prairie | 2025-01-13 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000145 | 31434 | 403 | 78 | CR-S13-01 | Crossroads | 2025-01-13 | 9 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000146 | 4725 | 45 | 105 | PR-S07-06 | Prairie | 2025-01-13 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000147 | 1332 | 6 | 222 | CR-S22-01 | Crossroads | 2025-01-13 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000148 | 810 | 6 | 135 | CR-S05-01 | Crossroads | 2025-01-13 | 12 | Animal | Transformer fuse | Forced | None
OE-25-000149 | 9456 | 48 | 197 | BY-S30-02 | Bayou | 2025-01-13 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000150 | 9296 | 56 | 166 | CR-S20-02 | Crossroads | 2025-01-13 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000151 | 1417 | 13 | 109 | HB-S06-05 | Harbor | 2025-01-13 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-000152 | 420 | 2 | 210 | BY-S10-05 | Bayou | 2025-01-13 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000153 | 1655 | 5 | 331 | CR-S17-02 | Crossroads | 2025-01-13 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000154 | 27115 | 319 | 85 | PR-S13-06 | Prairie | 2025-01-13 | 17 | Unknown | Feeder recloser | Forced | None
OE-25-000155 | 4606 | 47 | 98 | PR-S05-03 | Prairie | 2025-01-13 | 19 | Animal | Lateral fuse | Forced | None
OE-25-000156 | 218316 | 966 | 226 | BY-S11-01 | Bayou | 2025-01-13 | 21 | Vegetation | Feeder recloser | Forced | None
OE-25-000157 | 57433 | 727 | 79 | BY-S05-02 | Bayou | 2025-01-14 | 5 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000158 | 216 | 6 | 36 | HB-S09-05 | Harbor | 2025-01-14 | 8 | Animal | Transformer fuse | Forced | None
OE-25-000159 | 2325 | 25 | 93 | BY-S24-03 | Bayou | 2025-01-14 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000160 | 3287 | 19 | 173 | HB-S06-02 | Harbor | 2025-01-14 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-000161 | 7176 | 23 | 312 | BY-S30-01 | Bayou | 2025-01-14 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000162 | 2808 | 26 | 108 | CR-S08-02 | Crossroads | 2025-01-14 | 15 | Animal | Lateral fuse | Forced | None
OE-25-000163 | 1630 | 10 | 163 | PR-S19-03 | Prairie | 2025-01-14 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000164 | 79894 | 1858 | 43 | CR-S09-01 | Crossroads | 2025-01-14 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-000165 | 13144 | 62 | 212 | PR-S11-02 | Prairie | 2025-01-14 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000166 | 66960 | 2232 | 30 | BY-S29-01 | Bayou | 2025-01-15 | 0 | Vegetation | Feeder recloser | Forced | None
OE-25-000167 | 11374 | 121 | 94 | PR-S17-01 | Prairie | 2025-01-15 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000168 | 600 | 12 | 50 | BY-S15-06 | Bayou | 2025-01-15 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000169 | 164 | 2 | 82 | CR-S17-02 | Crossroads | 2025-01-15 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000170 | 1552 | 8 | 194 | CR-S13-05 | Crossroads | 2025-01-15 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000171 | 5817 | 21 | 277 | HB-S17-03 | Harbor | 2025-01-15 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000172 | 4023 | 27 | 149 | BY-S14-01 | Bayou | 2025-01-15 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000173 | 74404 | 979 | 76 | BY-S29-05 | Bayou | 2025-01-15 | 22 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000174 | 7392 | 28 | 264 | PR-S06-03 | Prairie | 2025-01-16 | 8 | Animal | Lateral fuse | Forced | None
OE-25-000175 | 5985 | 35 | 171 | BY-S13-04 | Bayou | 2025-01-16 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000176 | 9918 | 57 | 174 | BY-S09-05 | Bayou | 2025-01-16 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-000177 | 2312 | 8 | 289 | BY-S26-03 | Bayou | 2025-01-16 | 13 | Animal | Transformer fuse | Forced | None
OE-25-000178 | 3589 | 37 | 97 | PR-S19-03 | Prairie | 2025-01-16 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000179 | 1944 | 9 | 216 | HB-S10-03 | Harbor | 2025-01-17 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000180 | 1092 | 12 | 91 | PR-S18-02 | Prairie | 2025-01-17 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000181 | 6550 | 50 | 131 | BY-S26-05 | Bayou | 2025-01-17 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000182 | 676 | 4 | 169 | CR-S05-03 | Crossroads | 2025-01-17 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000183 | 4853 | 23 | 211 | BY-S20-03 | Bayou | 2025-01-17 | 11 | Animal | Lateral fuse | Forced | None
OE-25-000184 | 2418 | 13 | 186 | BY-S30-03 | Bayou | 2025-01-17 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000185 | 10230 | 66 | 155 | CR-S16-06 | Crossroads | 2025-01-17 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000186 | 3476 | 79 | 44 | HB-S05-05 | Harbor | 2025-01-17 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000187 | 8400 | 40 | 210 | BY-S20-01 | Bayou | 2025-01-17 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-000188 | 33226 | 449 | 74 | CR-S22-04 | Crossroads | 2025-01-17 | 18 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-000189 | 824 | 8 | 103 | CR-S30-01 | Crossroads | 2025-01-18 | 6 | Animal | Transformer fuse | Forced | None
OE-25-000190 | 165 | 1 | 165 | PR-S13-03 | Prairie | 2025-01-18 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000191 | 2783 | 11 | 253 | HB-S05-05 | Harbor | 2025-01-18 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-25-000192 | 891 | 3 | 297 | PR-S12-01 | Prairie | 2025-01-18 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000193 | 6083 | 77 | 79 | BY-S05-01 | Bayou | 2025-01-18 | 10 | Unknown | Lateral fuse | Forced | None
OE-25-000194 | 26367 | 141 | 187 | PR-S14-01 | Prairie | 2025-01-18 | 11 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-000195 | 82208 | 2569 | 32 | BY-S14-01 | Bayou | 2025-01-18 | 18 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000196 | 29511 | 1093 | 27 | PR-S12-03 | Prairie | 2025-01-18 | 18 | Equipment - underground | Substation breaker | Forced | None
OE-25-000197 | 4968 | 69 | 72 | CR-S28-01 | Crossroads | 2025-01-18 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000198 | 910 | 10 | 91 | CR-S06-02 | Crossroads | 2025-01-18 | 23 | Animal | Lateral fuse | Forced | None
OE-25-000199 | 2726 | 47 | 58 | PR-S19-03 | Prairie | 2025-01-19 | 3 | Vegetation | Lateral fuse | Forced | None
OE-25-000200 | 28956 | 127 | 228 | BY-S03-02 | Bayou | 2025-01-19 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000201 | 1209 | 13 | 93 | BY-S07-03 | Bayou | 2025-01-19 | 11 | Animal | Transformer fuse | Forced | None
OE-25-000202 | 1276 | 11 | 116 | CR-S07-07 | Crossroads | 2025-01-19 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000203 | 23312 | 188 | 124 | CR-S30-01 | Crossroads | 2025-01-19 | 13 | Animal | Lateral fuse | Forced | None
OE-25-000204 | 685 | 5 | 137 | BY-S02-01 | Bayou | 2025-01-19 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000205 | 6348 | 138 | 46 | PR-S10-03 | Prairie | 2025-01-20 | 3 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000206 | 24759 | 131 | 189 | PR-S12-01 | Prairie | 2025-01-20 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-000207 | 1344 | 6 | 224 | BY-S27-01 | Bayou | 2025-01-20 | 10 | Animal | Transformer fuse | Forced | None
OE-25-000208 | 11374 | 121 | 94 | CR-S09-03 | Crossroads | 2025-01-20 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000209 | 9050 | 50 | 181 | PR-S20-03 | Prairie | 2025-01-20 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-000210 | 4136 | 11 | 376 | PR-S01-05 | Prairie | 2025-01-20 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000211 | 2100 | 28 | 75 | BY-S03-03 | Bayou | 2025-01-20 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000212 | 13224 | 114 | 116 | BY-S29-03 | Bayou | 2025-01-20 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000213 | 2650 | 50 | 53 | CR-S02-04 | Crossroads | 2025-01-20 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000214 | 5278 | 29 | 182 | PR-S10-01 | Prairie | 2025-01-20 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000215 | 945 | 27 | 35 | PR-S06-01 | Prairie | 2025-01-20 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000216 | 2730 | 35 | 78 | PR-S05-02 | Prairie | 2025-01-20 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000217 | 1768 | 13 | 136 | PR-S16-04 | Prairie | 2025-01-20 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-000218 | 314 | 1 | 314 | PR-S15-06 | Prairie | 2025-01-20 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-000219 | 2871 | 11 | 261 | BY-S10-03 | Bayou | 2025-01-21 | 0 | Animal | Transformer fuse | Forced | None
OE-25-000220 | 33858 | 594 | 57 | CR-S30-06 | Crossroads | 2025-01-21 | 7 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000221 | 179334 | 4374 | 41 | HB-S10-03 | Harbor | 2025-01-21 | 7 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-000222 | 8010 | 45 | 178 | CR-S31-01 | Crossroads | 2025-01-21 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000223 | 10304 | 56 | 184 | BY-S29-03 | Bayou | 2025-01-21 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000224 | 4453 | 61 | 73 | BY-S30-02 | Bayou | 2025-01-21 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-000225 | 23680 | 640 | 37 | PR-S02-01 | Prairie | 2025-01-21 | 11 | Animal | Feeder recloser | Forced | None
OE-25-000226 | 332 | 4 | 83 | HB-S07-05 | Harbor | 2025-01-21 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000227 | 765 | 9 | 85 | CR-S22-04 | Crossroads | 2025-01-21 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000228 | 11340 | 63 | 180 | PR-S12-01 | Prairie | 2025-01-21 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000229 | 49176 | 683 | 72 | BY-S11-02 | Bayou | 2025-01-21 | 16 | Unknown | Substation breaker | Outside cause | None
OE-25-000230 | 16200 | 72 | 225 | BY-S18-05 | Bayou | 2025-01-21 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000231 | 6160 | 44 | 140 | PR-S19-04 | Prairie | 2025-01-21 | 22 | Weather - wind | Lateral fuse | Forced | None
OE-25-000232 | 14322 | 93 | 154 | BY-S06-03 | Bayou | 2025-01-22 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-000233 | 5632 | 32 | 176 | CR-S22-01 | Crossroads | 2025-01-22 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-000234 | 17848 | 92 | 194 | PR-S03-02 | Prairie | 2025-01-22 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000235 | 21600 | 360 | 60 | BY-S20-03 | Bayou | 2025-01-22 | 10 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000236 | 1638 | 14 | 117 | BY-S03-01 | Bayou | 2025-01-22 | 12 | Animal | Transformer fuse | Forced | None
OE-25-000237 | 2610 | 45 | 58 | HB-S15-03 | Harbor | 2025-01-22 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000238 | 4836 | 31 | 156 | PR-S08-01 | Prairie | 2025-01-22 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000239 | 1260 | 7 | 180 | PR-S15-06 | Prairie | 2025-01-22 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000240 | 60975 | 271 | 225 | BY-S02-02 | Bayou | 2025-01-22 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-000241 | 658 | 7 | 94 | CR-S04-03 | Crossroads | 2025-01-22 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000242 | 435 | 3 | 145 | CR-S17-02 | Crossroads | 2025-01-22 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000243 | 570 | 5 | 114 | BY-S05-02 | Bayou | 2025-01-22 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000244 | 1308 | 12 | 109 | PR-S14-04 | Prairie | 2025-01-22 | 21 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000245 | 1393 | 7 | 199 | PR-S07-05 | Prairie | 2025-01-22 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000246 | 3315 | 65 | 51 | CR-S24-01 | Crossroads | 2025-01-22 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000247 | 1083 | 3 | 361 | PR-S19-05 | Prairie | 2025-01-23 | 4 | Vegetation | Transformer fuse | Forced | None
OE-25-000248 | 4292 | 37 | 116 | CR-S15-01 | Crossroads | 2025-01-23 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-000249 | 1188 | 4 | 297 | BY-S27-02 | Bayou | 2025-01-23 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-000250 | 1368 | 8 | 171 | CR-S30-03 | Crossroads | 2025-01-23 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000251 | 1020 | 12 | 85 | CR-S15-01 | Crossroads | 2025-01-23 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000252 | 159640 | 614 | 260 | PR-S16-05 | Prairie | 2025-01-23 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000253 | 6815 | 29 | 235 | BY-S25-03 | Bayou | 2025-01-23 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000254 | 453 | 3 | 151 | CR-S10-03 | Crossroads | 2025-01-23 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000255 | 1340 | 20 | 67 | HB-S03-02 | Harbor | 2025-01-23 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000256 | 52839 | 103 | 513 | BY-S27-06 | Bayou | 2025-01-23 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000257 | 17446 | 61 | 286 | CR-S08-06 | Crossroads | 2025-01-23 | 19 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000258 | 14608 | 88 | 166 | PR-S01-01 | Prairie | 2025-01-24 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000259 | 396 | 12 | 33 | CR-S18-05 | Crossroads | 2025-01-24 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-25-000260 | 414 | 6 | 69 | BY-S21-05 | Bayou | 2025-01-24 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-000261 | 650 | 26 | 25 | PR-S09-03 | Prairie | 2025-01-24 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000262 | 262 | 2 | 131 | CR-S22-04 | Crossroads | 2025-01-24 | 13 | Unknown | Transformer fuse | Forced | None
OE-25-000263 | 321 | 1 | 321 | BY-S08-02 | Bayou | 2025-01-24 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-000264 | 3010 | 10 | 301 | HB-S09-03 | Harbor | 2025-01-24 | 17 | Animal | Transformer fuse | Forced | None
OE-25-000265 | 2290 | 10 | 229 | PR-S15-03 | Prairie | 2025-01-24 | 17 | Animal | Transformer fuse | Forced | None
OE-25-000266 | 1617 | 11 | 147 | PR-S20-03 | Prairie | 2025-01-24 | 18 | Unknown | Transformer fuse | Forced | None
OE-25-000267 | 6435 | 99 | 65 | HB-S10-01 | Harbor | 2025-01-24 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000268 | 1032 | 6 | 172 | BY-S15-04 | Bayou | 2025-01-25 | 2 | Vegetation | Transformer fuse | Forced | None
OE-25-000269 | 576 | 6 | 96 | CR-S19-01 | Crossroads | 2025-01-25 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000270 | 5710 | 571 | 10 | HB-S01-02 | Harbor | 2025-01-25 | 12 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-000271 | 7366 | 127 | 58 | HB-S12-03 | Harbor | 2025-01-25 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000272 | 3152 | 8 | 394 | PR-S03-05 | Prairie | 2025-01-25 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000273 | 576 | 12 | 48 | CR-S05-06 | Crossroads | 2025-01-25 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-000274 | 702 | 9 | 78 | CR-S01-03 | Crossroads | 2025-01-25 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000275 | 2046 | 33 | 62 | BY-S15-06 | Bayou | 2025-01-25 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-000276 | 79976 | 1538 | 52 | BY-S16-04 | Bayou | 2025-01-25 | 22 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-000277 | 756 | 9 | 84 | HB-S09-01 | Harbor | 2025-01-25 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000278 | 6302 | 23 | 274 | CR-S09-03 | Crossroads | 2025-01-26 | 2 | Weather - wind | Lateral fuse | Forced | None
OE-25-000279 | 1344 | 8 | 168 | PR-S17-01 | Prairie | 2025-01-26 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000280 | 10498 | 58 | 181 | PR-S14-01 | Prairie | 2025-01-26 | 8 | Animal | Lateral fuse | Forced | None
OE-25-000281 | 55360 | 1730 | 32 | BY-S07-02 | Bayou | 2025-01-26 | 9 | Vegetation | Substation breaker | Forced | None
OE-25-000282 | 2668 | 46 | 58 | HB-S10-01 | Harbor | 2025-01-26 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000283 | 1554 | 14 | 111 | HB-S19-04 | Harbor | 2025-01-26 | 9 | Animal | Transformer fuse | Forced | None
OE-25-000284 | 1860 | 10 | 186 | BY-S15-04 | Bayou | 2025-01-26 | 11 | Animal | Transformer fuse | Forced | None
OE-25-000285 | 1002 | 6 | 167 | HB-S03-03 | Harbor | 2025-01-26 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000286 | 2196 | 9 | 244 | BY-S04-01 | Bayou | 2025-01-26 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000287 | 8244 | 36 | 229 | BY-S07-02 | Bayou | 2025-01-26 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-000288 | 1179 | 3 | 393 | PR-S07-05 | Prairie | 2025-01-26 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000289 | 1200 | 12 | 100 | CR-S09-03 | Crossroads | 2025-01-26 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-000290 | 9600 | 48 | 200 | BY-S09-04 | Bayou | 2025-01-26 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-000291 | 1300 | 13 | 100 | BY-S12-01 | Bayou | 2025-01-26 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000292 | 9396 | 54 | 174 | BY-S13-05 | Bayou | 2025-01-26 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000293 | 6355 | 41 | 155 | PR-S06-01 | Prairie | 2025-01-26 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-000294 | 58400 | 1168 | 50 | HB-S06-01 | Harbor | 2025-01-27 | 0 | Equipment - underground | Substation breaker | Forced | None
OE-25-000295 | 1530 | 18 | 85 | BY-S16-01 | Bayou | 2025-01-27 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000296 | 1018 | 2 | 509 | PR-S14-04 | Prairie | 2025-01-27 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000297 | 30030 | 210 | 143 | CR-S18-06 | Crossroads | 2025-01-27 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000298 | 2375 | 19 | 125 | BY-S16-03 | Bayou | 2025-01-27 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000299 | 22624 | 808 | 28 | BY-S18-03 | Bayou | 2025-01-27 | 12 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-000300 | 2574 | 26 | 99 | BY-S13-03 | Bayou | 2025-01-27 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000301 | 58696 | 319 | 184 | HB-S10-02 | Harbor | 2025-01-27 | 14 | Unknown | Lateral fuse | Forced | None
OE-25-000302 | 2175 | 29 | 75 | BY-S10-02 | Bayou | 2025-01-27 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-000303 | 3654 | 63 | 58 | CR-S04-03 | Crossroads | 2025-01-27 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-000304 | 6192 | 48 | 129 | CR-S07-02 | Crossroads | 2025-01-27 | 18 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000305 | 59520 | 1240 | 48 | CR-S22-04 | Crossroads | 2025-01-27 | 23 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000306 | 1908 | 12 | 159 | CR-S01-03 | Crossroads | 2025-01-28 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-000307 | 2407 | 29 | 83 | CR-S26-06 | Crossroads | 2025-01-28 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000308 | 5782 | 49 | 118 | BY-S09-02 | Bayou | 2025-01-28 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-000309 | 3172 | 26 | 122 | CR-S22-04 | Crossroads | 2025-01-28 | 12 | Unknown | Lateral fuse | Forced | None
OE-25-000310 | 2052 | 12 | 171 | CR-S26-06 | Crossroads | 2025-01-28 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000311 | 25670 | 302 | 85 | BY-S18-03 | Bayou | 2025-01-28 | 17 | Animal | Feeder recloser | Forced | None
OE-25-000312 | 15224 | 88 | 173 | PR-S16-03 | Prairie | 2025-01-28 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000313 | 1560 | 10 | 156 | PR-S07-02 | Prairie | 2025-01-29 | 1 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000314 | 15246 | 99 | 154 | BY-S18-04 | Bayou | 2025-01-29 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000315 | 1520 | 19 | 80 | BY-S25-03 | Bayou | 2025-01-29 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000316 | 7425 | 45 | 165 | PR-S02-02 | Prairie | 2025-01-29 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000317 | 15481 | 113 | 137 | BY-S19-02 | Bayou | 2025-01-29 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000318 | 29177 | 179 | 163 | BY-S12-01 | Bayou | 2025-01-29 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-000319 | 2142 | 17 | 126 | BY-S13-05 | Bayou | 2025-01-29 | 19 | Animal | Lateral fuse | Forced | None
OE-25-000320 | 301636 | 2066 | 146 | CR-S07-03 | Crossroads | 2025-01-29 | 20 | Vegetation | Substation breaker | Forced | None
OE-25-000321 | 9911 | 53 | 187 | PR-S20-01 | Prairie | 2025-01-29 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-000322 | 14558 | 251 | 58 | CR-S13-03 | Crossroads | 2025-01-30 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000323 | 2775 | 15 | 185 | PR-S20-03 | Prairie | 2025-01-30 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000324 | 7626 | 62 | 123 | BY-S25-04 | Bayou | 2025-01-30 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000325 | 9860 | 85 | 116 | PR-S19-04 | Prairie | 2025-01-30 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000326 | 2820 | 47 | 60 | BY-S26-02 | Bayou | 2025-01-30 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000327 | 868 | 14 | 62 | CR-S16-05 | Crossroads | 2025-01-30 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-000328 | 3564 | 66 | 54 | HB-S03-03 | Harbor | 2025-01-30 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000329 | 649 | 11 | 59 | HB-S05-04 | Harbor | 2025-01-30 | 16 | Animal | Transformer fuse | Forced | None
OE-25-000330 | 24180 | 93 | 260 | PR-S02-02 | Prairie | 2025-01-30 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-000331 | 91355 | 755 | 121 | BY-S07-03 | Bayou | 2025-01-30 | 19 | Vegetation | Feeder recloser | Forced | None
OE-25-000332 | 2214 | 9 | 246 | BY-S09-01 | Bayou | 2025-01-31 | 11 | Animal | Transformer fuse | Forced | None
OE-25-000333 | 2961 | 7 | 423 | BY-S25-04 | Bayou | 2025-01-31 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000334 | 15204 | 724 | 21 | BY-S27-04 | Bayou | 2025-01-31 | 15 | Weather - wind | Substation breaker | Forced | None
OE-25-000335 | 285 | 1 | 285 | HB-S19-04 | Harbor | 2025-01-31 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000336 | 968 | 4 | 242 | BY-S07-01 | Bayou | 2025-01-31 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000337 | 9702 | 63 | 154 | HB-S16-05 | Harbor | 2025-01-31 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-000338 | 262 | 2 | 131 | BY-S11-02 | Bayou | 2025-02-01 | 0 | Unknown | Transformer fuse | Forced | None
OE-25-000339 | 3416 | 28 | 122 | CR-S04-01 | Crossroads | 2025-02-01 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000340 | 3552 | 24 | 148 | PR-S18-04 | Prairie | 2025-02-01 | 3 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000341 | 8700 | 60 | 145 | PR-S04-01 | Prairie | 2025-02-01 | 6 | Animal | Lateral fuse | Forced | None
OE-25-000342 | 1728 | 6 | 288 | BY-S24-05 | Bayou | 2025-02-01 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000343 | 18760 | 70 | 268 | PR-S09-01 | Prairie | 2025-02-01 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-25-000344 | 1650 | 11 | 150 | BY-S13-05 | Bayou | 2025-02-01 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-000345 | 8601 | 61 | 141 | BY-S07-05 | Bayou | 2025-02-01 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000346 | 328 | 2 | 164 | CR-S14-06 | Crossroads | 2025-02-01 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000347 | 1287 | 13 | 99 | HB-S18-02 | Harbor | 2025-02-01 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-000348 | 666 | 6 | 111 | HB-S06-02 | Harbor | 2025-02-01 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-000349 | 480 | 6 | 80 | HB-S19-03 | Harbor | 2025-02-01 | 19 | Animal | Transformer fuse | Forced | None
OE-25-000350 | 22627 | 121 | 187 | PR-S15-01 | Prairie | 2025-02-02 | 4 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000351 | 10384 | 118 | 88 | PR-S04-03 | Prairie | 2025-02-02 | 5 | Vegetation | Feeder recloser | Forced | None
OE-25-000352 | 1660 | 10 | 166 | BY-S05-02 | Bayou | 2025-02-02 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000353 | 85680 | 560 | 153 | CR-S23-04 | Crossroads | 2025-02-02 | 7 | Weather - lightning | Feeder recloser | Forced | None
OE-25-000354 | 1749 | 33 | 53 | CR-S20-01 | Crossroads | 2025-02-02 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000355 | 894 | 6 | 149 | BY-S03-02 | Bayou | 2025-02-02 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000356 | 23214 | 318 | 73 | PR-S07-01 | Prairie | 2025-02-02 | 11 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-000357 | 49385 | 581 | 85 | HB-S13-01 | Harbor | 2025-02-02 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000358 | 4192 | 16 | 262 | BY-S22-03 | Bayou | 2025-02-02 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000359 | 1246 | 14 | 89 | CR-S09-05 | Crossroads | 2025-02-02 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-000360 | 49302 | 99 | 498 | BY-S15-03 | Bayou | 2025-02-02 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-000361 | 3625 | 29 | 125 | HB-S15-01 | Harbor | 2025-02-02 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000362 | 17824 | 557 | 32 | BY-S10-01 | Bayou | 2025-02-02 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000363 | 77 | 1 | 77 | HB-S10-01 | Harbor | 2025-02-02 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000364 | 29841 | 147 | 203 | PR-S14-04 | Prairie | 2025-02-03 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000365 | 2166 | 3 | 722 | BY-S07-05 | Bayou | 2025-02-03 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000366 | 6572 | 212 | 31 | CR-S19-03 | Crossroads | 2025-02-03 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000367 | 162624 | 2464 | 66 | HB-S18-01 | Harbor | 2025-02-03 | 9 | Unknown | Substation breaker | Outside cause | None
OE-25-000368 | 1133 | 11 | 103 | BY-S17-01 | Bayou | 2025-02-03 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000369 | 51 | 1 | 51 | BY-S24-03 | Bayou | 2025-02-03 | 12 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000370 | 185 | 5 | 37 | CR-S12-01 | Crossroads | 2025-02-03 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000371 | 72780 | 1213 | 60 | HB-S01-01 | Harbor | 2025-02-03 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-25-000372 | 1638 | 14 | 117 | HB-S03-03 | Harbor | 2025-02-03 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000373 | 1261 | 13 | 97 | HB-S08-02 | Harbor | 2025-02-03 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000374 | 804 | 12 | 67 | BY-S02-02 | Bayou | 2025-02-03 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000375 | 6292 | 242 | 26 | PR-S04-03 | Prairie | 2025-02-03 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-000376 | 378 | 6 | 63 | PR-S11-03 | Prairie | 2025-02-03 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000377 | 900 | 4 | 225 | CR-S04-06 | Crossroads | 2025-02-03 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000378 | 9225 | 205 | 45 | PR-S18-03 | Prairie | 2025-02-03 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000379 | 2808 | 12 | 234 | BY-S05-02 | Bayou | 2025-02-04 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000380 | 90666 | 1242 | 73 | CR-S21-03 | Crossroads | 2025-02-04 | 7 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-000381 | 1071 | 21 | 51 | PR-S02-02 | Prairie | 2025-02-04 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000382 | 1261 | 13 | 97 | CR-S07-07 | Crossroads | 2025-02-04 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000383 | 8476 | 326 | 26 | BY-S18-07 | Bayou | 2025-02-04 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000384 | 8536 | 88 | 97 | CR-S29-02 | Crossroads | 2025-02-04 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000385 | 23490 | 145 | 162 | HB-S12-01 | Harbor | 2025-02-04 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000386 | 143968 | 818 | 176 | BY-S24-05 | Bayou | 2025-02-05 | 4 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000387 | 2392 | 23 | 104 | BY-S30-01 | Bayou | 2025-02-05 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000388 | 1548 | 12 | 129 | CR-S32-03 | Crossroads | 2025-02-05 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000389 | 612 | 12 | 51 | BY-S23-01 | Bayou | 2025-02-05 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000390 | 268157 | 2047 | 131 | CR-S26-02 | Crossroads | 2025-02-05 | 20 | Equipment - underground | Substation breaker | Forced | None
OE-25-000391 | 21840 | 140 | 156 | BY-S22-03 | Bayou | 2025-02-05 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000392 | 705 | 5 | 141 | CR-S17-01 | Crossroads | 2025-02-06 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-000393 | 7995 | 123 | 65 | BY-S16-03 | Bayou | 2025-02-06 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-000394 | 282 | 1 | 282 | BY-S27-06 | Bayou | 2025-02-06 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000395 | 6572 | 53 | 124 | CR-S01-01 | Crossroads | 2025-02-06 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000396 | 157920 | 987 | 160 | CR-S22-01 | Crossroads | 2025-02-06 | 10 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000397 | 11552 | 38 | 304 | BY-S10-03 | Bayou | 2025-02-06 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000398 | 1482 | 13 | 114 | BY-S13-01 | Bayou | 2025-02-06 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-000399 | 3230 | 17 | 190 | CR-S13-05 | Crossroads | 2025-02-06 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000400 | 14320 | 80 | 179 | PR-S20-02 | Prairie | 2025-02-06 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000401 | 74382 | 966 | 77 | BY-S21-04 | Bayou | 2025-02-06 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000402 | 5643 | 33 | 171 | CR-S08-04 | Crossroads | 2025-02-06 | 14 | Animal | Lateral fuse | Forced | None
OE-25-000403 | 155325 | 1425 | 109 | HB-S10-02 | Harbor | 2025-02-06 | 14 | Unknown | Substation breaker | Forced | None
OE-25-000404 | 2510 | 10 | 251 | PR-S18-02 | Prairie | 2025-02-06 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-000405 | 550 | 5 | 110 | CR-S05-03 | Crossroads | 2025-02-06 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000406 | 1651 | 13 | 127 | CR-S02-03 | Crossroads | 2025-02-06 | 16 | Animal | Transformer fuse | Forced | None
OE-25-000407 | 756 | 4 | 189 | CR-S32-05 | Crossroads | 2025-02-06 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000408 | 492 | 6 | 82 | CR-S05-01 | Crossroads | 2025-02-06 | 20 | Animal | Transformer fuse | Forced | None
OE-25-000409 | 414 | 3 | 138 | BY-S26-05 | Bayou | 2025-02-06 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-000410 | 1380 | 30 | 46 | BY-S28-03 | Bayou | 2025-02-07 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000411 | 36284 | 188 | 193 | PR-S01-05 | Prairie | 2025-02-07 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000412 | 6344 | 52 | 122 | CR-S12-03 | Crossroads | 2025-02-07 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000413 | 556 | 2 | 278 | CR-S05-05 | Crossroads | 2025-02-07 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000414 | 32938 | 766 | 43 | CR-S24-03 | Crossroads | 2025-02-07 | 10 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000415 | 441 | 3 | 147 | BY-S10-03 | Bayou | 2025-02-07 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000416 | 6140 | 20 | 307 | HB-S02-02 | Harbor | 2025-02-07 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-000417 | 9729 | 69 | 141 | PR-S20-03 | Prairie | 2025-02-07 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000418 | 30736 | 452 | 68 | PR-S16-02 | Prairie | 2025-02-07 | 15 | Animal | Substation breaker | Forced | None
OE-25-000419 | 33630 | 590 | 57 | BY-S19-04 | Bayou | 2025-02-07 | 16 | Vegetation | Feeder recloser | Forced | None
OE-25-000420 | 214979 | 1201 | 179 | BY-S17-04 | Bayou | 2025-02-07 | 19 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000421 | 684 | 4 | 171 | BY-S24-01 | Bayou | 2025-02-07 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-000422 | 960 | 5 | 192 | BY-S28-03 | Bayou | 2025-02-08 | 4 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000423 | 4216 | 62 | 68 | PR-S01-03 | Prairie | 2025-02-08 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-000424 | 1722 | 41 | 42 | BY-S26-04 | Bayou | 2025-02-08 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-000425 | 2652 | 12 | 221 | PR-S03-01 | Prairie | 2025-02-08 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-000426 | 7686 | 42 | 183 | BY-S01-02 | Bayou | 2025-02-08 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-000427 | 707 | 7 | 101 | BY-S16-01 | Bayou | 2025-02-08 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000428 | 528 | 8 | 66 | BY-S15-01 | Bayou | 2025-02-08 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000429 | 281990 | 1730 | 163 | CR-S27-04 | Crossroads | 2025-02-08 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-000430 | 910 | 13 | 70 | BY-S15-01 | Bayou | 2025-02-08 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000431 | 6633 | 67 | 99 | BY-S12-01 | Bayou | 2025-02-08 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000432 | 384 | 2 | 192 | BY-S17-01 | Bayou | 2025-02-08 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-000433 | 1251 | 9 | 139 | CR-S30-04 | Crossroads | 2025-02-08 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000434 | 405 | 3 | 135 | BY-S12-04 | Bayou | 2025-02-09 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-000435 | 23564 | 172 | 137 | BY-S21-05 | Bayou | 2025-02-09 | 1 | Animal | Lateral fuse | Forced | None
OE-25-000436 | 4368 | 78 | 56 | CR-S09-01 | Crossroads | 2025-02-09 | 1 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000437 | 3472 | 16 | 217 | BY-S26-06 | Bayou | 2025-02-09 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-000438 | 900 | 5 | 180 | BY-S22-03 | Bayou | 2025-02-09 | 8 | Animal | Transformer fuse | Forced | None
OE-25-000439 | 4968 | 54 | 92 | CR-S13-01 | Crossroads | 2025-02-09 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000440 | 51398 | 829 | 62 | CR-S21-02 | Crossroads | 2025-02-09 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000441 | 8060 | 62 | 130 | CR-S26-02 | Crossroads | 2025-02-09 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-000442 | 19967 | 41 | 487 | PR-S11-01 | Prairie | 2025-02-09 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-000443 | 10224 | 71 | 144 | PR-S16-04 | Prairie | 2025-02-09 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000444 | 6678 | 63 | 106 | HB-S20-01 | Harbor | 2025-02-10 | 0 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000445 | 12397 | 77 | 161 | CR-S30-05 | Crossroads | 2025-02-10 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000446 | 7670 | 59 | 130 | CR-S26-05 | Crossroads | 2025-02-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000447 | 122160 | 1527 | 80 | CR-S09-01 | Crossroads | 2025-02-10 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-000448 | 1485 | 33 | 45 | CR-S09-01 | Crossroads | 2025-02-10 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000449 | 2916 | 36 | 81 | PR-S15-03 | Prairie | 2025-02-10 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000450 | 1924 | 37 | 52 | HB-S05-04 | Harbor | 2025-02-11 | 0 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000451 | 2425 | 25 | 97 | PR-S13-05 | Prairie | 2025-02-11 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000452 | 840 | 6 | 140 | CR-S25-01 | Crossroads | 2025-02-11 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-000453 | 1485 | 11 | 135 | CR-S03-01 | Crossroads | 2025-02-11 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000454 | 625 | 5 | 125 | PR-S07-01 | Prairie | 2025-02-11 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000455 | 1206 | 9 | 134 | HB-S04-01 | Harbor | 2025-02-11 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000456 | 7896 | 47 | 168 | CR-S09-03 | Crossroads | 2025-02-11 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000457 | 1267 | 7 | 181 | PR-S20-03 | Prairie | 2025-02-11 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-25-000458 | 500 | 5 | 100 | CR-S02-02 | Crossroads | 2025-02-11 | 20 | Animal | Transformer fuse | Forced | None
OE-25-000459 | 1431 | 9 | 159 | BY-S21-01 | Bayou | 2025-02-11 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000460 | 4248 | 36 | 118 | PR-S11-01 | Prairie | 2025-02-12 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000461 | 2448 | 9 | 272 | BY-S13-06 | Bayou | 2025-02-12 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-25-000462 | 2376 | 27 | 88 | HB-S18-03 | Harbor | 2025-02-12 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000463 | 5824 | 52 | 112 | PR-S15-01 | Prairie | 2025-02-12 | 10 | Unknown | Lateral fuse | Forced | None
OE-25-000464 | 11956 | 98 | 122 | PR-S01-04 | Prairie | 2025-02-12 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-000465 | 260334 | 3214 | 81 | HB-S01-05 | Harbor | 2025-02-12 | 12 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000466 | 61632 | 576 | 107 | CR-S14-02 | Crossroads | 2025-02-12 | 14 | Vegetation | IGSD-isolated section | Forced | None
OE-25-000467 | 159 | 1 | 159 | BY-S10-03 | Bayou | 2025-02-12 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000468 | 18360 | 120 | 153 | CR-S19-03 | Crossroads | 2025-02-12 | 15 | Animal | Lateral fuse | Forced | None
OE-25-000469 | 450 | 6 | 75 | HB-S09-04 | Harbor | 2025-02-12 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000470 | 75207 | 583 | 129 | BY-S25-01 | Bayou | 2025-02-12 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-25-000471 | 1071 | 9 | 119 | CR-S25-06 | Crossroads | 2025-02-12 | 17 | Animal | Transformer fuse | Forced | None
OE-25-000472 | 4851 | 33 | 147 | CR-S22-01 | Crossroads | 2025-02-12 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000473 | 12264 | 219 | 56 | BY-S04-02 | Bayou | 2025-02-12 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000474 | 770 | 14 | 55 | HB-S16-05 | Harbor | 2025-02-12 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-000475 | 11025 | 105 | 105 | BY-S23-01 | Bayou | 2025-02-12 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-000476 | 3536 | 13 | 272 | PR-S03-05 | Prairie | 2025-02-12 | 22 | Unknown | Transformer fuse | Forced | None
OE-25-000477 | 25461 | 69 | 369 | PR-S13-06 | Prairie | 2025-02-13 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000478 | 6968 | 67 | 104 | HB-S07-02 | Harbor | 2025-02-13 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000479 | 135248 | 1712 | 79 | HB-S19-04 | Harbor | 2025-02-13 | 15 | Vegetation | Substation breaker | Forced | None
OE-25-000480 | 672 | 4 | 168 | BY-S15-04 | Bayou | 2025-02-13 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000481 | 882 | 7 | 126 | BY-S13-05 | Bayou | 2025-02-13 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000482 | 1218 | 7 | 174 | CR-S22-02 | Crossroads | 2025-02-13 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000483 | 5024 | 32 | 157 | CR-S03-02 | Crossroads | 2025-02-14 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000484 | 4824 | 8 | 603 | PR-S07-04 | Prairie | 2025-02-14 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000485 | 5185 | 17 | 305 | PR-S13-01 | Prairie | 2025-02-14 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000486 | 3936 | 24 | 164 | CR-S07-03 | Crossroads | 2025-02-14 | 15 | Unknown | Lateral fuse | Forced | None
OE-25-000487 | 460 | 5 | 92 | CR-S23-02 | Crossroads | 2025-02-14 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000488 | 195367 | 2473 | 79 | BY-S13-06 | Bayou | 2025-02-14 | 22 | Weather - wind | Substation breaker | Forced | None
OE-25-000489 | 73650 | 1473 | 50 | CR-S30-03 | Crossroads | 2025-02-15 | 0 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-000490 | 5148 | 11 | 468 | BY-S13-03 | Bayou | 2025-02-15 | 5 | Vegetation | Transformer fuse | Forced | None
OE-25-000491 | 1239 | 7 | 177 | BY-S16-04 | Bayou | 2025-02-15 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000492 | 42560 | 380 | 112 | HB-S03-01 | Harbor | 2025-02-15 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000493 | 635 | 5 | 127 | BY-S29-05 | Bayou | 2025-02-15 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000494 | 92 | 1 | 92 | PR-S05-02 | Prairie | 2025-02-15 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000495 | 1593 | 3 | 531 | PR-S07-04 | Prairie | 2025-02-15 | 12 | Animal | Transformer fuse | Forced | None
OE-25-000496 | 1421 | 7 | 203 | PR-S11-01 | Prairie | 2025-02-15 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000497 | 5928 | 114 | 52 | CR-S02-05 | Crossroads | 2025-02-16 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000498 | 60312 | 718 | 84 | BY-S07-06 | Bayou | 2025-02-16 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000499 | 8989 | 101 | 89 | CR-S06-02 | Crossroads | 2025-02-16 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000500 | 3186 | 9 | 354 | BY-S18-04 | Bayou | 2025-02-16 | 13 | Unknown | Transformer fuse | Forced | None
OE-25-000501 | 2240 | 10 | 224 | PR-S16-01 | Prairie | 2025-02-16 | 18 | Unknown | Transformer fuse | Forced | None
OE-25-000502 | 600 | 5 | 120 | PR-S07-04 | Prairie | 2025-02-16 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-25-000503 | 1904 | 16 | 119 | BY-S29-04 | Bayou | 2025-02-16 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-000504 | 5976 | 18 | 332 | BY-S15-02 | Bayou | 2025-02-17 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000505 | 540 | 5 | 108 | CR-S15-01 | Crossroads | 2025-02-17 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000506 | 824 | 8 | 103 | PR-S18-03 | Prairie | 2025-02-17 | 6 | Animal | Transformer fuse | Forced | None
OE-25-000507 | 417 | 3 | 139 | HB-S14-02 | Harbor | 2025-02-17 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000508 | 3132 | 29 | 108 | BY-S17-03 | Bayou | 2025-02-17 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000509 | 103100 | 1031 | 100 | BY-S06-02 | Bayou | 2025-02-17 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-000510 | 2024 | 11 | 184 | HB-S16-03 | Harbor | 2025-02-17 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-000511 | 428 | 4 | 107 | CR-S05-04 | Crossroads | 2025-02-17 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-000512 | 5225 | 95 | 55 | PR-S20-04 | Prairie | 2025-02-17 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000513 | 13600 | 85 | 160 | CR-S05-01 | Crossroads | 2025-02-17 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000514 | 88764 | 569 | 156 | BY-S12-02 | Bayou | 2025-02-18 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000515 | 7200 | 96 | 75 | PR-S15-03 | Prairie | 2025-02-18 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000516 | 3390 | 113 | 30 | BY-S01-01 | Bayou | 2025-02-18 | 13 | Unknown | Lateral fuse | Forced | None
OE-25-000517 | 3397 | 43 | 79 | CR-S14-05 | Crossroads | 2025-02-18 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000518 | 155620 | 1255 | 124 | PR-S15-06 | Prairie | 2025-02-18 | 14 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000519 | 882 | 14 | 63 | CR-S19-03 | Crossroads | 2025-02-18 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000520 | 17956 | 67 | 268 | BY-S16-06 | Bayou | 2025-02-18 | 18 | Animal | Lateral fuse | Forced | None
OE-25-000521 | 4144 | 56 | 74 | BY-S23-04 | Bayou | 2025-02-18 | 19 | Unknown | Lateral fuse | Forced | None
OE-25-000522 | 3458 | 38 | 91 | HB-S09-05 | Harbor | 2025-02-18 | 20 | Animal | Lateral fuse | Forced | None
OE-25-000523 | 3672 | 9 | 408 | PR-S09-03 | Prairie | 2025-02-19 | 3 | Vegetation | Transformer fuse | Forced | None
OE-25-000524 | 2880 | 30 | 96 | BY-S22-02 | Bayou | 2025-02-19 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-000525 | 9588 | 141 | 68 | BY-S28-03 | Bayou | 2025-02-19 | 6 | Vegetation | Lateral fuse | Forced | None
OE-25-000526 | 415 | 5 | 83 | BY-S29-01 | Bayou | 2025-02-19 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-000527 | 312 | 4 | 78 | CR-S11-02 | Crossroads | 2025-02-19 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-000528 | 1484 | 14 | 106 | CR-S25-04 | Crossroads | 2025-02-19 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-25-000529 | 37352 | 322 | 116 | HB-S03-01 | Harbor | 2025-02-19 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-000530 | 2244 | 17 | 132 | HB-S04-01 | Harbor | 2025-02-19 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000531 | 680 | 4 | 170 | HB-S09-05 | Harbor | 2025-02-19 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000532 | 570 | 3 | 190 | BY-S17-03 | Bayou | 2025-02-19 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000533 | 806 | 13 | 62 | BY-S03-02 | Bayou | 2025-02-19 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-000534 | 5088 | 96 | 53 | HB-S08-05 | Harbor | 2025-02-19 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000535 | 1520 | 10 | 152 | PR-S08-01 | Prairie | 2025-02-19 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000536 | 10875 | 25 | 435 | BY-S12-02 | Bayou | 2025-02-19 | 19 | Animal | Lateral fuse | Forced | None
OE-25-000537 | 8800 | 110 | 80 | PR-S12-01 | Prairie | 2025-02-19 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000538 | 1298 | 22 | 59 | HB-S02-02 | Harbor | 2025-02-19 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000539 | 226 | 2 | 113 | BY-S27-06 | Bayou | 2025-02-19 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000540 | 27378 | 162 | 169 | CR-S17-01 | Crossroads | 2025-02-19 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-000541 | 16452 | 457 | 36 | CR-S08-05 | Crossroads | 2025-02-20 | 8 | Animal | Feeder recloser | Forced | None
OE-25-000542 | 504 | 3 | 168 | BY-S21-04 | Bayou | 2025-02-20 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000543 | 4477 | 11 | 407 | CR-S05-03 | Crossroads | 2025-02-20 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000544 | 3564 | 12 | 297 | PR-S05-02 | Prairie | 2025-02-20 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-000545 | 623 | 7 | 89 | HB-S16-03 | Harbor | 2025-02-20 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000546 | 10560 | 120 | 88 | HB-S04-02 | Harbor | 2025-02-20 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000547 | 648 | 6 | 108 | HB-S05-04 | Harbor | 2025-02-20 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000548 | 294 | 3 | 98 | BY-S02-01 | Bayou | 2025-02-20 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000549 | 6160 | 28 | 220 | BY-S23-03 | Bayou | 2025-02-20 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-000550 | 195 | 5 | 39 | HB-S08-05 | Harbor | 2025-02-20 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-000551 | 558 | 9 | 62 | PR-S19-04 | Prairie | 2025-02-20 | 21 | Animal | Transformer fuse | Forced | None
OE-25-000552 | 105719 | 1489 | 71 | HB-S18-01 | Harbor | 2025-02-21 | 6 | Weather - wind | Feeder recloser | Forced | None
OE-25-000553 | 13068 | 54 | 242 | PR-S09-04 | Prairie | 2025-02-21 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000554 | 648 | 9 | 72 | PR-S13-05 | Prairie | 2025-02-21 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000555 | 14469 | 53 | 273 | PR-S04-02 | Prairie | 2025-02-21 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000556 | 1820 | 7 | 260 | BY-S18-05 | Bayou | 2025-02-21 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-000557 | 244 | 2 | 122 | BY-S27-05 | Bayou | 2025-02-21 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-000558 | 1246 | 7 | 178 | CR-S27-01 | Crossroads | 2025-02-21 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000559 | 2030 | 14 | 145 | HB-S16-04 | Harbor | 2025-02-21 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-000560 | 250 | 2 | 125 | PR-S16-04 | Prairie | 2025-02-21 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000561 | 6422 | 26 | 247 | BY-S30-01 | Bayou | 2025-02-21 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000562 | 2364 | 12 | 197 | PR-S04-01 | Prairie | 2025-02-21 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000563 | 4125 | 11 | 375 | CR-S13-03 | Crossroads | 2025-02-21 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000564 | 822 | 6 | 137 | CR-S23-05 | Crossroads | 2025-02-21 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000565 | 1403 | 23 | 61 | CR-S31-03 | Crossroads | 2025-02-21 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-000566 | 945 | 7 | 135 | PR-S09-01 | Prairie | 2025-02-21 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000567 | 285 | 1 | 285 | PR-S09-03 | Prairie | 2025-02-22 | 6 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000568 | 1804 | 44 | 41 | PR-S03-03 | Prairie | 2025-02-22 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000569 | 2176 | 34 | 64 | BY-S26-02 | Bayou | 2025-02-22 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000570 | 7298 | 41 | 178 | PR-S10-03 | Prairie | 2025-02-22 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000571 | 137852 | 572 | 241 | PR-S10-02 | Prairie | 2025-02-22 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000572 | 612 | 3 | 204 | PR-S15-05 | Prairie | 2025-02-22 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000573 | 14355 | 99 | 145 | PR-S16-03 | Prairie | 2025-02-22 | 17 | Animal | Lateral fuse | Forced | None
OE-25-000574 | 2170 | 35 | 62 | BY-S26-02 | Bayou | 2025-02-22 | 18 | Animal | Lateral fuse | Forced | None
OE-25-000575 | 1310 | 10 | 131 | CR-S27-01 | Crossroads | 2025-02-22 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000576 | 66458 | 707 | 94 | CR-S24-04 | Crossroads | 2025-02-22 | 19 | Vegetation | Feeder recloser | Forced | None
OE-25-000577 | 476 | 4 | 119 | HB-S09-02 | Harbor | 2025-02-22 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-000578 | 1078 | 11 | 98 | BY-S29-04 | Bayou | 2025-02-22 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000579 | 19596 | 276 | 71 | HB-S13-02 | Harbor | 2025-02-22 | 23 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000580 | 5239 | 13 | 403 | BY-S10-01 | Bayou | 2025-02-23 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000581 | 1895 | 5 | 379 | PR-S09-02 | Prairie | 2025-02-23 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000582 | 12240 | 204 | 60 | HB-S19-03 | Harbor | 2025-02-23 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-000583 | 1416 | 6 | 236 | BY-S08-01 | Bayou | 2025-02-23 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000584 | 85 | 1 | 85 | CR-S20-02 | Crossroads | 2025-02-23 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-000585 | 648 | 12 | 54 | PR-S07-04 | Prairie | 2025-02-23 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000586 | 268 | 2 | 134 | HB-S03-03 | Harbor | 2025-02-23 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000587 | 28260 | 157 | 180 | PR-S13-03 | Prairie | 2025-02-23 | 13 | Vegetation | IGSD-isolated section | Forced | None
OE-25-000588 | 770 | 7 | 110 | CR-S27-03 | Crossroads | 2025-02-23 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000589 | 290 | 5 | 58 | CR-S16-02 | Crossroads | 2025-02-23 | 15 | Unknown | Transformer fuse | Forced | None
OE-25-000590 | 540 | 3 | 180 | CR-S26-03 | Crossroads | 2025-02-23 | 15 | Animal | Transformer fuse | Forced | None
OE-25-000591 | 2660 | 10 | 266 | HB-S09-02 | Harbor | 2025-02-23 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000592 | 11324 | 149 | 76 | CR-S16-02 | Crossroads | 2025-02-23 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000593 | 1400 | 14 | 100 | BY-S08-01 | Bayou | 2025-02-23 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000594 | 6264 | 116 | 54 | CR-S13-02 | Crossroads | 2025-02-24 | 0 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000595 | 1617 | 7 | 231 | CR-S26-04 | Crossroads | 2025-02-24 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000596 | 2840 | 10 | 284 | PR-S15-04 | Prairie | 2025-02-24 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000597 | 740 | 5 | 148 | PR-S03-01 | Prairie | 2025-02-24 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-000598 | 9516 | 156 | 61 | BY-S12-04 | Bayou | 2025-02-24 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-000599 | 2646 | 9 | 294 | BY-S26-06 | Bayou | 2025-02-24 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-000600 | 12390 | 354 | 35 | BY-S22-02 | Bayou | 2025-02-24 | 17 | Weather - lightning | Feeder recloser | Forced | None
OE-25-000601 | 2324 | 14 | 166 | CR-S05-01 | Crossroads | 2025-02-24 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000602 | 266 | 2 | 133 | BY-S09-01 | Bayou | 2025-02-24 | 18 | Unknown | Transformer fuse | Forced | None
OE-25-000603 | 5112 | 71 | 72 | CR-S04-01 | Crossroads | 2025-02-25 | 3 | Animal | Lateral fuse | Forced | None
OE-25-000604 | 60196 | 404 | 149 | CR-S20-01 | Crossroads | 2025-02-25 | 6 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-000605 | 3268 | 38 | 86 | BY-S16-05 | Bayou | 2025-02-25 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-000606 | 1520 | 8 | 190 | HB-S14-03 | Harbor | 2025-02-25 | 10 | Animal | Transformer fuse | Forced | None
OE-25-000607 | 1909 | 23 | 83 | CR-S26-02 | Crossroads | 2025-02-25 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-000608 | 28483 | 313 | 91 | PR-S20-01 | Prairie | 2025-02-25 | 13 | Unknown | Feeder recloser | Forced | None
OE-25-000609 | 4508 | 46 | 98 | HB-S02-02 | Harbor | 2025-02-25 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-000610 | 3738 | 42 | 89 | CR-S23-02 | Crossroads | 2025-02-25 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000611 | 5096 | 56 | 91 | PR-S18-03 | Prairie | 2025-02-26 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-25-000612 | 16014 | 314 | 51 | CR-S23-03 | Crossroads | 2025-02-26 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-000613 | 9936 | 108 | 92 | HB-S05-01 | Harbor | 2025-02-26 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000614 | 1568 | 14 | 112 | BY-S27-01 | Bayou | 2025-02-26 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000615 | 1360 | 4 | 340 | PR-S02-01 | Prairie | 2025-02-26 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-000616 | 50876 | 161 | 316 | PR-S20-04 | Prairie | 2025-02-26 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000617 | 2624 | 16 | 164 | HB-S16-03 | Harbor | 2025-02-27 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000618 | 6120 | 120 | 51 | BY-S03-01 | Bayou | 2025-02-27 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-000619 | 24530 | 110 | 223 | CR-S13-02 | Crossroads | 2025-02-27 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000620 | 6776 | 154 | 44 | BY-S16-01 | Bayou | 2025-02-27 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000621 | 549 | 9 | 61 | CR-S02-05 | Crossroads | 2025-02-27 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000622 | 5280 | 96 | 55 | BY-S26-03 | Bayou | 2025-02-27 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000623 | 1428 | 34 | 42 | BY-S19-02 | Bayou | 2025-02-27 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-000624 | 35334 | 151 | 234 | BY-S24-04 | Bayou | 2025-02-28 | 10 | Animal | Lateral fuse | Forced | None
OE-25-000625 | 6210 | 46 | 135 | CR-S23-04 | Crossroads | 2025-02-28 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000626 | 1030 | 10 | 103 | HB-S02-02 | Harbor | 2025-02-28 | 12 | Animal | Transformer fuse | Forced | None
OE-25-000627 | 224 | 7 | 32 | CR-S09-01 | Crossroads | 2025-02-28 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000628 | 10720 | 80 | 134 | BY-S26-02 | Bayou | 2025-02-28 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000629 | 4088 | 73 | 56 | CR-S20-04 | Crossroads | 2025-02-28 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-000630 | 858 | 26 | 33 | HB-S01-02 | Harbor | 2025-02-28 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-000631 | 8360 | 190 | 44 | PR-S03-03 | Prairie | 2025-02-28 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000632 | 29601 | 253 | 117 | CR-S12-02 | Crossroads | 2025-02-28 | 21 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000633 | 7035 | 105 | 67 | HB-S02-02 | Harbor | 2025-02-28 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000634 | 336 | 6 | 56 | CR-S31-02 | Crossroads | 2025-03-01 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000635 | 92 | 1 | 92 | CR-S10-01 | Crossroads | 2025-03-01 | 7 | Unknown | Transformer fuse | Forced | None
OE-25-000636 | 9320 | 233 | 40 | BY-S03-03 | Bayou | 2025-03-01 | 9 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000637 | 2262 | 29 | 78 | BY-S10-01 | Bayou | 2025-03-01 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-000638 | 17702 | 106 | 167 | PR-S01-02 | Prairie | 2025-03-01 | 13 | Animal | Lateral fuse | Forced | None
OE-25-000639 | 2366 | 13 | 182 | BY-S06-02 | Bayou | 2025-03-01 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-000640 | 19671 | 237 | 83 | BY-S23-01 | Bayou | 2025-03-01 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-000641 | 1133 | 11 | 103 | PR-S07-05 | Prairie | 2025-03-01 | 17 | Animal | Transformer fuse | Forced | None
OE-25-000642 | 43725 | 583 | 75 | HB-S19-02 | Harbor | 2025-03-01 | 20 | Vegetation | IGSD-isolated section | Forced | None
OE-25-000643 | 43845 | 555 | 79 | CR-S04-05 | Crossroads | 2025-03-01 | 21 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000644 | 67473 | 441 | 153 | BY-S07-06 | Bayou | 2025-03-01 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-000645 | 5104 | 88 | 58 | BY-S03-02 | Bayou | 2025-03-01 | 23 | Animal | Lateral fuse | Forced | None
OE-25-000646 | 266 | 2 | 133 | HB-S05-02 | Harbor | 2025-03-02 | 2 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000647 | 13200 | 165 | 80 | HB-S18-02 | Harbor | 2025-03-02 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-000648 | 22110 | 670 | 33 | BY-S06-03 | Bayou | 2025-03-02 | 9 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000649 | 798 | 6 | 133 | CR-S22-01 | Crossroads | 2025-03-02 | 10 | Unknown | Transformer fuse | Forced | None
OE-25-000650 | 2016 | 12 | 168 | HB-S17-02 | Harbor | 2025-03-02 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000651 | 603 | 3 | 201 | BY-S18-03 | Bayou | 2025-03-02 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000652 | 29295 | 465 | 63 | PR-S02-02 | Prairie | 2025-03-02 | 12 | Weather - wind | Feeder recloser | Forced | None
OE-25-000653 | 5712 | 56 | 102 | CR-S32-03 | Crossroads | 2025-03-02 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000654 | 1624 | 14 | 116 | PR-S07-03 | Prairie | 2025-03-02 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-000655 | 936 | 9 | 104 | CR-S04-06 | Crossroads | 2025-03-02 | 16 | Unknown | Transformer fuse | Forced | None
OE-25-000656 | 59736 | 786 | 76 | BY-S11-01 | Bayou | 2025-03-02 | 17 | Weather - lightning | Feeder recloser | Forced | None
OE-25-000657 | 1360 | 8 | 170 | CR-S30-03 | Crossroads | 2025-03-02 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000658 | 41268 | 543 | 76 | BY-S14-02 | Bayou | 2025-03-02 | 18 | Unknown | Feeder recloser | Forced | None
OE-25-000659 | 1687 | 7 | 241 | PR-S06-03 | Prairie | 2025-03-02 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-000660 | 1785 | 21 | 85 | PR-S17-01 | Prairie | 2025-03-03 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-000661 | 34380 | 191 | 180 | PR-S14-04 | Prairie | 2025-03-03 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000662 | 3350 | 25 | 134 | HB-S12-02 | Harbor | 2025-03-03 | 10 | Unknown | Lateral fuse | Forced | None
OE-25-000663 | 3064 | 8 | 383 | PR-S03-02 | Prairie | 2025-03-03 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-000664 | 1352 | 26 | 52 | CR-S26-05 | Crossroads | 2025-03-03 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000665 | 24257 | 191 | 127 | PR-S07-05 | Prairie | 2025-03-03 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000666 | 7150 | 65 | 110 | BY-S18-05 | Bayou | 2025-03-03 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-000667 | 4321 | 29 | 149 | BY-S11-02 | Bayou | 2025-03-03 | 21 | Animal | Lateral fuse | Forced | None
OE-25-000668 | 1218 | 7 | 174 | PR-S14-02 | Prairie | 2025-03-04 | 1 | Vegetation | Transformer fuse | Forced | None
OE-25-000669 | 960 | 4 | 240 | BY-S16-04 | Bayou | 2025-03-04 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-000670 | 21692 | 116 | 187 | CR-S22-01 | Crossroads | 2025-03-04 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000671 | 126 | 1 | 126 | CR-S30-05 | Crossroads | 2025-03-04 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000672 | 6981 | 179 | 39 | BY-S24-04 | Bayou | 2025-03-04 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000673 | 18795 | 179 | 105 | BY-S15-03 | Bayou | 2025-03-04 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-000674 | 1521 | 9 | 169 | PR-S09-04 | Prairie | 2025-03-04 | 19 | Weather - wind | Transformer fuse | Forced | None
OE-25-000675 | 684 | 3 | 228 | PR-S15-05 | Prairie | 2025-03-04 | 19 | Animal | Transformer fuse | Forced | None
OE-25-000676 | 21038 | 67 | 314 | CR-S15-01 | Crossroads | 2025-03-05 | 1 | Vegetation | Lateral fuse | Forced | None
OE-25-000677 | 8512 | 112 | 76 | PR-S01-05 | Prairie | 2025-03-05 | 6 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000678 | 702 | 6 | 117 | PR-S18-03 | Prairie | 2025-03-05 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-25-000679 | 5719 | 43 | 133 | CR-S01-04 | Crossroads | 2025-03-05 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000680 | 25380 | 108 | 235 | PR-S19-02 | Prairie | 2025-03-05 | 10 | Animal | Lateral fuse | Forced | None
OE-25-000681 | 313929 | 1661 | 189 | BY-S21-01 | Bayou | 2025-03-05 | 11 | Unknown | Substation breaker | Outside cause | None
OE-25-000682 | 23904 | 166 | 144 | PR-S09-03 | Prairie | 2025-03-05 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000683 | 266 | 2 | 133 | HB-S17-03 | Harbor | 2025-03-05 | 12 | Animal | Transformer fuse | Forced | None
OE-25-000684 | 16188 | 114 | 142 | PR-S05-03 | Prairie | 2025-03-05 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000685 | 2512 | 16 | 157 | CR-S06-03 | Crossroads | 2025-03-05 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000686 | 588 | 3 | 196 | PR-S15-04 | Prairie | 2025-03-05 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000687 | 1020 | 4 | 255 | PR-S19-01 | Prairie | 2025-03-05 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000688 | 1246 | 7 | 178 | BY-S19-01 | Bayou | 2025-03-05 | 18 | Unknown | Transformer fuse | Forced | None
OE-25-000689 | 2303 | 7 | 329 | BY-S12-03 | Bayou | 2025-03-05 | 20 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000690 | 106236 | 468 | 227 | BY-S15-05 | Bayou | 2025-03-05 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-000691 | 1372 | 14 | 98 | HB-S19-01 | Harbor | 2025-03-06 | 6 | Unknown | Transformer fuse | Forced | None
OE-25-000692 | 16170 | 66 | 245 | CR-S22-04 | Crossroads | 2025-03-06 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000693 | 10664 | 86 | 124 | CR-S24-03 | Crossroads | 2025-03-06 | 9 | Unknown | Lateral fuse | Forced | None
OE-25-000694 | 356 | 2 | 178 | PR-S01-03 | Prairie | 2025-03-06 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-000695 | 123 | 1 | 123 | CR-S10-02 | Crossroads | 2025-03-06 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000696 | 4644 | 54 | 86 | CR-S21-03 | Crossroads | 2025-03-06 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000697 | 1005 | 5 | 201 | PR-S13-01 | Prairie | 2025-03-06 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-000698 | 1920 | 12 | 160 | PR-S09-03 | Prairie | 2025-03-06 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-000699 | 10230 | 55 | 186 | PR-S10-02 | Prairie | 2025-03-06 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000700 | 63232 | 304 | 208 | BY-S12-02 | Bayou | 2025-03-06 | 13 | Animal | IGSD-isolated section | Forced | None
OE-25-000701 | 864 | 6 | 144 | HB-S19-02 | Harbor | 2025-03-06 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000702 | 501 | 3 | 167 | BY-S14-03 | Bayou | 2025-03-06 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000703 | 37400 | 374 | 100 | HB-S02-01 | Harbor | 2025-03-06 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000704 | 497 | 7 | 71 | CR-S06-01 | Crossroads | 2025-03-06 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-000705 | 22374 | 198 | 113 | CR-S30-07 | Crossroads | 2025-03-06 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000706 | 44 | 1 | 44 | CR-S11-01 | Crossroads | 2025-03-06 | 23 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000707 | 555 | 3 | 185 | CR-S04-01 | Crossroads | 2025-03-07 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000708 | 24250 | 250 | 97 | CR-S24-02 | Crossroads | 2025-03-07 | 11 | Animal | Lateral fuse | Forced | None
OE-25-000709 | 2190 | 10 | 219 | CR-S23-04 | Crossroads | 2025-03-07 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000710 | 510 | 10 | 51 | HB-S14-04 | Harbor | 2025-03-07 | 12 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000711 | 64344 | 168 | 383 | PR-S12-01 | Prairie | 2025-03-07 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-000712 | 1640 | 40 | 41 | PR-S01-01 | Prairie | 2025-03-07 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-000713 | 1744 | 8 | 218 | CR-S02-03 | Crossroads | 2025-03-07 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000714 | 34572 | 516 | 67 | PR-S03-01 | Prairie | 2025-03-07 | 22 | Weather - lightning | Feeder recloser | Forced | None
OE-25-000715 | 804 | 3 | 268 | BY-S03-02 | Bayou | 2025-03-08 | 3 | Weather - wind | Transformer fuse | Forced | None
OE-25-000716 | 576 | 12 | 48 | BY-S24-03 | Bayou | 2025-03-08 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000717 | 21983 | 89 | 247 | CR-S16-05 | Crossroads | 2025-03-08 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000718 | 4860 | 90 | 54 | BY-S03-02 | Bayou | 2025-03-08 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-000719 | 702 | 13 | 54 | CR-S04-01 | Crossroads | 2025-03-08 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000720 | 931 | 7 | 133 | CR-S04-04 | Crossroads | 2025-03-08 | 16 | Animal | Transformer fuse | Forced | None
OE-25-000721 | 2421 | 9 | 269 | CR-S05-02 | Crossroads | 2025-03-08 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000722 | 11400 | 95 | 120 | BY-S26-04 | Bayou | 2025-03-08 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000723 | 7791 | 159 | 49 | CR-S15-02 | Crossroads | 2025-03-08 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000724 | 546 | 6 | 91 | BY-S11-01 | Bayou | 2025-03-08 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000725 | 11750 | 94 | 125 | HB-S02-01 | Harbor | 2025-03-08 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-000726 | 24747 | 73 | 339 | PR-S19-05 | Prairie | 2025-03-08 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000727 | 1393 | 7 | 199 | CR-S25-01 | Crossroads | 2025-03-08 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000728 | 1152 | 24 | 48 | HB-S05-02 | Harbor | 2025-03-09 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000729 | 623 | 7 | 89 | CR-S30-05 | Crossroads | 2025-03-09 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-000730 | 9730 | 70 | 139 | BY-S23-02 | Bayou | 2025-03-09 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000731 | 64664 | 1096 | 59 | HB-S17-03 | Harbor | 2025-03-09 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000732 | 7171 | 101 | 71 | HB-S12-03 | Harbor | 2025-03-09 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-000733 | 8880 | 111 | 80 | BY-S03-02 | Bayou | 2025-03-09 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-000734 | 72525 | 967 | 75 | CR-S30-07 | Crossroads | 2025-03-09 | 14 | Vehicle or public | Feeder recloser | Forced | None
OE-25-000735 | 1692 | 9 | 188 | BY-S06-01 | Bayou | 2025-03-09 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000736 | 90 | 1 | 90 | CR-S06-02 | Crossroads | 2025-03-09 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000737 | 23807 | 179 | 133 | BY-S04-01 | Bayou | 2025-03-09 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000738 | 3618 | 67 | 54 | CR-S09-01 | Crossroads | 2025-03-09 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000739 | 1860 | 20 | 93 | PR-S11-02 | Prairie | 2025-03-09 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000740 | 968 | 8 | 121 | CR-S13-04 | Crossroads | 2025-03-09 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000741 | 550 | 5 | 110 | CR-S01-01 | Crossroads | 2025-03-09 | 22 | Weather - wind | Transformer fuse | Forced | None
OE-25-000742 | 11900 | 119 | 100 | BY-S13-06 | Bayou | 2025-03-10 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-25-000743 | 12544 | 28 | 448 | CR-S14-05 | Crossroads | 2025-03-10 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000744 | 39237 | 451 | 87 | CR-S27-03 | Crossroads | 2025-03-10 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000745 | 3808 | 34 | 112 | HB-S02-02 | Harbor | 2025-03-10 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000746 | 960 | 8 | 120 | PR-S10-01 | Prairie | 2025-03-10 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000747 | 3024 | 54 | 56 | HB-S15-02 | Harbor | 2025-03-10 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000748 | 6968 | 67 | 104 | BY-S07-01 | Bayou | 2025-03-10 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000749 | 2497 | 11 | 227 | CR-S28-01 | Crossroads | 2025-03-10 | 13 | Animal | Transformer fuse | Forced | None
OE-25-000750 | 482 | 2 | 241 | BY-S12-04 | Bayou | 2025-03-10 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000751 | 690 | 5 | 138 | HB-S06-01 | Harbor | 2025-03-10 | 15 | Animal | Transformer fuse | Forced | None
OE-25-000752 | 10965 | 85 | 129 | PR-S01-03 | Prairie | 2025-03-10 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000753 | 3003 | 11 | 273 | BY-S22-03 | Bayou | 2025-03-10 | 16 | Animal | Transformer fuse | Forced | None
OE-25-000754 | 81060 | 1351 | 60 | BY-S13-06 | Bayou | 2025-03-10 | 21 | Vegetation | Feeder recloser | Forced | None
OE-25-000755 | 15708 | 84 | 187 | BY-S19-02 | Bayou | 2025-03-10 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-000756 | 408 | 3 | 136 | BY-S27-06 | Bayou | 2025-03-10 | 23 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000757 | 3330 | 45 | 74 | HB-S08-03 | Harbor | 2025-03-11 | 2 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000758 | 6254 | 59 | 106 | PR-S10-03 | Prairie | 2025-03-11 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000759 | 84480 | 1280 | 66 | CR-S25-03 | Crossroads | 2025-03-11 | 8 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000760 | 4017 | 39 | 103 | PR-S05-02 | Prairie | 2025-03-11 | 8 | Unknown | Lateral fuse | Forced | None
OE-25-000761 | 10032 | 152 | 66 | BY-S14-03 | Bayou | 2025-03-11 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-000762 | 297 | 3 | 99 | BY-S29-01 | Bayou | 2025-03-11 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000763 | 1530 | 9 | 170 | CR-S02-05 | Crossroads | 2025-03-11 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000764 | 168 | 3 | 56 | HB-S08-04 | Harbor | 2025-03-11 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000765 | 12012 | 143 | 84 | CR-S30-06 | Crossroads | 2025-03-11 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000766 | 1130 | 10 | 113 | BY-S21-04 | Bayou | 2025-03-11 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000767 | 139050 | 927 | 150 | BY-S30-01 | Bayou | 2025-03-11 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-000768 | 16684 | 97 | 172 | HB-S08-01 | Harbor | 2025-03-11 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-000769 | 2030 | 14 | 145 | PR-S20-03 | Prairie | 2025-03-11 | 23 | Weather - wind | Transformer fuse | Forced | None
OE-25-000770 | 6000 | 48 | 125 | PR-S03-06 | Prairie | 2025-03-12 | 1 | Vegetation | Lateral fuse | Forced | None
OE-25-000771 | 3400 | 50 | 68 | BY-S21-04 | Bayou | 2025-03-12 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000772 | 1530 | 17 | 90 | PR-S18-04 | Prairie | 2025-03-12 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000773 | 3507 | 21 | 167 | CR-S07-07 | Crossroads | 2025-03-12 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000774 | 2055 | 15 | 137 | CR-S15-02 | Crossroads | 2025-03-12 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000775 | 20293 | 91 | 223 | BY-S19-02 | Bayou | 2025-03-12 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000776 | 16362 | 54 | 303 | BY-S19-04 | Bayou | 2025-03-12 | 12 | Animal | Lateral fuse | Forced | None
OE-25-000777 | 20184 | 174 | 116 | CR-S10-02 | Crossroads | 2025-03-12 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000778 | 11340 | 84 | 135 | BY-S29-04 | Bayou | 2025-03-12 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000779 | 416512 | 3254 | 128 | CR-S14-02 | Crossroads | 2025-03-12 | 15 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000780 | 138573 | 1557 | 89 | HB-S05-06 | Harbor | 2025-03-13 | 8 | Vegetation | Feeder recloser | Forced | None
OE-25-000781 | 17935 | 85 | 211 | BY-S27-02 | Bayou | 2025-03-13 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-25-000782 | 7840 | 70 | 112 | BY-S27-05 | Bayou | 2025-03-13 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-000783 | 242 | 2 | 121 | CR-S14-01 | Crossroads | 2025-03-13 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000784 | 276 | 4 | 69 | BY-S07-06 | Bayou | 2025-03-13 | 13 | Animal | Transformer fuse | Forced | None
OE-25-000785 | 8410 | 58 | 145 | BY-S18-06 | Bayou | 2025-03-13 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-000786 | 3010 | 35 | 86 | BY-S23-02 | Bayou | 2025-03-13 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000787 | 2856 | 34 | 84 | HB-S12-01 | Harbor | 2025-03-13 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000788 | 1456 | 8 | 182 | BY-S10-01 | Bayou | 2025-03-13 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-000789 | 8487 | 123 | 69 | BY-S18-07 | Bayou | 2025-03-13 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-000790 | 252 | 2 | 126 | BY-S18-03 | Bayou | 2025-03-13 | 20 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000791 | 17280 | 480 | 36 | BY-S16-02 | Bayou | 2025-03-13 | 22 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000792 | 2911 | 41 | 71 | CR-S04-01 | Crossroads | 2025-03-14 | 9 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000793 | 10764 | 468 | 23 | CR-S30-06 | Crossroads | 2025-03-14 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000794 | 8930 | 190 | 47 | CR-S05-05 | Crossroads | 2025-03-14 | 12 | Vehicle or public | IGSD-isolated section | Forced | None
OE-25-000795 | 8325 | 37 | 225 | CR-S20-01 | Crossroads | 2025-03-14 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000796 | 2093 | 13 | 161 | BY-S15-04 | Bayou | 2025-03-14 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000797 | 9052 | 73 | 124 | BY-S21-02 | Bayou | 2025-03-14 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-000798 | 21964 | 68 | 323 | CR-S05-05 | Crossroads | 2025-03-14 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000799 | 296 | 2 | 148 | PR-S07-03 | Prairie | 2025-03-14 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-000800 | 1092 | 26 | 42 | BY-S29-05 | Bayou | 2025-03-14 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000801 | 194 | 2 | 97 | HB-S18-01 | Harbor | 2025-03-14 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-000802 | 2000 | 8 | 250 | PR-S03-04 | Prairie | 2025-03-14 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000803 | 385 | 7 | 55 | CR-S07-01 | Crossroads | 2025-03-14 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000804 | 22960 | 410 | 56 | BY-S14-03 | Bayou | 2025-03-14 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000805 | 45264 | 943 | 48 | BY-S27-03 | Bayou | 2025-03-14 | 19 | Vegetation | Substation breaker | Forced | None
OE-25-000806 | 1014 | 6 | 169 | PR-S08-03 | Prairie | 2025-03-14 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000807 | 600 | 3 | 200 | BY-S29-01 | Bayou | 2025-03-15 | 7 | Animal | Transformer fuse | Forced | None
OE-25-000808 | 74750 | 115 | 650 | PR-S11-02 | Prairie | 2025-03-15 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000809 | 12120 | 60 | 202 | BY-S24-02 | Bayou | 2025-03-15 | 8 | Unknown | Lateral fuse | Forced | None
OE-25-000810 | 3550 | 50 | 71 | PR-S01-03 | Prairie | 2025-03-15 | 8 | Animal | Lateral fuse | Forced | None
OE-25-000811 | 360 | 3 | 120 | PR-S06-03 | Prairie | 2025-03-15 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000812 | 19552 | 94 | 208 | BY-S16-04 | Bayou | 2025-03-15 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-000813 | 570 | 15 | 38 | BY-S08-03 | Bayou | 2025-03-15 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000814 | 330 | 5 | 66 | CR-S23-01 | Crossroads | 2025-03-15 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-000815 | 3200 | 25 | 128 | BY-S10-03 | Bayou | 2025-03-15 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-000816 | 15470 | 119 | 130 | PR-S10-03 | Prairie | 2025-03-15 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-000817 | 2646 | 21 | 126 | PR-S04-01 | Prairie | 2025-03-15 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-000818 | 510 | 3 | 170 | CR-S18-05 | Crossroads | 2025-03-15 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000819 | 4752 | 44 | 108 | BY-S28-03 | Bayou | 2025-03-15 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000820 | 10010 | 77 | 130 | BY-S08-02 | Bayou | 2025-03-15 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-000821 | 2119 | 13 | 163 | BY-S24-04 | Bayou | 2025-03-15 | 20 | Animal | Transformer fuse | Forced | None
OE-25-000822 | 676 | 13 | 52 | CR-S32-01 | Crossroads | 2025-03-16 | 2 | Vegetation | Transformer fuse | Forced | None
OE-25-000823 | 53690 | 413 | 130 | BY-S24-03 | Bayou | 2025-03-16 | 4 | Animal | Feeder recloser | Forced | None
OE-25-000824 | 5640 | 60 | 94 | CR-S26-02 | Crossroads | 2025-03-16 | 8 | Animal | Lateral fuse | Forced | None
OE-25-000825 | 3712 | 58 | 64 | CR-S04-03 | Crossroads | 2025-03-16 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000826 | 9108 | 69 | 132 | CR-S25-06 | Crossroads | 2025-03-16 | 9 | Animal | Lateral fuse | Forced | None
OE-25-000827 | 2639 | 13 | 203 | PR-S20-01 | Prairie | 2025-03-16 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-25-000828 | 1974 | 14 | 141 | BY-S13-06 | Bayou | 2025-03-16 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000829 | 12874 | 82 | 157 | CR-S32-04 | Crossroads | 2025-03-16 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000830 | 1152 | 16 | 72 | HB-S10-02 | Harbor | 2025-03-16 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-000831 | 1078 | 11 | 98 | HB-S17-02 | Harbor | 2025-03-16 | 13 | Animal | Transformer fuse | Forced | None
OE-25-000832 | 1820 | 35 | 52 | CR-S26-05 | Crossroads | 2025-03-16 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-000833 | 3240 | 40 | 81 | PR-S03-01 | Prairie | 2025-03-16 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000834 | 88 | 1 | 88 | BY-S07-02 | Bayou | 2025-03-17 | 5 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000835 | 7905 | 93 | 85 | HB-S09-05 | Harbor | 2025-03-17 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-000836 | 8384 | 32 | 262 | CR-S05-01 | Crossroads | 2025-03-17 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000837 | 7315 | 55 | 133 | PR-S01-05 | Prairie | 2025-03-17 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000838 | 2277 | 11 | 207 | CR-S22-02 | Crossroads | 2025-03-17 | 12 | Animal | Transformer fuse | Forced | None
OE-25-000839 | 2100 | 10 | 210 | PR-S19-01 | Prairie | 2025-03-17 | 12 | Animal | Transformer fuse | Forced | None
OE-25-000840 | 1810 | 10 | 181 | CR-S25-05 | Crossroads | 2025-03-17 | 14 | Animal | Transformer fuse | Forced | None
OE-25-000841 | 9672 | 52 | 186 | PR-S03-04 | Prairie | 2025-03-17 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000842 | 24930 | 554 | 45 | BY-S25-04 | Bayou | 2025-03-17 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000843 | 1335 | 5 | 267 | PR-S09-03 | Prairie | 2025-03-17 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000844 | 648 | 6 | 108 | BY-S27-01 | Bayou | 2025-03-17 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000845 | 10260 | 270 | 38 | HB-S09-01 | Harbor | 2025-03-17 | 21 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-000846 | 630 | 7 | 90 | CR-S04-06 | Crossroads | 2025-03-17 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000847 | 210 | 2 | 105 | BY-S03-03 | Bayou | 2025-03-18 | 3 | Unknown | Transformer fuse | Forced | None
OE-25-000848 | 396 | 2 | 198 | PR-S18-04 | Prairie | 2025-03-18 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-000849 | 2625 | 15 | 175 | CR-S06-03 | Crossroads | 2025-03-18 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000850 | 13737 | 57 | 241 | BY-S05-01 | Bayou | 2025-03-18 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000851 | 14196 | 91 | 156 | CR-S14-02 | Crossroads | 2025-03-18 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000852 | 756 | 3 | 252 | BY-S27-04 | Bayou | 2025-03-18 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000853 | 37638 | 123 | 306 | BY-S18-07 | Bayou | 2025-03-18 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000854 | 172 | 2 | 86 | CR-S22-01 | Crossroads | 2025-03-18 | 15 | Animal | Transformer fuse | Forced | None
OE-25-000855 | 18088 | 476 | 38 | CR-S24-02 | Crossroads | 2025-03-18 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-000856 | 26503 | 1559 | 17 | HB-S02-01 | Harbor | 2025-03-18 | 17 | Weather - lightning | Feeder recloser | Forced | None
OE-25-000857 | 987 | 7 | 141 | BY-S20-01 | Bayou | 2025-03-18 | 19 | Weather - wind | Transformer fuse | Forced | None
OE-25-000858 | 138753 | 1713 | 81 | HB-S16-01 | Harbor | 2025-03-18 | 21 | Unknown | Substation breaker | Outside cause | None
OE-25-000859 | 6864 | 13 | 528 | BY-S07-03 | Bayou | 2025-03-19 | 3 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000860 | 29684 | 164 | 181 | BY-S15-04 | Bayou | 2025-03-19 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000861 | 8694 | 46 | 189 | PR-S09-04 | Prairie | 2025-03-19 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000862 | 75850 | 1517 | 50 | CR-S03-01 | Crossroads | 2025-03-19 | 11 | Equipment - overhead | Substation breaker | Forced | None
OE-25-000863 | 576 | 8 | 72 | CR-S10-03 | Crossroads | 2025-03-19 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-000864 | 53600 | 1072 | 50 | CR-S30-05 | Crossroads | 2025-03-19 | 12 | Equipment - underground | Substation breaker | Forced | None
OE-25-000865 | 1617 | 11 | 147 | PR-S19-03 | Prairie | 2025-03-19 | 12 | Unknown | Transformer fuse | Forced | None
OE-25-000866 | 532 | 2 | 266 | BY-S15-06 | Bayou | 2025-03-19 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000867 | 26425 | 175 | 151 | CR-S18-01 | Crossroads | 2025-03-19 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000868 | 1470 | 35 | 42 | HB-S07-04 | Harbor | 2025-03-19 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000869 | 33972 | 228 | 149 | BY-S05-03 | Bayou | 2025-03-19 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-000870 | 1582 | 14 | 113 | BY-S22-03 | Bayou | 2025-03-19 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-000871 | 13680 | 1140 | 12 | PR-S03-02 | Prairie | 2025-03-19 | 14 | Unknown | Substation breaker | Outside cause | None
OE-25-000872 | 1800 | 9 | 200 | PR-S20-03 | Prairie | 2025-03-19 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000873 | 1840 | 40 | 46 | CR-S23-02 | Crossroads | 2025-03-19 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-000874 | 27120 | 113 | 240 | HB-S05-04 | Harbor | 2025-03-19 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-000875 | 60168 | 654 | 92 | BY-S25-04 | Bayou | 2025-03-19 | 19 | Vegetation | Feeder recloser | Forced | None
OE-25-000876 | 6251 | 47 | 133 | CR-S06-03 | Crossroads | 2025-03-19 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000877 | 8400 | 105 | 80 | CR-S15-01 | Crossroads | 2025-03-19 | 20 | Animal | Lateral fuse | Forced | None
OE-25-000878 | 78 | 1 | 78 | PR-S07-06 | Prairie | 2025-03-19 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000879 | 1690 | 26 | 65 | HB-S15-01 | Harbor | 2025-03-19 | 21 | Vehicle or public | Lateral fuse | Forced | None
OE-25-000880 | 1396 | 4 | 349 | PR-S19-04 | Prairie | 2025-03-19 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000881 | 43400 | 700 | 62 | CR-S05-06 | Crossroads | 2025-03-19 | 23 | Vegetation | Substation breaker | Forced | None
OE-25-000882 | 3827 | 43 | 89 | HB-S02-02 | Harbor | 2025-03-20 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000883 | 2090 | 11 | 190 | CR-S24-03 | Crossroads | 2025-03-20 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000884 | 2520 | 14 | 180 | PR-S03-01 | Prairie | 2025-03-20 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-25-000885 | 2340 | 12 | 195 | CR-S09-01 | Crossroads | 2025-03-20 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000886 | 2700 | 30 | 90 | CR-S26-06 | Crossroads | 2025-03-20 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000887 | 5940 | 54 | 110 | HB-S20-01 | Harbor | 2025-03-20 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000888 | 38544 | 88 | 438 | PR-S07-03 | Prairie | 2025-03-20 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000889 | 9790 | 110 | 89 | CR-S02-04 | Crossroads | 2025-03-20 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000890 | 707 | 7 | 101 | CR-S29-03 | Crossroads | 2025-03-20 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000891 | 946 | 11 | 86 | CR-S26-02 | Crossroads | 2025-03-20 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000892 | 17342 | 58 | 299 | PR-S08-02 | Prairie | 2025-03-20 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000893 | 138 | 1 | 138 | PR-S12-03 | Prairie | 2025-03-20 | 16 | Animal | Transformer fuse | Forced | None
OE-25-000894 | 1120 | 8 | 140 | PR-S07-03 | Prairie | 2025-03-20 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000895 | 501 | 3 | 167 | PR-S13-02 | Prairie | 2025-03-20 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-000896 | 1836 | 12 | 153 | PR-S19-02 | Prairie | 2025-03-21 | 3 | Vegetation | Transformer fuse | Forced | None
OE-25-000897 | 39960 | 370 | 108 | HB-S17-02 | Harbor | 2025-03-21 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000898 | 9400 | 50 | 188 | BY-S16-04 | Bayou | 2025-03-21 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000899 | 1944 | 12 | 162 | BY-S10-02 | Bayou | 2025-03-21 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000900 | 5780 | 85 | 68 | BY-S29-01 | Bayou | 2025-03-21 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000901 | 4081 | 11 | 371 | CR-S05-06 | Crossroads | 2025-03-21 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000902 | 147 | 1 | 147 | CR-S23-05 | Crossroads | 2025-03-21 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-000903 | 12160 | 76 | 160 | HB-S19-01 | Harbor | 2025-03-22 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000904 | 5875 | 47 | 125 | PR-S10-02 | Prairie | 2025-03-22 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000905 | 434 | 2 | 217 | PR-S19-03 | Prairie | 2025-03-22 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-25-000906 | 68503 | 1123 | 61 | BY-S24-04 | Bayou | 2025-03-22 | 9 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-000907 | 1264 | 8 | 158 | BY-S15-02 | Bayou | 2025-03-22 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000908 | 1144 | 11 | 104 | BY-S21-01 | Bayou | 2025-03-22 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-000909 | 3354 | 43 | 78 | CR-S13-04 | Crossroads | 2025-03-22 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000910 | 1596 | 21 | 76 | BY-S25-02 | Bayou | 2025-03-22 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000911 | 490 | 10 | 49 | BY-S04-03 | Bayou | 2025-03-22 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-000912 | 6437 | 41 | 157 | CR-S06-02 | Crossroads | 2025-03-22 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000913 | 672 | 4 | 168 | BY-S07-02 | Bayou | 2025-03-22 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000914 | 248 | 2 | 124 | CR-S17-01 | Crossroads | 2025-03-22 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000915 | 50652 | 402 | 126 | BY-S25-04 | Bayou | 2025-03-22 | 20 | Vegetation | Feeder recloser | Forced | None
OE-25-000916 | 1308 | 12 | 109 | HB-S02-01 | Harbor | 2025-03-22 | 20 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000917 | 4675 | 85 | 55 | HB-S05-04 | Harbor | 2025-03-23 | 1 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000918 | 1075 | 5 | 215 | PR-S13-01 | Prairie | 2025-03-23 | 1 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000919 | 71125 | 569 | 125 | PR-S03-02 | Prairie | 2025-03-23 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000920 | 77273 | 581 | 133 | CR-S03-03 | Crossroads | 2025-03-23 | 5 | Weather - wind | Feeder recloser | Forced | None
OE-25-000921 | 10716 | 141 | 76 | CR-S14-03 | Crossroads | 2025-03-23 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000922 | 489 | 3 | 163 | PR-S15-01 | Prairie | 2025-03-23 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000923 | 1495 | 5 | 299 | BY-S20-02 | Bayou | 2025-03-23 | 17 | Animal | Transformer fuse | Forced | None
OE-25-000924 | 20090 | 245 | 82 | CR-S04-05 | Crossroads | 2025-03-23 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000925 | 66924 | 429 | 156 | CR-S26-04 | Crossroads | 2025-03-23 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000926 | 8480 | 40 | 212 | PR-S09-01 | Prairie | 2025-03-23 | 19 | Unknown | Lateral fuse | Forced | None
OE-25-000927 | 1050 | 10 | 105 | BY-S16-02 | Bayou | 2025-03-23 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-000928 | 86346 | 1053 | 82 | BY-S09-02 | Bayou | 2025-03-24 | 5 | Animal | Substation breaker | Forced | None
OE-25-000929 | 2028 | 12 | 169 | BY-S29-03 | Bayou | 2025-03-24 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-000930 | 44612 | 587 | 76 | BY-S01-01 | Bayou | 2025-03-24 | 8 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000931 | 21158 | 142 | 149 | PR-S10-03 | Prairie | 2025-03-24 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000932 | 11438 | 38 | 301 | PR-S01-04 | Prairie | 2025-03-24 | 9 | Unknown | Lateral fuse | Forced | None
OE-25-000933 | 424 | 2 | 212 | PR-S15-06 | Prairie | 2025-03-24 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-000934 | 11280 | 47 | 240 | BY-S23-05 | Bayou | 2025-03-24 | 10 | Unknown | Lateral fuse | Forced | None
OE-25-000935 | 820 | 4 | 205 | BY-S12-04 | Bayou | 2025-03-24 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-000936 | 302 | 2 | 151 | BY-S04-01 | Bayou | 2025-03-24 | 15 | Animal | Transformer fuse | Forced | None
OE-25-000937 | 77982 | 1902 | 41 | CR-S20-05 | Crossroads | 2025-03-24 | 15 | Unknown | Substation breaker | Outside cause | None
OE-25-000938 | 785 | 5 | 157 | PR-S01-06 | Prairie | 2025-03-24 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000939 | 75990 | 510 | 149 | CR-S22-04 | Crossroads | 2025-03-24 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000940 | 37400 | 550 | 68 | CR-S14-04 | Crossroads | 2025-03-24 | 20 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000941 | 2771 | 17 | 163 | HB-S08-02 | Harbor | 2025-03-24 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000942 | 7175 | 25 | 287 | HB-S08-04 | Harbor | 2025-03-24 | 21 | Animal | Lateral fuse | Forced | None
OE-25-000943 | 37062 | 522 | 71 | PR-S08-01 | Prairie | 2025-03-25 | 0 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000944 | 1386 | 11 | 126 | CR-S12-01 | Crossroads | 2025-03-25 | 4 | Equipment - underground | Transformer fuse | Forced | None
OE-25-000945 | 64944 | 984 | 66 | BY-S15-01 | Bayou | 2025-03-25 | 5 | Vegetation | Feeder recloser | Forced | None
OE-25-000946 | 12878 | 94 | 137 | CR-S19-02 | Crossroads | 2025-03-25 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000947 | 18920 | 86 | 220 | BY-S25-01 | Bayou | 2025-03-25 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000948 | 8176 | 146 | 56 | PR-S13-01 | Prairie | 2025-03-25 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000949 | 4251 | 39 | 109 | BY-S08-02 | Bayou | 2025-03-25 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000950 | 24640 | 112 | 220 | PR-S16-05 | Prairie | 2025-03-25 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-000951 | 801 | 9 | 89 | CR-S19-04 | Crossroads | 2025-03-25 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000952 | 2090 | 38 | 55 | BY-S25-02 | Bayou | 2025-03-25 | 13 | Animal | Lateral fuse | Forced | None
OE-25-000953 | 35188 | 926 | 38 | BY-S21-03 | Bayou | 2025-03-25 | 14 | Vehicle or public | Feeder recloser | Forced | None
OE-25-000954 | 1666 | 14 | 119 | HB-S12-03 | Harbor | 2025-03-25 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000955 | 52275 | 425 | 123 | PR-S15-06 | Prairie | 2025-03-25 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000956 | 72297 | 831 | 87 | HB-S19-04 | Harbor | 2025-03-25 | 15 | Weather - lightning | Feeder recloser | Forced | None
OE-25-000957 | 222 | 1 | 222 | BY-S23-01 | Bayou | 2025-03-25 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-000958 | 730 | 5 | 146 | HB-S07-01 | Harbor | 2025-03-25 | 16 | Unknown | Transformer fuse | Forced | None
OE-25-000959 | 32100 | 535 | 60 | CR-S01-01 | Crossroads | 2025-03-25 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-000960 | 8540 | 61 | 140 | CR-S31-03 | Crossroads | 2025-03-25 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-000961 | 3008 | 32 | 94 | PR-S11-01 | Prairie | 2025-03-25 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000962 | 2160 | 6 | 360 | PR-S08-01 | Prairie | 2025-03-26 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000963 | 10224 | 71 | 144 | PR-S11-01 | Prairie | 2025-03-26 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000964 | 12180 | 145 | 84 | BY-S07-03 | Bayou | 2025-03-26 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-000965 | 32899 | 197 | 167 | CR-S17-03 | Crossroads | 2025-03-26 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000966 | 6798 | 33 | 206 | CR-S32-01 | Crossroads | 2025-03-26 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-000967 | 64893 | 669 | 97 | PR-S15-06 | Prairie | 2025-03-26 | 8 | Weather - lightning | Feeder recloser | Forced | None
OE-25-000968 | 4185 | 45 | 93 | BY-S25-01 | Bayou | 2025-03-26 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-000969 | 684 | 6 | 114 | BY-S29-01 | Bayou | 2025-03-26 | 11 | Animal | Transformer fuse | Forced | None
OE-25-000970 | 8060 | 31 | 260 | BY-S12-03 | Bayou | 2025-03-26 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-000971 | 4788 | 57 | 84 | BY-S22-03 | Bayou | 2025-03-26 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000972 | 2581 | 29 | 89 | CR-S04-01 | Crossroads | 2025-03-26 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000973 | 46144 | 412 | 112 | PR-S14-03 | Prairie | 2025-03-26 | 14 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-000974 | 2947 | 7 | 421 | PR-S16-05 | Prairie | 2025-03-26 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000975 | 426 | 2 | 213 | BY-S02-02 | Bayou | 2025-03-26 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000976 | 1325 | 5 | 265 | BY-S29-01 | Bayou | 2025-03-26 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000977 | 1155 | 7 | 165 | HB-S18-03 | Harbor | 2025-03-26 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-000978 | 1353 | 11 | 123 | BY-S08-03 | Bayou | 2025-03-26 | 17 | Unknown | Transformer fuse | Forced | None
OE-25-000979 | 31150 | 175 | 178 | PR-S18-01 | Prairie | 2025-03-26 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-000980 | 540 | 4 | 135 | CR-S14-04 | Crossroads | 2025-03-27 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000981 | 1179 | 9 | 131 | PR-S14-01 | Prairie | 2025-03-27 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-000982 | 3950 | 25 | 158 | BY-S12-02 | Bayou | 2025-03-27 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-25-000983 | 424 | 4 | 106 | BY-S16-02 | Bayou | 2025-03-27 | 7 | Animal | Transformer fuse | Forced | None
OE-25-000984 | 2464 | 14 | 176 | CR-S30-01 | Crossroads | 2025-03-27 | 7 | Animal | Transformer fuse | Forced | None
OE-25-000985 | 89675 | 1055 | 85 | BY-S23-01 | Bayou | 2025-03-27 | 9 | Animal | Feeder recloser | Forced | None
OE-25-000986 | 12636 | 162 | 78 | PR-S16-03 | Prairie | 2025-03-27 | 9 | Unknown | Lateral fuse | Forced | None
OE-25-000987 | 6192 | 72 | 86 | BY-S09-03 | Bayou | 2025-03-27 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000988 | 204 | 3 | 68 | CR-S01-04 | Crossroads | 2025-03-27 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000989 | 5842 | 46 | 127 | CR-S22-02 | Crossroads | 2025-03-27 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000990 | 12834 | 69 | 186 | CR-S30-03 | Crossroads | 2025-03-27 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-000991 | 273 | 3 | 91 | BY-S06-02 | Bayou | 2025-03-27 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-000992 | 42480 | 354 | 120 | PR-S15-02 | Prairie | 2025-03-27 | 13 | Vegetation | IGSD-isolated section | Forced | None
OE-25-000993 | 23950 | 479 | 50 | BY-S26-05 | Bayou | 2025-03-27 | 18 | Weather - wind | Feeder recloser | Forced | None
OE-25-000994 | 1705 | 11 | 155 | BY-S28-02 | Bayou | 2025-03-27 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-25-000995 | 3325 | 25 | 133 | CR-S01-03 | Crossroads | 2025-03-27 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-000996 | 1503 | 9 | 167 | PR-S20-03 | Prairie | 2025-03-27 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-25-000997 | 44515 | 145 | 307 | CR-S21-02 | Crossroads | 2025-03-27 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-25-000998 | 2030 | 7 | 290 | CR-S13-04 | Crossroads | 2025-03-28 | 1 | Weather - lightning | Transformer fuse | Forced | None
OE-25-000999 | 1170 | 9 | 130 | HB-S10-01 | Harbor | 2025-03-28 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001000 | 5511 | 33 | 167 | BY-S05-01 | Bayou | 2025-03-28 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001001 | 1908 | 18 | 106 | CR-S14-02 | Crossroads | 2025-03-28 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001002 | 43680 | 168 | 260 | PR-S02-03 | Prairie | 2025-03-28 | 10 | Animal | Lateral fuse | Forced | None
OE-25-001003 | 5863 | 13 | 451 | PR-S05-03 | Prairie | 2025-03-28 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001004 | 912 | 24 | 38 | BY-S14-02 | Bayou | 2025-03-28 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-001005 | 8190 | 30 | 273 | BY-S30-02 | Bayou | 2025-03-28 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-001006 | 1105 | 13 | 85 | CR-S08-05 | Crossroads | 2025-03-28 | 13 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001007 | 60588 | 748 | 81 | CR-S19-02 | Crossroads | 2025-03-28 | 14 | Weather - wind | Feeder recloser | Forced | None
OE-25-001008 | 1910 | 10 | 191 | CR-S16-04 | Crossroads | 2025-03-28 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001009 | 17248 | 98 | 176 | PR-S11-01 | Prairie | 2025-03-28 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-001010 | 1232 | 14 | 88 | PR-S15-03 | Prairie | 2025-03-28 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001011 | 4242 | 42 | 101 | CR-S25-03 | Crossroads | 2025-03-28 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001012 | 312624 | 668 | 468 | PR-S18-04 | Prairie | 2025-03-28 | 23 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001013 | 81367 | 569 | 143 | CR-S09-03 | Crossroads | 2025-03-29 | 1 | Weather - wind | Lateral fuse | Forced | None
OE-25-001014 | 708 | 4 | 177 | HB-S13-02 | Harbor | 2025-03-29 | 1 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001015 | 16863 | 77 | 219 | PR-S01-05 | Prairie | 2025-03-29 | 5 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001016 | 15960 | 57 | 280 | BY-S15-02 | Bayou | 2025-03-29 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-001017 | 48440 | 280 | 173 | BY-S10-04 | Bayou | 2025-03-29 | 9 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-001018 | 1261 | 13 | 97 | CR-S20-01 | Crossroads | 2025-03-29 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-001019 | 1344 | 14 | 96 | BY-S16-03 | Bayou | 2025-03-29 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-001020 | 3992 | 8 | 499 | PR-S08-02 | Prairie | 2025-03-29 | 16 | Animal | Transformer fuse | Forced | None
OE-25-001021 | 1696 | 8 | 212 | PR-S13-05 | Prairie | 2025-03-29 | 16 | Animal | Transformer fuse | Forced | None
OE-25-001022 | 585 | 3 | 195 | BY-S07-03 | Bayou | 2025-03-29 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-001023 | 14415 | 465 | 31 | CR-S30-02 | Crossroads | 2025-03-29 | 17 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001024 | 33325 | 775 | 43 | CR-S30-04 | Crossroads | 2025-03-29 | 18 | Equipment - overhead | Substation breaker | Forced | None
OE-25-001025 | 63360 | 1980 | 32 | BY-S23-03 | Bayou | 2025-03-30 | 0 | Vegetation | Substation breaker | Forced | None
OE-25-001026 | 5580 | 60 | 93 | HB-S01-05 | Harbor | 2025-03-30 | 1 | Animal | Lateral fuse | Forced | None
OE-25-001027 | 1968 | 24 | 82 | HB-S02-03 | Harbor | 2025-03-30 | 1 | Vegetation | Lateral fuse | Forced | None
OE-25-001028 | 5456 | 62 | 88 | BY-S23-04 | Bayou | 2025-03-30 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-001029 | 25025 | 143 | 175 | CR-S29-02 | Crossroads | 2025-03-30 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001030 | 519 | 3 | 173 | CR-S30-07 | Crossroads | 2025-03-30 | 9 | Animal | Transformer fuse | Forced | None
OE-25-001031 | 1512 | 12 | 126 | HB-S13-02 | Harbor | 2025-03-30 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001032 | 1666 | 14 | 119 | HB-S07-03 | Harbor | 2025-03-30 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-001033 | 5727 | 69 | 83 | PR-S04-01 | Prairie | 2025-03-30 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001034 | 2208 | 23 | 96 | BY-S13-04 | Bayou | 2025-03-30 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001035 | 5096 | 14 | 364 | CR-S21-01 | Crossroads | 2025-03-30 | 14 | Animal | Transformer fuse | Forced | None
OE-25-001036 | 6968 | 67 | 104 | CR-S16-04 | Crossroads | 2025-03-30 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001037 | 30688 | 137 | 224 | CR-S13-06 | Crossroads | 2025-03-30 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001038 | 19964 | 92 | 217 | BY-S20-02 | Bayou | 2025-03-30 | 20 | Animal | Lateral fuse | Forced | None
OE-25-001039 | 13494 | 78 | 173 | PR-S13-06 | Prairie | 2025-03-30 | 20 | Animal | Lateral fuse | Forced | None
OE-25-001040 | 2520 | 9 | 280 | HB-S10-02 | Harbor | 2025-03-31 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001041 | 18942 | 246 | 77 | CR-S09-03 | Crossroads | 2025-03-31 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001042 | 3995 | 47 | 85 | PR-S09-03 | Prairie | 2025-03-31 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001043 | 5460 | 26 | 210 | CR-S04-05 | Crossroads | 2025-03-31 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-001044 | 4352 | 32 | 136 | CR-S19-02 | Crossroads | 2025-03-31 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001045 | 4284 | 36 | 119 | HB-S05-01 | Harbor | 2025-03-31 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001046 | 1016 | 8 | 127 | HB-S05-04 | Harbor | 2025-03-31 | 17 | Animal | Transformer fuse | Forced | None
OE-25-001047 | 1176 | 2 | 588 | PR-S13-06 | Prairie | 2025-03-31 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-001048 | 33264 | 924 | 36 | BY-S06-01 | Bayou | 2025-03-31 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-001049 | 82 | 1 | 82 | CR-S02-05 | Crossroads | 2025-03-31 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001050 | 26376 | 1256 | 21 | CR-S20-04 | Crossroads | 2025-03-31 | 20 | Unknown | Substation breaker | Outside cause | None
OE-25-001051 | 47520 | 297 | 160 | BY-S27-04 | Bayou | 2025-03-31 | 22 | Unknown | Feeder recloser | Forced | None
OE-25-001052 | 912 | 6 | 152 | PR-S01-03 | Prairie | 2025-04-01 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001053 | 1016 | 8 | 127 | HB-S01-05 | Harbor | 2025-04-01 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-001054 | 138 | 3 | 46 | HB-S20-02 | Harbor | 2025-04-01 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001055 | 2160 | 20 | 108 | CR-S11-01 | Crossroads | 2025-04-01 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001056 | 2250 | 45 | 50 | HB-S19-04 | Harbor | 2025-04-01 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001057 | 351 | 3 | 117 | HB-S20-03 | Harbor | 2025-04-01 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-001058 | 59100 | 1182 | 50 | BY-S29-02 | Bayou | 2025-04-01 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-25-001059 | 1134 | 14 | 81 | CR-S18-01 | Crossroads | 2025-04-01 | 17 | Unknown | Transformer fuse | Forced | None
OE-25-001060 | 318 | 3 | 106 | BY-S25-04 | Bayou | 2025-04-01 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001061 | 358820 | 2330 | 154 | PR-S14-04 | Prairie | 2025-04-01 | 19 | Animal | Substation breaker | Forced | None
OE-25-001062 | 297 | 1 | 297 | BY-S22-04 | Bayou | 2025-04-01 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001063 | 11256 | 134 | 84 | CR-S08-02 | Crossroads | 2025-04-01 | 22 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001064 | 269 | 1 | 269 | CR-S18-02 | Crossroads | 2025-04-01 | 23 | Unknown | Transformer fuse | Forced | None
OE-25-001065 | 16940 | 77 | 220 | CR-S12-01 | Crossroads | 2025-04-02 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-001066 | 17331 | 109 | 159 | PR-S02-03 | Prairie | 2025-04-02 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-001067 | 2405 | 13 | 185 | CR-S28-04 | Crossroads | 2025-04-02 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-001068 | 26832 | 559 | 48 | BY-S15-04 | Bayou | 2025-04-02 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001069 | 23091 | 537 | 43 | CR-S20-03 | Crossroads | 2025-04-02 | 11 | Animal | Feeder recloser | Forced | None
OE-25-001070 | 68172 | 437 | 156 | BY-S23-05 | Bayou | 2025-04-02 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001071 | 11890 | 58 | 205 | CR-S07-06 | Crossroads | 2025-04-02 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001072 | 98044 | 508 | 193 | HB-S03-02 | Harbor | 2025-04-02 | 13 | Vehicle or public | Feeder recloser | Forced | None
OE-25-001073 | 400 | 5 | 80 | CR-S13-02 | Crossroads | 2025-04-02 | 17 | Animal | Transformer fuse | Forced | None
OE-25-001074 | 8410 | 29 | 290 | BY-S08-02 | Bayou | 2025-04-02 | 23 | Vegetation | Lateral fuse | Forced | None
OE-25-001075 | 5341 | 49 | 109 | HB-S06-05 | Harbor | 2025-04-02 | 23 | Vegetation | Lateral fuse | Forced | None
OE-25-001076 | 4738 | 46 | 103 | BY-S18-07 | Bayou | 2025-04-03 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001077 | 1302 | 6 | 217 | BY-S04-01 | Bayou | 2025-04-03 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-001078 | 735 | 7 | 105 | CR-S30-05 | Crossroads | 2025-04-03 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001079 | 3135 | 33 | 95 | CR-S14-01 | Crossroads | 2025-04-03 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001080 | 9920 | 80 | 124 | CR-S18-04 | Crossroads | 2025-04-03 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-001081 | 8820 | 84 | 105 | HB-S02-02 | Harbor | 2025-04-03 | 11 | Unknown | Lateral fuse | Forced | None
OE-25-001082 | 72237 | 363 | 199 | HB-S16-03 | Harbor | 2025-04-03 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-001083 | 7685 | 53 | 145 | PR-S15-06 | Prairie | 2025-04-03 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001084 | 21238 | 574 | 37 | PR-S06-03 | Prairie | 2025-04-03 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-001085 | 22311 | 201 | 111 | CR-S08-01 | Crossroads | 2025-04-03 | 16 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-001086 | 288 | 4 | 72 | PR-S15-04 | Prairie | 2025-04-03 | 17 | Animal | Transformer fuse | Forced | None
OE-25-001087 | 1384 | 8 | 173 | PR-S03-01 | Prairie | 2025-04-03 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-25-001088 | 1272 | 12 | 106 | HB-S17-02 | Harbor | 2025-04-03 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001089 | 772 | 4 | 193 | BY-S18-06 | Bayou | 2025-04-04 | 1 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001090 | 332 | 4 | 83 | HB-S05-05 | Harbor | 2025-04-04 | 5 | Weather - wind | Transformer fuse | Forced | None
OE-25-001091 | 1392 | 12 | 116 | CR-S10-03 | Crossroads | 2025-04-04 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001092 | 2782 | 13 | 214 | BY-S07-02 | Bayou | 2025-04-04 | 9 | Unknown | Transformer fuse | Forced | None
OE-25-001093 | 1335 | 15 | 89 | CR-S28-01 | Crossroads | 2025-04-04 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001094 | 840 | 7 | 120 | CR-S13-04 | Crossroads | 2025-04-04 | 12 | Animal | Transformer fuse | Forced | None
OE-25-001095 | 2070 | 23 | 90 | PR-S18-01 | Prairie | 2025-04-04 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001096 | 8733 | 41 | 213 | PR-S19-04 | Prairie | 2025-04-04 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001097 | 693 | 9 | 77 | HB-S03-01 | Harbor | 2025-04-04 | 14 | Animal | Transformer fuse | Forced | None
OE-25-001098 | 10878 | 111 | 98 | PR-S07-03 | Prairie | 2025-04-04 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-001099 | 24534 | 423 | 58 | PR-S14-01 | Prairie | 2025-04-04 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-25-001100 | 5166 | 14 | 369 | PR-S14-01 | Prairie | 2025-04-04 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001101 | 25600 | 640 | 40 | CR-S22-02 | Crossroads | 2025-04-04 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001102 | 740 | 10 | 74 | CR-S26-06 | Crossroads | 2025-04-04 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001103 | 28686 | 683 | 42 | BY-S16-05 | Bayou | 2025-04-04 | 20 | Vehicle or public | Feeder recloser | Forced | None
OE-25-001104 | 179 | 1 | 179 | BY-S13-04 | Bayou | 2025-04-05 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001105 | 8645 | 133 | 65 | CR-S19-03 | Crossroads | 2025-04-05 | 7 | Animal | Lateral fuse | Forced | None
OE-25-001106 | 12963 | 87 | 149 | HB-S15-01 | Harbor | 2025-04-05 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-001107 | 13833 | 53 | 261 | PR-S13-06 | Prairie | 2025-04-05 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001108 | 3135 | 33 | 95 | HB-S10-01 | Harbor | 2025-04-05 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001109 | 2960 | 40 | 74 | BY-S14-03 | Bayou | 2025-04-05 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001110 | 5616 | 26 | 216 | PR-S01-03 | Prairie | 2025-04-05 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-001111 | 5928 | 52 | 114 | CR-S28-03 | Crossroads | 2025-04-05 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001112 | 3172 | 26 | 122 | PR-S04-01 | Prairie | 2025-04-06 | 4 | Animal | Lateral fuse | Forced | None
OE-25-001113 | 1692 | 12 | 141 | PR-S07-06 | Prairie | 2025-04-06 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001114 | 1683 | 17 | 99 | PR-S16-05 | Prairie | 2025-04-06 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001115 | 6478 | 79 | 82 | HB-S20-02 | Harbor | 2025-04-06 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-001116 | 72051 | 511 | 141 | BY-S12-03 | Bayou | 2025-04-06 | 10 | Animal | Feeder recloser | Forced | None
OE-25-001117 | 30030 | 154 | 195 | CR-S22-01 | Crossroads | 2025-04-06 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001118 | 31588 | 149 | 212 | PR-S17-01 | Prairie | 2025-04-06 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-001119 | 1292 | 19 | 68 | BY-S15-06 | Bayou | 2025-04-06 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001120 | 31047 | 393 | 79 | CR-S10-02 | Crossroads | 2025-04-06 | 17 | Vegetation | IGSD-isolated section | Forced | None
OE-25-001121 | 1256 | 4 | 314 | PR-S20-02 | Prairie | 2025-04-06 | 17 | Animal | Transformer fuse | Forced | None
OE-25-001122 | 2926 | 14 | 209 | CR-S31-02 | Crossroads | 2025-04-06 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001123 | 4631 | 11 | 421 | PR-S01-01 | Prairie | 2025-04-06 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-001124 | 795 | 53 | 15 | CR-S01-03 | Crossroads | 2025-04-07 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001125 | 469 | 7 | 67 | PR-S03-05 | Prairie | 2025-04-07 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001126 | 32520 | 542 | 60 | CR-S07-05 | Crossroads | 2025-04-07 | 7 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-001127 | 33782 | 254 | 133 | CR-S21-03 | Crossroads | 2025-04-07 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001128 | 324 | 2 | 162 | BY-S23-02 | Bayou | 2025-04-07 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001129 | 2410 | 10 | 241 | CR-S24-02 | Crossroads | 2025-04-07 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001130 | 26448 | 348 | 76 | BY-S10-03 | Bayou | 2025-04-07 | 9 | Animal | Feeder recloser | Forced | None
OE-25-001131 | 8024 | 59 | 136 | HB-S04-01 | Harbor | 2025-04-07 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001132 | 1710 | 38 | 45 | CR-S04-02 | Crossroads | 2025-04-07 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-001133 | 8136 | 36 | 226 | BY-S15-02 | Bayou | 2025-04-07 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001134 | 912 | 6 | 152 | HB-S07-04 | Harbor | 2025-04-07 | 12 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001135 | 750 | 5 | 150 | BY-S25-05 | Bayou | 2025-04-07 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001136 | 2125 | 25 | 85 | CR-S28-03 | Crossroads | 2025-04-07 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-001137 | 314 | 2 | 157 | BY-S02-01 | Bayou | 2025-04-07 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001138 | 620 | 4 | 155 | BY-S11-03 | Bayou | 2025-04-07 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001139 | 3600 | 25 | 144 | HB-S11-01 | Harbor | 2025-04-07 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001140 | 2875 | 23 | 125 | BY-S03-03 | Bayou | 2025-04-07 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001141 | 3201 | 33 | 97 | HB-S09-03 | Harbor | 2025-04-07 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001142 | 846 | 6 | 141 | CR-S31-02 | Crossroads | 2025-04-07 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-001143 | 315 | 3 | 105 | HB-S01-03 | Harbor | 2025-04-07 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-001144 | 1362 | 6 | 227 | PR-S07-01 | Prairie | 2025-04-07 | 20 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001145 | 62010 | 689 | 90 | BY-S13-01 | Bayou | 2025-04-07 | 22 | Weather - lightning | Feeder recloser | Forced | None
OE-25-001146 | 19782 | 157 | 126 | BY-S17-01 | Bayou | 2025-04-07 | 22 | Unknown | Lateral fuse | Forced | None
OE-25-001147 | 37727 | 1217 | 31 | CR-S01-03 | Crossroads | 2025-04-07 | 22 | Animal | Feeder recloser | Forced | None
OE-25-001148 | 4392 | 4 | 1098 | CR-S25-06 | Crossroads | 2025-04-08 | 5 | Vegetation | Transformer fuse | Forced | None
OE-25-001149 | 78156 | 501 | 156 | BY-S21-04 | Bayou | 2025-04-08 | 8 | Vegetation | Feeder recloser | Forced | None
OE-25-001150 | 868 | 7 | 124 | HB-S12-02 | Harbor | 2025-04-08 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-001151 | 3653 | 13 | 281 | CR-S04-01 | Crossroads | 2025-04-08 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001152 | 42504 | 462 | 92 | HB-S03-02 | Harbor | 2025-04-08 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001153 | 404 | 4 | 101 | CR-S23-03 | Crossroads | 2025-04-08 | 15 | Animal | Transformer fuse | Forced | None
OE-25-001154 | 1785 | 5 | 357 | PR-S17-01 | Prairie | 2025-04-08 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-25-001155 | 663 | 3 | 221 | BY-S15-05 | Bayou | 2025-04-08 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-001156 | 7840 | 98 | 80 | CR-S10-02 | Crossroads | 2025-04-09 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001157 | 1105 | 13 | 85 | CR-S04-01 | Crossroads | 2025-04-09 | 11 | Animal | Transformer fuse | Forced | None
OE-25-001158 | 144 | 2 | 72 | CR-S14-02 | Crossroads | 2025-04-09 | 11 | Unknown | Transformer fuse | Forced | None
OE-25-001159 | 20022 | 282 | 71 | CR-S19-03 | Crossroads | 2025-04-09 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-001160 | 1476 | 12 | 123 | CR-S15-02 | Crossroads | 2025-04-09 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001161 | 41922 | 306 | 137 | HB-S08-03 | Harbor | 2025-04-09 | 12 | Animal | Feeder recloser | Forced | None
OE-25-001162 | 34400 | 172 | 200 | HB-S14-02 | Harbor | 2025-04-09 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001163 | 14647 | 97 | 151 | BY-S16-01 | Bayou | 2025-04-09 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001164 | 15600 | 78 | 200 | BY-S14-03 | Bayou | 2025-04-09 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001165 | 123510 | 1074 | 115 | PR-S14-04 | Prairie | 2025-04-09 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-001166 | 1072 | 8 | 134 | BY-S14-02 | Bayou | 2025-04-09 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001167 | 405 | 15 | 27 | CR-S02-05 | Crossroads | 2025-04-09 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001168 | 685 | 5 | 137 | PR-S16-04 | Prairie | 2025-04-09 | 17 | Animal | Transformer fuse | Forced | None
OE-25-001169 | 17860 | 95 | 188 | PR-S15-05 | Prairie | 2025-04-09 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-001170 | 882 | 14 | 63 | BY-S15-06 | Bayou | 2025-04-10 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-001171 | 20580 | 147 | 140 | HB-S11-03 | Harbor | 2025-04-10 | 2 | Vegetation | Lateral fuse | Forced | None
OE-25-001172 | 6860 | 35 | 196 | BY-S29-05 | Bayou | 2025-04-10 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001173 | 187 | 1 | 187 | HB-S03-02 | Harbor | 2025-04-10 | 7 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001174 | 24062 | 227 | 106 | CR-S21-02 | Crossroads | 2025-04-10 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-001175 | 13440 | 112 | 120 | PR-S01-05 | Prairie | 2025-04-10 | 9 | Animal | Lateral fuse | Forced | None
OE-25-001176 | 14528 | 64 | 227 | BY-S01-01 | Bayou | 2025-04-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001177 | 1870 | 11 | 170 | BY-S15-05 | Bayou | 2025-04-10 | 13 | Animal | Transformer fuse | Forced | None
OE-25-001178 | 304 | 2 | 152 | BY-S23-03 | Bayou | 2025-04-10 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001179 | 8748 | 81 | 108 | HB-S02-02 | Harbor | 2025-04-10 | 14 | Animal | Lateral fuse | Forced | None
OE-25-001180 | 3240 | 9 | 360 | BY-S24-04 | Bayou | 2025-04-10 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001181 | 948 | 12 | 79 | CR-S02-03 | Crossroads | 2025-04-10 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001182 | 1456 | 8 | 182 | PR-S02-02 | Prairie | 2025-04-10 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001183 | 2700 | 10 | 270 | BY-S23-02 | Bayou | 2025-04-10 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001184 | 1092 | 7 | 156 | CR-S32-02 | Crossroads | 2025-04-10 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001185 | 7025 | 25 | 281 | PR-S10-02 | Prairie | 2025-04-10 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001186 | 1118 | 13 | 86 | PR-S11-02 | Prairie | 2025-04-11 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001187 | 25143 | 87 | 289 | BY-S18-03 | Bayou | 2025-04-11 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001188 | 11270 | 115 | 98 | BY-S22-04 | Bayou | 2025-04-11 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001189 | 4950 | 22 | 225 | CR-S30-04 | Crossroads | 2025-04-11 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001190 | 2145 | 13 | 165 | PR-S08-01 | Prairie | 2025-04-11 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001191 | 3311 | 11 | 301 | BY-S27-02 | Bayou | 2025-04-11 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-001192 | 21584 | 568 | 38 | BY-S07-06 | Bayou | 2025-04-11 | 12 | Weather - wind | Feeder recloser | Forced | None
OE-25-001193 | 3685 | 67 | 55 | BY-S26-05 | Bayou | 2025-04-11 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001194 | 17355 | 89 | 195 | CR-S15-01 | Crossroads | 2025-04-11 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001195 | 22852 | 58 | 394 | HB-S13-02 | Harbor | 2025-04-11 | 15 | Unknown | Lateral fuse | Forced | None
OE-25-001196 | 3672 | 24 | 153 | BY-S20-03 | Bayou | 2025-04-11 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001197 | 1350 | 27 | 50 | BY-S28-03 | Bayou | 2025-04-11 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001198 | 37576 | 671 | 56 | CR-S15-01 | Crossroads | 2025-04-11 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001199 | 6072 | 46 | 132 | HB-S01-03 | Harbor | 2025-04-11 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001200 | 6528 | 34 | 192 | PR-S02-03 | Prairie | 2025-04-11 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001201 | 58 | 1 | 58 | BY-S18-02 | Bayou | 2025-04-11 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-001202 | 24600 | 300 | 82 | HB-S01-02 | Harbor | 2025-04-12 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001203 | 99 | 1 | 99 | BY-S10-03 | Bayou | 2025-04-12 | 4 | Vegetation | Transformer fuse | Forced | None
OE-25-001204 | 120 | 3 | 40 | HB-S19-02 | Harbor | 2025-04-12 | 7 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001205 | 1924 | 13 | 148 | CR-S32-01 | Crossroads | 2025-04-12 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001206 | 2211 | 33 | 67 | CR-S05-04 | Crossroads | 2025-04-12 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-001207 | 6063 | 129 | 47 | CR-S14-06 | Crossroads | 2025-04-12 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-001208 | 71760 | 1794 | 40 | CR-S04-02 | Crossroads | 2025-04-12 | 11 | Equipment - underground | Substation breaker | Forced | None
OE-25-001209 | 34983 | 299 | 117 | HB-S11-01 | Harbor | 2025-04-12 | 14 | Weather - wind | Feeder recloser | Forced | None
OE-25-001210 | 11684 | 46 | 254 | PR-S02-01 | Prairie | 2025-04-12 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-001211 | 144144 | 528 | 273 | CR-S32-01 | Crossroads | 2025-04-12 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-001212 | 8700 | 150 | 58 | HB-S01-05 | Harbor | 2025-04-12 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001213 | 1220 | 5 | 244 | CR-S03-01 | Crossroads | 2025-04-13 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001214 | 1390 | 10 | 139 | PR-S12-01 | Prairie | 2025-04-13 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001215 | 1092 | 12 | 91 | BY-S01-02 | Bayou | 2025-04-13 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-001216 | 172 | 2 | 86 | CR-S25-01 | Crossroads | 2025-04-13 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001217 | 1364 | 11 | 124 | PR-S03-05 | Prairie | 2025-04-13 | 13 | Animal | Transformer fuse | Forced | None
OE-25-001218 | 5236 | 28 | 187 | CR-S05-03 | Crossroads | 2025-04-13 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001219 | 2958 | 34 | 87 | PR-S05-02 | Prairie | 2025-04-13 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-001220 | 9747 | 57 | 171 | BY-S27-04 | Bayou | 2025-04-13 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001221 | 60047 | 1937 | 31 | CR-S24-03 | Crossroads | 2025-04-13 | 20 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-001222 | 732 | 6 | 122 | BY-S15-05 | Bayou | 2025-04-14 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-001223 | 1908 | 6 | 318 | BY-S12-02 | Bayou | 2025-04-14 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-001224 | 27984 | 176 | 159 | HB-S12-02 | Harbor | 2025-04-14 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001225 | 13038 | 159 | 82 | HB-S20-01 | Harbor | 2025-04-14 | 9 | Animal | Lateral fuse | Forced | None
OE-25-001226 | 4704 | 56 | 84 | HB-S05-01 | Harbor | 2025-04-14 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-25-001227 | 177632 | 1952 | 91 | CR-S27-04 | Crossroads | 2025-04-14 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001228 | 3612 | 14 | 258 | HB-S03-03 | Harbor | 2025-04-14 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-001229 | 870 | 5 | 174 | HB-S01-02 | Harbor | 2025-04-14 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001230 | 1508 | 13 | 116 | PR-S18-05 | Prairie | 2025-04-14 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001231 | 41040 | 2052 | 20 | CR-S02-03 | Crossroads | 2025-04-14 | 16 | Unknown | Substation breaker | Outside cause | None
OE-25-001232 | 775 | 5 | 155 | CR-S18-01 | Crossroads | 2025-04-14 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001233 | 19400 | 97 | 200 | BY-S21-01 | Bayou | 2025-04-14 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-001234 | 6460 | 68 | 95 | HB-S19-03 | Harbor | 2025-04-14 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001235 | 162 | 3 | 54 | HB-S02-01 | Harbor | 2025-04-14 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001236 | 3034 | 41 | 74 | CR-S09-05 | Crossroads | 2025-04-15 | 2 | Animal | Lateral fuse | Forced | None
OE-25-001237 | 560 | 7 | 80 | CR-S07-02 | Crossroads | 2025-04-15 | 4 | Animal | Transformer fuse | Forced | None
OE-25-001238 | 4746 | 42 | 113 | CR-S14-03 | Crossroads | 2025-04-15 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001239 | 1112 | 4 | 278 | BY-S10-05 | Bayou | 2025-04-15 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001240 | 1521 | 9 | 169 | BY-S06-02 | Bayou | 2025-04-15 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001241 | 3912 | 24 | 163 | CR-S32-01 | Crossroads | 2025-04-15 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001242 | 13650 | 75 | 182 | HB-S01-05 | Harbor | 2025-04-15 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001243 | 1827 | 9 | 203 | BY-S09-04 | Bayou | 2025-04-15 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-001244 | 2184 | 12 | 182 | PR-S20-03 | Prairie | 2025-04-15 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-25-001245 | 5984 | 32 | 187 | BY-S15-06 | Bayou | 2025-04-15 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001246 | 23569 | 91 | 259 | BY-S26-05 | Bayou | 2025-04-15 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-001247 | 65016 | 1161 | 56 | CR-S32-01 | Crossroads | 2025-04-15 | 14 | Unknown | Feeder recloser | Forced | None
OE-25-001248 | 107559 | 969 | 111 | CR-S14-01 | Crossroads | 2025-04-15 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001249 | 2156 | 11 | 196 | CR-S14-05 | Crossroads | 2025-04-15 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001250 | 1980 | 11 | 180 | BY-S25-04 | Bayou | 2025-04-15 | 19 | Unknown | Transformer fuse | Forced | None
OE-25-001251 | 3950 | 79 | 50 | CR-S18-04 | Crossroads | 2025-04-15 | 19 | Unknown | Lateral fuse | Forced | None
OE-25-001252 | 46693 | 881 | 53 | CR-S20-05 | Crossroads | 2025-04-15 | 20 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001253 | 5148 | 52 | 99 | CR-S25-03 | Crossroads | 2025-04-16 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001254 | 1150 | 5 | 230 | CR-S02-05 | Crossroads | 2025-04-16 | 2 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001255 | 515 | 5 | 103 | HB-S09-02 | Harbor | 2025-04-16 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001256 | 1740 | 10 | 174 | PR-S02-02 | Prairie | 2025-04-16 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001257 | 1416 | 12 | 118 | BY-S01-02 | Bayou | 2025-04-16 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001258 | 1452 | 11 | 132 | BY-S29-01 | Bayou | 2025-04-16 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001259 | 11748 | 89 | 132 | PR-S08-02 | Prairie | 2025-04-16 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-001260 | 9120 | 48 | 190 | CR-S07-01 | Crossroads | 2025-04-16 | 12 | Animal | Lateral fuse | Forced | None
OE-25-001261 | 1608 | 12 | 134 | CR-S22-04 | Crossroads | 2025-04-16 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001262 | 187082 | 1127 | 166 | BY-S29-01 | Bayou | 2025-04-16 | 13 | Animal | Feeder recloser | Forced | None
OE-25-001263 | 2310 | 7 | 330 | PR-S16-05 | Prairie | 2025-04-16 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001264 | 5762 | 67 | 86 | PR-S15-05 | Prairie | 2025-04-16 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-001265 | 14259 | 147 | 97 | PR-S19-04 | Prairie | 2025-04-16 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-001266 | 6344 | 52 | 122 | HB-S12-02 | Harbor | 2025-04-16 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001267 | 5148 | 66 | 78 | BY-S16-06 | Bayou | 2025-04-16 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-001268 | 14720 | 320 | 46 | BY-S03-03 | Bayou | 2025-04-17 | 0 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001269 | 3168 | 8 | 396 | PR-S13-04 | Prairie | 2025-04-17 | 1 | Vegetation | Transformer fuse | Forced | None
OE-25-001270 | 146 | 2 | 73 | CR-S29-03 | Crossroads | 2025-04-17 | 2 | Unknown | Transformer fuse | Forced | None
OE-25-001271 | 12328 | 92 | 134 | PR-S12-01 | Prairie | 2025-04-17 | 7 | Animal | Lateral fuse | Forced | None
OE-25-001272 | 9200 | 40 | 230 | CR-S05-02 | Crossroads | 2025-04-17 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001273 | 2926 | 11 | 266 | CR-S11-01 | Crossroads | 2025-04-17 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001274 | 14500 | 500 | 29 | HB-S14-01 | Harbor | 2025-04-17 | 9 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001275 | 1950 | 13 | 150 | CR-S28-02 | Crossroads | 2025-04-17 | 14 | Animal | Transformer fuse | Forced | None
OE-25-001276 | 15631 | 203 | 77 | CR-S20-02 | Crossroads | 2025-04-17 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-001277 | 1106 | 7 | 158 | BY-S07-02 | Bayou | 2025-04-17 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-001278 | 1200 | 8 | 150 | CR-S18-06 | Crossroads | 2025-04-17 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001279 | 94552 | 892 | 106 | PR-S10-02 | Prairie | 2025-04-17 | 20 | Vegetation | Substation breaker | Forced | None
OE-25-001280 | 185 | 1 | 185 | HB-S08-02 | Harbor | 2025-04-18 | 1 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001281 | 4740 | 30 | 158 | PR-S03-03 | Prairie | 2025-04-18 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-001282 | 2623 | 61 | 43 | BY-S06-01 | Bayou | 2025-04-18 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001283 | 9180 | 51 | 180 | BY-S26-01 | Bayou | 2025-04-18 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001284 | 11505 | 59 | 195 | PR-S18-02 | Prairie | 2025-04-18 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001285 | 573 | 3 | 191 | HB-S05-03 | Harbor | 2025-04-18 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001286 | 52142 | 899 | 58 | PR-S12-01 | Prairie | 2025-04-18 | 14 | Animal | Feeder recloser | Forced | None
OE-25-001287 | 9779 | 77 | 127 | CR-S14-02 | Crossroads | 2025-04-18 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001288 | 448 | 8 | 56 | PR-S01-05 | Prairie | 2025-04-18 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-001289 | 12825 | 75 | 171 | PR-S09-04 | Prairie | 2025-04-18 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-001290 | 3555 | 45 | 79 | PR-S11-01 | Prairie | 2025-04-18 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001291 | 665 | 7 | 95 | CR-S04-03 | Crossroads | 2025-04-18 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-001292 | 9460 | 86 | 110 | BY-S06-03 | Bayou | 2025-04-19 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-25-001293 | 11649 | 33 | 353 | BY-S16-01 | Bayou | 2025-04-19 | 9 | Unknown | Lateral fuse | Forced | None
OE-25-001294 | 684 | 12 | 57 | BY-S09-01 | Bayou | 2025-04-19 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001295 | 1470 | 7 | 210 | PR-S02-02 | Prairie | 2025-04-19 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001296 | 31374 | 581 | 54 | CR-S20-03 | Crossroads | 2025-04-19 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001297 | 33984 | 144 | 236 | PR-S06-01 | Prairie | 2025-04-19 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-001298 | 42588 | 676 | 63 | BY-S08-02 | Bayou | 2025-04-19 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-001299 | 1819 | 17 | 107 | BY-S20-01 | Bayou | 2025-04-19 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-001300 | 2350 | 25 | 94 | PR-S09-03 | Prairie | 2025-04-19 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001301 | 858 | 13 | 66 | CR-S26-04 | Crossroads | 2025-04-19 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001302 | 840 | 7 | 120 | HB-S07-05 | Harbor | 2025-04-20 | 3 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001303 | 1460 | 10 | 146 | BY-S19-01 | Bayou | 2025-04-20 | 7 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001304 | 1024 | 8 | 128 | CR-S18-03 | Crossroads | 2025-04-20 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-25-001305 | 3648 | 48 | 76 | PR-S07-02 | Prairie | 2025-04-20 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001306 | 38122 | 778 | 49 | CR-S16-01 | Crossroads | 2025-04-20 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001307 | 561 | 3 | 187 | BY-S23-03 | Bayou | 2025-04-20 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001308 | 236 | 4 | 59 | HB-S05-04 | Harbor | 2025-04-20 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001309 | 11925 | 225 | 53 | CR-S30-04 | Crossroads | 2025-04-20 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001310 | 5395 | 83 | 65 | CR-S07-05 | Crossroads | 2025-04-20 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001311 | 13114 | 79 | 166 | PR-S07-03 | Prairie | 2025-04-20 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-001312 | 2480 | 20 | 124 | PR-S07-06 | Prairie | 2025-04-20 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-001313 | 14850 | 54 | 275 | HB-S08-04 | Harbor | 2025-04-20 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001314 | 47970 | 585 | 82 | HB-S20-04 | Harbor | 2025-04-20 | 23 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001315 | 3016 | 26 | 116 | CR-S07-03 | Crossroads | 2025-04-21 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001316 | 1036 | 7 | 148 | BY-S15-04 | Bayou | 2025-04-21 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001317 | 9071 | 47 | 193 | BY-S16-03 | Bayou | 2025-04-21 | 9 | Animal | Lateral fuse | Forced | None
OE-25-001318 | 48792 | 856 | 57 | CR-S13-06 | Crossroads | 2025-04-21 | 11 | Animal | Feeder recloser | Forced | None
OE-25-001319 | 31350 | 330 | 95 | PR-S15-02 | Prairie | 2025-04-21 | 11 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-001320 | 1430 | 13 | 110 | HB-S09-04 | Harbor | 2025-04-21 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-001321 | 12444 | 61 | 204 | PR-S03-05 | Prairie | 2025-04-21 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001322 | 3848 | 13 | 296 | PR-S10-03 | Prairie | 2025-04-21 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001323 | 30485 | 455 | 67 | HB-S18-03 | Harbor | 2025-04-21 | 16 | Vegetation | IGSD-isolated section | Forced | None
OE-25-001324 | 1586 | 13 | 122 | BY-S10-04 | Bayou | 2025-04-21 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-001325 | 1824 | 8 | 228 | PR-S08-01 | Prairie | 2025-04-21 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-001326 | 9010 | 34 | 265 | BY-S07-03 | Bayou | 2025-04-22 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001327 | 41822 | 1901 | 22 | CR-S04-03 | Crossroads | 2025-04-22 | 10 | Equipment - underground | Substation breaker | Forced | None
OE-25-001328 | 149632 | 896 | 167 | PR-S15-01 | Prairie | 2025-04-22 | 12 | Equipment - overhead | Substation breaker | Forced | None
OE-25-001329 | 14300 | 220 | 65 | BY-S22-04 | Bayou | 2025-04-22 | 13 | Animal | Lateral fuse | Forced | None
OE-25-001330 | 382 | 2 | 191 | CR-S18-05 | Crossroads | 2025-04-22 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001331 | 30210 | 53 | 570 | BY-S29-04 | Bayou | 2025-04-22 | 14 | Unknown | Lateral fuse | Forced | None
OE-25-001332 | 15857 | 101 | 157 | PR-S08-03 | Prairie | 2025-04-22 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001333 | 23058 | 427 | 54 | CR-S29-03 | Crossroads | 2025-04-22 | 15 | Weather - lightning | Feeder recloser | Forced | None
OE-25-001334 | 36729 | 231 | 159 | PR-S02-02 | Prairie | 2025-04-22 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001335 | 4452 | 14 | 318 | PR-S09-03 | Prairie | 2025-04-22 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001336 | 1162 | 14 | 83 | PR-S16-01 | Prairie | 2025-04-22 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001337 | 12744 | 54 | 236 | BY-S30-02 | Bayou | 2025-04-22 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-001338 | 332 | 4 | 83 | HB-S20-02 | Harbor | 2025-04-22 | 19 | Animal | Transformer fuse | Forced | None
OE-25-001339 | 35322 | 174 | 203 | CR-S07-05 | Crossroads | 2025-04-22 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001340 | 92352 | 962 | 96 | PR-S07-06 | Prairie | 2025-04-22 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-001341 | 310 | 1 | 310 | BY-S18-06 | Bayou | 2025-04-22 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001342 | 69300 | 660 | 105 | PR-S12-03 | Prairie | 2025-04-23 | 1 | Vegetation | Feeder recloser | Forced | None
OE-25-001343 | 9500 | 95 | 100 | BY-S14-03 | Bayou | 2025-04-23 | 2 | Weather - wind | Lateral fuse | Forced | None
OE-25-001344 | 585 | 3 | 195 | CR-S15-01 | Crossroads | 2025-04-23 | 4 | Vegetation | Transformer fuse | Forced | None
OE-25-001345 | 492 | 4 | 123 | CR-S07-03 | Crossroads | 2025-04-23 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001346 | 45815 | 187 | 245 | CR-S13-05 | Crossroads | 2025-04-23 | 7 | Animal | Lateral fuse | Forced | None
OE-25-001347 | 4180 | 44 | 95 | CR-S12-01 | Crossroads | 2025-04-23 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001348 | 6336 | 48 | 132 | CR-S16-04 | Crossroads | 2025-04-23 | 9 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001349 | 7400 | 100 | 74 | CR-S19-01 | Crossroads | 2025-04-23 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001350 | 14620 | 86 | 170 | PR-S14-04 | Prairie | 2025-04-23 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001351 | 19900 | 199 | 100 | BY-S07-01 | Bayou | 2025-04-23 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001352 | 10758 | 33 | 326 | BY-S12-04 | Bayou | 2025-04-23 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-001353 | 710 | 5 | 142 | PR-S15-06 | Prairie | 2025-04-23 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-25-001354 | 728 | 14 | 52 | BY-S13-06 | Bayou | 2025-04-23 | 13 | Unknown | Lateral fuse | Forced | None
OE-25-001355 | 7068 | 62 | 114 | PR-S03-05 | Prairie | 2025-04-23 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001356 | 2754 | 9 | 306 | PR-S18-05 | Prairie | 2025-04-23 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001357 | 6960 | 145 | 48 | BY-S09-02 | Bayou | 2025-04-23 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001358 | 118 | 1 | 118 | BY-S29-03 | Bayou | 2025-04-23 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001359 | 119534 | 1013 | 118 | BY-S10-05 | Bayou | 2025-04-23 | 17 | Vegetation | Substation breaker | Forced | None
OE-25-001360 | 644 | 4 | 161 | HB-S19-04 | Harbor | 2025-04-23 | 17 | Animal | Transformer fuse | Forced | None
OE-25-001361 | 246870 | 1266 | 195 | PR-S02-02 | Prairie | 2025-04-23 | 17 | Vegetation | Substation breaker | Forced | None
OE-25-001362 | 1848 | 8 | 231 | PR-S06-01 | Prairie | 2025-04-23 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001363 | 1552 | 8 | 194 | CR-S09-01 | Crossroads | 2025-04-23 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001364 | 24621 | 283 | 87 | PR-S01-05 | Prairie | 2025-04-23 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-001365 | 12240 | 612 | 20 | HB-S18-03 | Harbor | 2025-04-24 | 0 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001366 | 3080 | 11 | 280 | PR-S17-01 | Prairie | 2025-04-24 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001367 | 2058 | 42 | 49 | BY-S14-03 | Bayou | 2025-04-24 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-001368 | 2400 | 8 | 300 | HB-S07-01 | Harbor | 2025-04-24 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001369 | 1407 | 7 | 201 | PR-S09-03 | Prairie | 2025-04-24 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-001370 | 18164 | 478 | 38 | BY-S18-02 | Bayou | 2025-04-24 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001371 | 16320 | 170 | 96 | CR-S19-01 | Crossroads | 2025-04-24 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001372 | 4416 | 46 | 96 | BY-S03-02 | Bayou | 2025-04-24 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-001373 | 1794 | 39 | 46 | HB-S14-01 | Harbor | 2025-04-24 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001374 | 1269 | 9 | 141 | HB-S10-02 | Harbor | 2025-04-24 | 21 | Unknown | Transformer fuse | Forced | None
OE-25-001375 | 516 | 4 | 129 | BY-S18-05 | Bayou | 2025-04-25 | 0 | Animal | Transformer fuse | Forced | None
OE-25-001376 | 1980 | 9 | 220 | PR-S13-04 | Prairie | 2025-04-25 | 8 | Animal | Transformer fuse | Forced | None
OE-25-001377 | 244 | 1 | 244 | CR-S23-02 | Crossroads | 2025-04-25 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001378 | 13160 | 94 | 140 | CR-S22-01 | Crossroads | 2025-04-25 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001379 | 13386 | 138 | 97 | CR-S30-05 | Crossroads | 2025-04-25 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001380 | 1480 | 10 | 148 | HB-S10-03 | Harbor | 2025-04-25 | 10 | Unknown | Lateral fuse | Forced | None
OE-25-001381 | 41078 | 437 | 94 | PR-S20-03 | Prairie | 2025-04-25 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-001382 | 8858 | 103 | 86 | PR-S18-05 | Prairie | 2025-04-25 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001383 | 609 | 7 | 87 | BY-S29-05 | Bayou | 2025-04-25 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001384 | 920 | 10 | 92 | CR-S11-02 | Crossroads | 2025-04-25 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001385 | 738 | 9 | 82 | CR-S13-01 | Crossroads | 2025-04-25 | 16 | Animal | Transformer fuse | Forced | None
OE-25-001386 | 11084 | 68 | 163 | BY-S28-03 | Bayou | 2025-04-25 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001387 | 1131 | 13 | 87 | BY-S06-03 | Bayou | 2025-04-26 | 6 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001388 | 1344 | 12 | 112 | BY-S21-02 | Bayou | 2025-04-26 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001389 | 576 | 3 | 192 | BY-S18-01 | Bayou | 2025-04-26 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-001390 | 4554 | 69 | 66 | BY-S24-04 | Bayou | 2025-04-26 | 10 | Animal | Lateral fuse | Forced | None
OE-25-001391 | 1240 | 10 | 124 | CR-S05-03 | Crossroads | 2025-04-26 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001392 | 1008 | 8 | 126 | PR-S19-04 | Prairie | 2025-04-26 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001393 | 460 | 5 | 92 | CR-S09-02 | Crossroads | 2025-04-26 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001394 | 220158 | 1359 | 162 | HB-S09-03 | Harbor | 2025-04-26 | 15 | Equipment - overhead | Substation breaker | Forced | None
OE-25-001395 | 3234 | 49 | 66 | BY-S08-01 | Bayou | 2025-04-26 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-001396 | 236 | 1 | 236 | HB-S02-03 | Harbor | 2025-04-26 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001397 | 3150 | 14 | 225 | CR-S29-03 | Crossroads | 2025-04-26 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001398 | 6040 | 40 | 151 | PR-S07-01 | Prairie | 2025-04-26 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001399 | 13420 | 110 | 122 | PR-S02-02 | Prairie | 2025-04-27 | 4 | Unknown | Lateral fuse | Forced | None
OE-25-001400 | 1116 | 9 | 124 | BY-S04-02 | Bayou | 2025-04-27 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001401 | 222940 | 710 | 314 | CR-S24-04 | Crossroads | 2025-04-27 | 8 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001402 | 4410 | 70 | 63 | HB-S03-02 | Harbor | 2025-04-27 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001403 | 14828 | 44 | 337 | PR-S12-01 | Prairie | 2025-04-27 | 12 | Animal | Lateral fuse | Forced | None
OE-25-001404 | 105265 | 569 | 185 | BY-S14-01 | Bayou | 2025-04-27 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001405 | 42966 | 558 | 77 | BY-S16-01 | Bayou | 2025-04-27 | 13 | Weather - wind | IGSD-isolated section | Forced | None
OE-25-001406 | 76687 | 347 | 221 | CR-S32-01 | Crossroads | 2025-04-27 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001407 | 56 | 1 | 56 | HB-S14-04 | Harbor | 2025-04-27 | 13 | Animal | Transformer fuse | Forced | None
OE-25-001408 | 27999 | 153 | 183 | PR-S18-06 | Prairie | 2025-04-27 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001409 | 36369 | 449 | 81 | HB-S01-01 | Harbor | 2025-04-27 | 15 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-001410 | 2556 | 9 | 284 | PR-S03-03 | Prairie | 2025-04-27 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001411 | 51964 | 1181 | 44 | PR-S07-05 | Prairie | 2025-04-27 | 15 | Equipment - underground | Substation breaker | Forced | None
OE-25-001412 | 61008 | 496 | 123 | CR-S03-03 | Crossroads | 2025-04-27 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001413 | 2701 | 37 | 73 | CR-S08-02 | Crossroads | 2025-04-27 | 19 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001414 | 6534 | 99 | 66 | CR-S09-05 | Crossroads | 2025-04-27 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-001415 | 48174 | 518 | 93 | BY-S01-01 | Bayou | 2025-04-27 | 23 | Vegetation | Feeder recloser | Forced | None
OE-25-001416 | 5661 | 17 | 333 | PR-S02-02 | Prairie | 2025-04-28 | 2 | Vegetation | Lateral fuse | Forced | None
OE-25-001417 | 11526 | 226 | 51 | CR-S23-05 | Crossroads | 2025-04-28 | 4 | Unknown | IGSD-isolated section | Forced | None
OE-25-001418 | 2124 | 12 | 177 | CR-S31-01 | Crossroads | 2025-04-28 | 11 | Animal | Transformer fuse | Forced | None
OE-25-001419 | 7830 | 54 | 145 | BY-S17-03 | Bayou | 2025-04-28 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001420 | 51220 | 788 | 65 | BY-S17-03 | Bayou | 2025-04-28 | 13 | Equipment - overhead | Substation breaker | Forced | None
OE-25-001421 | 16019 | 83 | 193 | BY-S22-03 | Bayou | 2025-04-28 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001422 | 280 | 2 | 140 | CR-S13-01 | Crossroads | 2025-04-28 | 15 | Unknown | Transformer fuse | Forced | None
OE-25-001423 | 395 | 5 | 79 | HB-S01-05 | Harbor | 2025-04-28 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-25-001424 | 240 | 4 | 60 | HB-S03-03 | Harbor | 2025-04-28 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-001425 | 512 | 2 | 256 | PR-S03-05 | Prairie | 2025-04-28 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001426 | 41374 | 274 | 151 | PR-S14-01 | Prairie | 2025-04-28 | 17 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-001427 | 1261 | 13 | 97 | BY-S22-04 | Bayou | 2025-04-28 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-001428 | 18620 | 95 | 196 | HB-S14-04 | Harbor | 2025-04-28 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-001429 | 25670 | 151 | 170 | PR-S13-05 | Prairie | 2025-04-28 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001430 | 2450 | 10 | 245 | CR-S03-02 | Crossroads | 2025-04-28 | 20 | Unknown | Transformer fuse | Forced | None
OE-25-001431 | 1846 | 13 | 142 | BY-S03-02 | Bayou | 2025-04-28 | 21 | Animal | Transformer fuse | Forced | None
OE-25-001432 | 3760 | 94 | 40 | CR-S04-04 | Crossroads | 2025-04-29 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001433 | 35821 | 113 | 317 | CR-S25-01 | Crossroads | 2025-04-29 | 3 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001434 | 13464 | 66 | 204 | CR-S13-01 | Crossroads | 2025-04-29 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001435 | 6004 | 38 | 158 | HB-S06-05 | Harbor | 2025-04-29 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001436 | 2533 | 17 | 149 | BY-S14-02 | Bayou | 2025-04-29 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001437 | 17215 | 55 | 313 | BY-S18-07 | Bayou | 2025-04-29 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001438 | 19635 | 85 | 231 | PR-S13-03 | Prairie | 2025-04-29 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001439 | 1694 | 7 | 242 | PR-S16-05 | Prairie | 2025-04-29 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001440 | 1015 | 5 | 203 | HB-S11-01 | Harbor | 2025-04-29 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001441 | 352 | 2 | 176 | PR-S06-01 | Prairie | 2025-04-29 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001442 | 38830 | 353 | 110 | PR-S18-04 | Prairie | 2025-04-29 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-001443 | 39852 | 486 | 82 | CR-S31-03 | Crossroads | 2025-04-29 | 14 | Weather - lightning | Feeder recloser | Forced | None
OE-25-001444 | 39195 | 335 | 117 | CR-S05-05 | Crossroads | 2025-04-29 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001445 | 492 | 6 | 82 | CR-S22-01 | Crossroads | 2025-04-29 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001446 | 616 | 8 | 77 | CR-S27-02 | Crossroads | 2025-04-29 | 16 | Unknown | Transformer fuse | Forced | None
OE-25-001447 | 145824 | 1302 | 112 | PR-S17-01 | Prairie | 2025-04-29 | 16 | Vegetation | Feeder recloser | Forced | None
OE-25-001448 | 1804 | 11 | 164 | BY-S28-02 | Bayou | 2025-04-29 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001449 | 3953 | 67 | 59 | BY-S07-02 | Bayou | 2025-04-29 | 19 | Animal | Lateral fuse | Forced | None
OE-25-001450 | 327 | 3 | 109 | CR-S04-04 | Crossroads | 2025-04-29 | 21 | Animal | Transformer fuse | Forced | None
OE-25-001451 | 9592 | 88 | 109 | BY-S26-05 | Bayou | 2025-04-29 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-001452 | 960 | 10 | 96 | PR-S18-05 | Prairie | 2025-04-29 | 23 | Vegetation | Transformer fuse | Forced | None
OE-25-001453 | 3810 | 30 | 127 | BY-S23-05 | Bayou | 2025-04-30 | 6 | Vegetation | Lateral fuse | Forced | None
OE-25-001454 | 8944 | 86 | 104 | BY-S24-01 | Bayou | 2025-04-30 | 6 | Vegetation | Lateral fuse | Forced | None
OE-25-001455 | 9048 | 87 | 104 | HB-S01-01 | Harbor | 2025-04-30 | 8 | Animal | Lateral fuse | Forced | None
OE-25-001456 | 29670 | 115 | 258 | BY-S26-06 | Bayou | 2025-04-30 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-001457 | 828 | 9 | 92 | CR-S24-03 | Crossroads | 2025-04-30 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001458 | 2873 | 13 | 221 | PR-S01-04 | Prairie | 2025-04-30 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001459 | 3248 | 14 | 232 | PR-S20-02 | Prairie | 2025-04-30 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001460 | 16748 | 316 | 53 | BY-S09-05 | Bayou | 2025-04-30 | 11 | Weather - lightning | Feeder recloser | Forced | None
OE-25-001461 | 11700 | 78 | 150 | HB-S01-02 | Harbor | 2025-04-30 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001462 | 29575 | 175 | 169 | PR-S13-05 | Prairie | 2025-04-30 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001463 | 5250 | 50 | 105 | BY-S25-04 | Bayou | 2025-04-30 | 14 | Animal | Lateral fuse | Forced | None
OE-25-001464 | 3384 | 36 | 94 | BY-S22-02 | Bayou | 2025-04-30 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001465 | 30800 | 220 | 140 | PR-S13-03 | Prairie | 2025-04-30 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-25-001466 | 712 | 8 | 89 | PR-S06-03 | Prairie | 2025-04-30 | 19 | Animal | Transformer fuse | Forced | None
OE-25-001467 | 19412 | 211 | 92 | CR-S14-02 | Crossroads | 2025-04-30 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001468 | 415 | 5 | 83 | HB-S13-01 | Harbor | 2025-05-01 | 7 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001469 | 1296 | 9 | 144 | BY-S06-02 | Bayou | 2025-05-01 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001470 | 194 | 1 | 194 | PR-S05-03 | Prairie | 2025-05-01 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001471 | 1456 | 7 | 208 | BY-S29-05 | Bayou | 2025-05-01 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001472 | 4984 | 28 | 178 | CR-S01-03 | Crossroads | 2025-05-01 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001473 | 113152 | 3536 | 32 | CR-S14-02 | Crossroads | 2025-05-01 | 14 | Weather - lightning | Substation breaker | Forced | None
OE-25-001474 | 732 | 4 | 183 | HB-S10-01 | Harbor | 2025-05-01 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001475 | 95 | 1 | 95 | BY-S13-05 | Bayou | 2025-05-01 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001476 | 6241 | 79 | 79 | BY-S21-02 | Bayou | 2025-05-01 | 16 | Animal | Lateral fuse | Forced | None
OE-25-001477 | 1064 | 7 | 152 | HB-S04-01 | Harbor | 2025-05-01 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-25-001478 | 565 | 5 | 113 | PR-S07-01 | Prairie | 2025-05-01 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001479 | 23048 | 67 | 344 | BY-S13-06 | Bayou | 2025-05-01 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001480 | 1104 | 12 | 92 | BY-S23-04 | Bayou | 2025-05-01 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001481 | 2747 | 67 | 41 | HB-S03-03 | Harbor | 2025-05-01 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001482 | 2405 | 13 | 185 | CR-S27-02 | Crossroads | 2025-05-01 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001483 | 950 | 10 | 95 | CR-S24-04 | Crossroads | 2025-05-01 | 20 | Unknown | Transformer fuse | Forced | None
OE-25-001484 | 26663 | 293 | 91 | BY-S13-04 | Bayou | 2025-05-01 | 21 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001485 | 2970 | 11 | 270 | CR-S30-06 | Crossroads | 2025-05-01 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001486 | 4080 | 34 | 120 | CR-S28-01 | Crossroads | 2025-05-02 | 3 | Animal | Lateral fuse | Forced | None
OE-25-001487 | 6808 | 37 | 184 | BY-S17-01 | Bayou | 2025-05-02 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001488 | 6517 | 49 | 133 | CR-S22-03 | Crossroads | 2025-05-02 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001489 | 1140 | 10 | 114 | HB-S13-01 | Harbor | 2025-05-02 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-001490 | 16445 | 143 | 115 | CR-S12-01 | Crossroads | 2025-05-02 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001491 | 1309 | 7 | 187 | BY-S05-03 | Bayou | 2025-05-02 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001492 | 904 | 8 | 113 | CR-S05-06 | Crossroads | 2025-05-02 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001493 | 30375 | 405 | 75 | CR-S22-04 | Crossroads | 2025-05-02 | 11 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-001494 | 2052 | 9 | 228 | PR-S03-05 | Prairie | 2025-05-02 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-001495 | 30740 | 145 | 212 | CR-S14-02 | Crossroads | 2025-05-02 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001496 | 12272 | 59 | 208 | BY-S18-05 | Bayou | 2025-05-02 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001497 | 1956 | 12 | 163 | CR-S30-01 | Crossroads | 2025-05-02 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001498 | 528 | 8 | 66 | BY-S06-03 | Bayou | 2025-05-02 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001499 | 1246 | 14 | 89 | BY-S29-03 | Bayou | 2025-05-02 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001500 | 645 | 5 | 129 | BY-S24-02 | Bayou | 2025-05-02 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-001501 | 1428 | 14 | 102 | CR-S32-01 | Crossroads | 2025-05-03 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001502 | 127440 | 3186 | 40 | BY-S15-02 | Bayou | 2025-05-03 | 2 | Vegetation | Substation breaker | Forced | None
OE-25-001503 | 1232 | 11 | 112 | HB-S12-03 | Harbor | 2025-05-03 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001504 | 112320 | 416 | 270 | PR-S15-03 | Prairie | 2025-05-03 | 7 | Weather - wind | Feeder recloser | Forced | None
OE-25-001505 | 53196 | 1023 | 52 | HB-S19-04 | Harbor | 2025-05-03 | 8 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001506 | 1656 | 12 | 138 | HB-S14-01 | Harbor | 2025-05-03 | 9 | Animal | Transformer fuse | Forced | None
OE-25-001507 | 896 | 8 | 112 | CR-S32-04 | Crossroads | 2025-05-03 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001508 | 1728 | 9 | 192 | BY-S27-03 | Bayou | 2025-05-03 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001509 | 531 | 9 | 59 | PR-S16-05 | Prairie | 2025-05-03 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001510 | 748 | 4 | 187 | BY-S16-02 | Bayou | 2025-05-03 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001511 | 14522 | 53 | 274 | PR-S17-01 | Prairie | 2025-05-03 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001512 | 81536 | 784 | 104 | BY-S16-05 | Bayou | 2025-05-03 | 21 | Weather - lightning | Feeder recloser | Forced | None
OE-25-001513 | 2345 | 35 | 67 | PR-S10-01 | Prairie | 2025-05-03 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001514 | 9717 | 123 | 79 | BY-S27-05 | Bayou | 2025-05-03 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001515 | 67269 | 1319 | 51 | BY-S27-06 | Bayou | 2025-05-04 | 3 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001516 | 513 | 3 | 171 | CR-S09-02 | Crossroads | 2025-05-04 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001517 | 6993 | 63 | 111 | BY-S05-01 | Bayou | 2025-05-04 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001518 | 19266 | 247 | 78 | CR-S19-02 | Crossroads | 2025-05-04 | 12 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-001519 | 1660 | 5 | 332 | HB-S14-01 | Harbor | 2025-05-04 | 16 | Unknown | Transformer fuse | Forced | None
OE-25-001520 | 2241 | 27 | 83 | BY-S13-03 | Bayou | 2025-05-04 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-001521 | 5355 | 45 | 119 | BY-S22-02 | Bayou | 2025-05-04 | 23 | Weather - wind | Lateral fuse | Forced | None
OE-25-001522 | 270 | 2 | 135 | HB-S20-02 | Harbor | 2025-05-05 | 5 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001523 | 944 | 4 | 236 | PR-S14-04 | Prairie | 2025-05-05 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001524 | 876 | 12 | 73 | CR-S18-02 | Crossroads | 2025-05-05 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001525 | 77994 | 1857 | 42 | BY-S07-02 | Bayou | 2025-05-05 | 9 | Animal | Substation breaker | Forced | None
OE-25-001526 | 26840 | 220 | 122 | HB-S20-05 | Harbor | 2025-05-05 | 14 | Unknown | Lateral fuse | Forced | None
OE-25-001527 | 8960 | 28 | 320 | CR-S22-01 | Crossroads | 2025-05-05 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001528 | 2528 | 16 | 158 | HB-S10-01 | Harbor | 2025-05-05 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-001529 | 5300 | 25 | 212 | PR-S08-01 | Prairie | 2025-05-05 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001530 | 37480 | 937 | 40 | CR-S06-02 | Crossroads | 2025-05-05 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001531 | 732 | 6 | 122 | BY-S29-02 | Bayou | 2025-05-05 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-001532 | 609 | 7 | 87 | PR-S18-06 | Prairie | 2025-05-05 | 22 | Animal | Transformer fuse | Forced | None
OE-25-001533 | 11264 | 64 | 176 | CR-S08-06 | Crossroads | 2025-05-05 | 23 | Weather - wind | Lateral fuse | Forced | None
OE-25-001534 | 4158 | 27 | 154 | CR-S29-02 | Crossroads | 2025-05-06 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001535 | 166 | 2 | 83 | BY-S25-05 | Bayou | 2025-05-06 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001536 | 1608 | 12 | 134 | CR-S04-03 | Crossroads | 2025-05-06 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001537 | 6327 | 57 | 111 | BY-S16-05 | Bayou | 2025-05-06 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001538 | 7475 | 25 | 299 | CR-S30-01 | Crossroads | 2025-05-06 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001539 | 113628 | 1114 | 102 | CR-S04-02 | Crossroads | 2025-05-06 | 9 | Animal | Feeder recloser | Forced | None
OE-25-001540 | 2475 | 9 | 275 | PR-S07-04 | Prairie | 2025-05-06 | 10 | Animal | Transformer fuse | Forced | None
OE-25-001541 | 2480 | 20 | 124 | BY-S09-04 | Bayou | 2025-05-06 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001542 | 720 | 6 | 120 | BY-S23-03 | Bayou | 2025-05-06 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001543 | 14616 | 348 | 42 | HB-S01-03 | Harbor | 2025-05-06 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001544 | 3675 | 105 | 35 | BY-S21-02 | Bayou | 2025-05-06 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001545 | 8352 | 87 | 96 | CR-S21-01 | Crossroads | 2025-05-06 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001546 | 116044 | 866 | 134 | BY-S05-02 | Bayou | 2025-05-06 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001547 | 1463 | 19 | 77 | CR-S07-03 | Crossroads | 2025-05-06 | 15 | Animal | Lateral fuse | Forced | None
OE-25-001548 | 585 | 3 | 195 | CR-S12-01 | Crossroads | 2025-05-06 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001549 | 7488 | 117 | 64 | HB-S09-02 | Harbor | 2025-05-06 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-001550 | 1235 | 13 | 95 | PR-S18-01 | Prairie | 2025-05-06 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001551 | 2303 | 47 | 49 | HB-S15-02 | Harbor | 2025-05-06 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-001552 | 5616 | 104 | 54 | CR-S04-01 | Crossroads | 2025-05-06 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001553 | 7998 | 86 | 93 | BY-S22-02 | Bayou | 2025-05-06 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001554 | 1610 | 23 | 70 | CR-S20-05 | Crossroads | 2025-05-07 | 4 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001555 | 80606 | 983 | 82 | BY-S29-02 | Bayou | 2025-05-07 | 5 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001556 | 300 | 6 | 50 | CR-S23-02 | Crossroads | 2025-05-07 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001557 | 5369 | 59 | 91 | BY-S30-01 | Bayou | 2025-05-07 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-001558 | 357 | 3 | 119 | BY-S15-05 | Bayou | 2025-05-07 | 10 | Animal | Transformer fuse | Forced | None
OE-25-001559 | 19865 | 145 | 137 | BY-S15-03 | Bayou | 2025-05-07 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001560 | 522 | 9 | 58 | CR-S03-03 | Crossroads | 2025-05-07 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001561 | 26877 | 289 | 93 | CR-S04-02 | Crossroads | 2025-05-07 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001562 | 3604 | 68 | 53 | BY-S17-02 | Bayou | 2025-05-07 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001563 | 12062 | 163 | 74 | HB-S11-01 | Harbor | 2025-05-07 | 17 | Animal | IGSD-isolated section | Forced | None
OE-25-001564 | 1281 | 7 | 183 | CR-S07-03 | Crossroads | 2025-05-07 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-001565 | 2688 | 64 | 42 | BY-S15-05 | Bayou | 2025-05-07 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001566 | 110 | 1 | 110 | HB-S18-01 | Harbor | 2025-05-07 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001567 | 570 | 5 | 114 | CR-S29-02 | Crossroads | 2025-05-08 | 3 | Vegetation | Transformer fuse | Forced | None
OE-25-001568 | 1428 | 12 | 119 | PR-S07-06 | Prairie | 2025-05-08 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001569 | 27477 | 387 | 71 | BY-S15-05 | Bayou | 2025-05-08 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001570 | 19740 | 940 | 21 | BY-S18-02 | Bayou | 2025-05-08 | 11 | Animal | Feeder recloser | Forced | None
OE-25-001571 | 1464 | 24 | 61 | CR-S24-03 | Crossroads | 2025-05-08 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-001572 | 4632 | 24 | 193 | BY-S27-01 | Bayou | 2025-05-08 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001573 | 5886 | 27 | 218 | HB-S01-05 | Harbor | 2025-05-08 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-001574 | 3978 | 102 | 39 | BY-S24-02 | Bayou | 2025-05-08 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001575 | 5382 | 46 | 117 | HB-S19-04 | Harbor | 2025-05-08 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001576 | 47200 | 400 | 118 | CR-S26-03 | Crossroads | 2025-05-08 | 15 | Vehicle or public | Feeder recloser | Forced | None
OE-25-001577 | 1809 | 27 | 67 | PR-S09-03 | Prairie | 2025-05-08 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-001578 | 901 | 17 | 53 | BY-S30-02 | Bayou | 2025-05-08 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001579 | 23800 | 136 | 175 | PR-S01-06 | Prairie | 2025-05-08 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001580 | 1176 | 21 | 56 | PR-S18-03 | Prairie | 2025-05-08 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001581 | 1680 | 14 | 120 | CR-S20-02 | Crossroads | 2025-05-08 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001582 | 143715 | 2145 | 67 | BY-S29-01 | Bayou | 2025-05-08 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001583 | 80948 | 1652 | 49 | BY-S21-01 | Bayou | 2025-05-08 | 21 | Vegetation | Substation breaker | Forced | None
OE-25-001584 | 1416 | 8 | 177 | HB-S01-05 | Harbor | 2025-05-08 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-001585 | 2730 | 26 | 105 | CR-S08-05 | Crossroads | 2025-05-09 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-25-001586 | 1590 | 6 | 265 | PR-S08-03 | Prairie | 2025-05-09 | 10 | Animal | Transformer fuse | Forced | None
OE-25-001587 | 875 | 5 | 175 | BY-S16-03 | Bayou | 2025-05-09 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-001588 | 552 | 6 | 92 | BY-S21-01 | Bayou | 2025-05-09 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001589 | 50367 | 489 | 103 | CR-S02-01 | Crossroads | 2025-05-09 | 13 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-001590 | 15322 | 163 | 94 | PR-S14-02 | Prairie | 2025-05-09 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001591 | 40044 | 426 | 94 | HB-S20-02 | Harbor | 2025-05-09 | 14 | Unknown | IGSD-isolated section | Forced | None
OE-25-001592 | 1000 | 8 | 125 | HB-S01-03 | Harbor | 2025-05-09 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001593 | 13104 | 126 | 104 | PR-S06-03 | Prairie | 2025-05-09 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-001594 | 9594 | 41 | 234 | PR-S14-01 | Prairie | 2025-05-09 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-001595 | 78514 | 1061 | 74 | BY-S16-06 | Bayou | 2025-05-09 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001596 | 1704 | 24 | 71 | CR-S31-03 | Crossroads | 2025-05-09 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001597 | 10464 | 109 | 96 | PR-S19-02 | Prairie | 2025-05-09 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001598 | 4551 | 41 | 111 | CR-S07-07 | Crossroads | 2025-05-09 | 22 | Unknown | Lateral fuse | Forced | None
OE-25-001599 | 2673 | 33 | 81 | CR-S28-04 | Crossroads | 2025-05-10 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001600 | 658 | 7 | 94 | CR-S05-03 | Crossroads | 2025-05-10 | 2 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001601 | 378 | 3 | 126 | CR-S14-02 | Crossroads | 2025-05-10 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001602 | 1133 | 11 | 103 | HB-S06-02 | Harbor | 2025-05-10 | 6 | Animal | Transformer fuse | Forced | None
OE-25-001603 | 1224 | 9 | 136 | HB-S19-04 | Harbor | 2025-05-10 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-25-001604 | 784 | 7 | 112 | PR-S08-03 | Prairie | 2025-05-10 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001605 | 2310 | 35 | 66 | BY-S23-03 | Bayou | 2025-05-10 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001606 | 1056 | 12 | 88 | BY-S30-01 | Bayou | 2025-05-10 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001607 | 511 | 7 | 73 | PR-S18-04 | Prairie | 2025-05-10 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001608 | 115 | 1 | 115 | CR-S14-06 | Crossroads | 2025-05-10 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-25-001609 | 2730 | 78 | 35 | BY-S10-03 | Bayou | 2025-05-10 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001610 | 1596 | 12 | 133 | CR-S13-04 | Crossroads | 2025-05-10 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-001611 | 91 | 1 | 91 | CR-S13-06 | Crossroads | 2025-05-10 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001612 | 2639 | 13 | 203 | BY-S19-02 | Bayou | 2025-05-10 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001613 | 22010 | 310 | 71 | CR-S22-02 | Crossroads | 2025-05-10 | 15 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-001614 | 30940 | 182 | 170 | PR-S16-04 | Prairie | 2025-05-10 | 15 | Animal | Lateral fuse | Forced | None
OE-25-001615 | 13515 | 85 | 159 | CR-S13-04 | Crossroads | 2025-05-10 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-001616 | 4128 | 12 | 344 | PR-S12-01 | Prairie | 2025-05-10 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001617 | 67732 | 1148 | 59 | CR-S04-03 | Crossroads | 2025-05-10 | 20 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001618 | 18963 | 129 | 147 | PR-S11-01 | Prairie | 2025-05-11 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001619 | 51253 | 107 | 479 | BY-S22-01 | Bayou | 2025-05-11 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001620 | 7656 | 66 | 116 | BY-S26-03 | Bayou | 2025-05-11 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-001621 | 98 | 1 | 98 | CR-S22-01 | Crossroads | 2025-05-11 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001622 | 664 | 2 | 332 | PR-S09-03 | Prairie | 2025-05-11 | 7 | Animal | Transformer fuse | Forced | None
OE-25-001623 | 79800 | 760 | 105 | BY-S14-01 | Bayou | 2025-05-11 | 8 | Weather - wind | Feeder recloser | Forced | None
OE-25-001624 | 850 | 5 | 170 | BY-S29-03 | Bayou | 2025-05-11 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001625 | 55762 | 569 | 98 | PR-S17-02 | Prairie | 2025-05-11 | 8 | Equipment - overhead | Substation breaker | Forced | None
OE-25-001626 | 150548 | 1234 | 122 | CR-S17-01 | Crossroads | 2025-05-11 | 9 | Animal | Feeder recloser | Forced | None
OE-25-001627 | 1512 | 8 | 189 | BY-S18-02 | Bayou | 2025-05-11 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001628 | 15254 | 58 | 263 | BY-S27-03 | Bayou | 2025-05-11 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001629 | 2754 | 6 | 459 | BY-S15-06 | Bayou | 2025-05-11 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001630 | 984 | 4 | 246 | BY-S22-02 | Bayou | 2025-05-11 | 15 | Animal | Transformer fuse | Forced | None
OE-25-001631 | 120872 | 1042 | 116 | HB-S10-03 | Harbor | 2025-05-11 | 16 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-001632 | 184 | 2 | 92 | CR-S14-03 | Crossroads | 2025-05-11 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001633 | 2704 | 13 | 208 | CR-S31-02 | Crossroads | 2025-05-11 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001634 | 12934 | 58 | 223 | CR-S30-04 | Crossroads | 2025-05-11 | 21 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001635 | 500 | 4 | 125 | PR-S19-03 | Prairie | 2025-05-11 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-25-001636 | 21624 | 159 | 136 | PR-S03-03 | Prairie | 2025-05-11 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-001637 | 88374 | 1339 | 66 | PR-S04-01 | Prairie | 2025-05-12 | 4 | Equipment - overhead | Substation breaker | Forced | None
OE-25-001638 | 23458 | 317 | 74 | PR-S18-01 | Prairie | 2025-05-12 | 6 | Weather - wind | Lateral fuse | Forced | None
OE-25-001639 | 68712 | 818 | 84 | BY-S18-02 | Bayou | 2025-05-12 | 7 | Vegetation | Feeder recloser | Forced | None
OE-25-001640 | 6612 | 12 | 551 | BY-S22-03 | Bayou | 2025-05-12 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-001641 | 31096 | 184 | 169 | BY-S26-01 | Bayou | 2025-05-12 | 10 | Animal | Lateral fuse | Forced | None
OE-25-001642 | 10755 | 45 | 239 | CR-S04-05 | Crossroads | 2025-05-12 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001643 | 14553 | 147 | 99 | HB-S10-03 | Harbor | 2025-05-12 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001644 | 2958 | 34 | 87 | CR-S23-04 | Crossroads | 2025-05-12 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001645 | 9701 | 89 | 109 | BY-S15-05 | Bayou | 2025-05-12 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001646 | 35400 | 590 | 60 | CR-S26-03 | Crossroads | 2025-05-12 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001647 | 2088 | 12 | 174 | BY-S11-03 | Bayou | 2025-05-12 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001648 | 372 | 1 | 372 | CR-S09-01 | Crossroads | 2025-05-12 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001649 | 680 | 5 | 136 | PR-S18-01 | Prairie | 2025-05-12 | 21 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001650 | 11004 | 84 | 131 | BY-S18-07 | Bayou | 2025-05-12 | 22 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001651 | 2076 | 12 | 173 | CR-S19-04 | Crossroads | 2025-05-13 | 2 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001652 | 980 | 14 | 70 | BY-S09-01 | Bayou | 2025-05-13 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-001653 | 17825 | 575 | 31 | CR-S09-01 | Crossroads | 2025-05-13 | 7 | Weather - wind | IGSD-isolated section | Forced | None
OE-25-001654 | 1021724 | 2111 | 484 | CR-S20-02 | Crossroads | 2025-05-13 | 8 | Animal | Feeder recloser | Forced | None
OE-25-001655 | 3045 | 29 | 105 | PR-S16-05 | Prairie | 2025-05-13 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001656 | 1460 | 10 | 146 | CR-S23-05 | Crossroads | 2025-05-13 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001657 | 1680 | 20 | 84 | HB-S14-04 | Harbor | 2025-05-13 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-001658 | 1260 | 9 | 140 | PR-S15-06 | Prairie | 2025-05-13 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001659 | 1824 | 16 | 114 | PR-S17-01 | Prairie | 2025-05-13 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001660 | 5824 | 28 | 208 | HB-S14-01 | Harbor | 2025-05-13 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-001661 | 4400 | 10 | 440 | PR-S14-04 | Prairie | 2025-05-13 | 16 | Animal | Transformer fuse | Forced | None
OE-25-001662 | 578 | 2 | 289 | PR-S19-03 | Prairie | 2025-05-13 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001663 | 3840 | 64 | 60 | BY-S16-01 | Bayou | 2025-05-13 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001664 | 1032 | 12 | 86 | BY-S18-04 | Bayou | 2025-05-13 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001665 | 7930 | 122 | 65 | BY-S22-01 | Bayou | 2025-05-13 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001666 | 2340 | 30 | 78 | BY-S25-02 | Bayou | 2025-05-14 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001667 | 15360 | 120 | 128 | BY-S10-01 | Bayou | 2025-05-14 | 1 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001668 | 35979 | 201 | 179 | PR-S03-05 | Prairie | 2025-05-14 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-001669 | 3393 | 87 | 39 | BY-S27-05 | Bayou | 2025-05-14 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-001670 | 1422 | 9 | 158 | CR-S05-03 | Crossroads | 2025-05-14 | 8 | Unknown | Transformer fuse | Forced | None
OE-25-001671 | 2144 | 8 | 268 | BY-S13-03 | Bayou | 2025-05-14 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001672 | 141358 | 161 | 878 | PR-S09-04 | Prairie | 2025-05-14 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001673 | 3094 | 17 | 182 | BY-S22-02 | Bayou | 2025-05-14 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001674 | 6110 | 47 | 130 | CR-S07-04 | Crossroads | 2025-05-14 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001675 | 5368 | 44 | 122 | CR-S13-06 | Crossroads | 2025-05-14 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001676 | 4992 | 32 | 156 | PR-S19-03 | Prairie | 2025-05-14 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001677 | 17170 | 170 | 101 | BY-S25-05 | Bayou | 2025-05-14 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001678 | 155617 | 2021 | 77 | CR-S04-03 | Crossroads | 2025-05-14 | 14 | Equipment - overhead | Substation breaker | Forced | None
OE-25-001679 | 2054 | 13 | 158 | PR-S14-01 | Prairie | 2025-05-14 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001680 | 1584 | 12 | 132 | PR-S13-02 | Prairie | 2025-05-14 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-001681 | 1820 | 13 | 140 | BY-S15-02 | Bayou | 2025-05-14 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001682 | 9450 | 70 | 135 | HB-S07-04 | Harbor | 2025-05-14 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-001683 | 5499 | 39 | 141 | PR-S03-02 | Prairie | 2025-05-14 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-001684 | 4896 | 48 | 102 | BY-S17-04 | Bayou | 2025-05-14 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-001685 | 574 | 7 | 82 | BY-S30-01 | Bayou | 2025-05-15 | 5 | Animal | Transformer fuse | Forced | None
OE-25-001686 | 1440 | 12 | 120 | HB-S16-05 | Harbor | 2025-05-15 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-001687 | 140 | 2 | 70 | BY-S13-04 | Bayou | 2025-05-15 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-25-001688 | 33575 | 79 | 425 | HB-S18-03 | Harbor | 2025-05-15 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001689 | 2025 | 15 | 135 | CR-S28-04 | Crossroads | 2025-05-15 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001690 | 4455 | 45 | 99 | HB-S07-02 | Harbor | 2025-05-15 | 11 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001691 | 2772 | 14 | 198 | PR-S12-01 | Prairie | 2025-05-15 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001692 | 28365 | 183 | 155 | HB-S18-01 | Harbor | 2025-05-15 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001693 | 228845 | 1237 | 185 | BY-S08-01 | Bayou | 2025-05-15 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-001694 | 380 | 5 | 76 | BY-S24-03 | Bayou | 2025-05-15 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-001695 | 57327 | 591 | 97 | CR-S23-01 | Crossroads | 2025-05-15 | 14 | Weather - wind | Feeder recloser | Forced | None
OE-25-001696 | 626 | 2 | 313 | BY-S18-05 | Bayou | 2025-05-15 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001697 | 20215 | 65 | 311 | BY-S16-04 | Bayou | 2025-05-15 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-001698 | 8904 | 53 | 168 | CR-S19-04 | Crossroads | 2025-05-15 | 17 | Animal | Lateral fuse | Forced | None
OE-25-001699 | 13818 | 94 | 147 | CR-S07-03 | Crossroads | 2025-05-15 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001700 | 3136 | 32 | 98 | CR-S29-02 | Crossroads | 2025-05-16 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001701 | 1333 | 43 | 31 | BY-S17-01 | Bayou | 2025-05-16 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-25-001702 | 609 | 3 | 203 | PR-S14-03 | Prairie | 2025-05-16 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001703 | 7224 | 129 | 56 | BY-S09-04 | Bayou | 2025-05-16 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001704 | 1582 | 14 | 113 | HB-S07-05 | Harbor | 2025-05-16 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001705 | 620 | 10 | 62 | BY-S03-01 | Bayou | 2025-05-16 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001706 | 8900 | 50 | 178 | HB-S08-04 | Harbor | 2025-05-16 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001707 | 1680 | 14 | 120 | HB-S09-05 | Harbor | 2025-05-16 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001708 | 1212 | 6 | 202 | PR-S06-02 | Prairie | 2025-05-16 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001709 | 27216 | 144 | 189 | BY-S07-01 | Bayou | 2025-05-16 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-001710 | 2430 | 9 | 270 | BY-S03-01 | Bayou | 2025-05-16 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-001711 | 825 | 11 | 75 | BY-S29-03 | Bayou | 2025-05-16 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001712 | 1328 | 8 | 166 | PR-S07-02 | Prairie | 2025-05-16 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-25-001713 | 11392 | 89 | 128 | BY-S13-04 | Bayou | 2025-05-16 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001714 | 2640 | 33 | 80 | BY-S15-05 | Bayou | 2025-05-17 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-001715 | 552 | 3 | 184 | HB-S12-02 | Harbor | 2025-05-17 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001716 | 2301 | 13 | 177 | HB-S10-03 | Harbor | 2025-05-17 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-25-001717 | 21510 | 239 | 90 | BY-S25-03 | Bayou | 2025-05-17 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001718 | 360 | 3 | 120 | CR-S07-07 | Crossroads | 2025-05-17 | 11 | Animal | Transformer fuse | Forced | None
OE-25-001719 | 781 | 11 | 71 | CR-S11-02 | Crossroads | 2025-05-17 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001720 | 1944 | 24 | 81 | PR-S14-01 | Prairie | 2025-05-17 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001721 | 53998 | 266 | 203 | BY-S16-02 | Bayou | 2025-05-17 | 13 | Vegetation | IGSD-isolated section | Forced | None
OE-25-001722 | 837 | 3 | 279 | BY-S23-01 | Bayou | 2025-05-17 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001723 | 1800 | 12 | 150 | CR-S06-01 | Crossroads | 2025-05-17 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001724 | 332 | 2 | 166 | PR-S02-01 | Prairie | 2025-05-17 | 14 | Animal | Transformer fuse | Forced | None
OE-25-001725 | 1278 | 9 | 142 | PR-S15-05 | Prairie | 2025-05-17 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-001726 | 76494 | 366 | 209 | BY-S13-04 | Bayou | 2025-05-17 | 15 | Weather - wind | Feeder recloser | Forced | None
OE-25-001727 | 105465 | 445 | 237 | BY-S15-05 | Bayou | 2025-05-17 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-001728 | 1595 | 11 | 145 | CR-S09-02 | Crossroads | 2025-05-17 | 15 | Animal | Transformer fuse | Forced | None
OE-25-001729 | 36582 | 469 | 78 | HB-S17-03 | Harbor | 2025-05-17 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001730 | 4186 | 26 | 161 | HB-S11-01 | Harbor | 2025-05-17 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-001731 | 6864 | 52 | 132 | BY-S13-04 | Bayou | 2025-05-17 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-001732 | 11975 | 25 | 479 | BY-S02-01 | Bayou | 2025-05-17 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001733 | 1302 | 6 | 217 | PR-S18-03 | Prairie | 2025-05-18 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001734 | 20410 | 130 | 157 | BY-S15-05 | Bayou | 2025-05-18 | 12 | Unknown | Lateral fuse | Forced | None
OE-25-001735 | 384 | 6 | 64 | CR-S12-02 | Crossroads | 2025-05-18 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-001736 | 3720 | 124 | 30 | CR-S06-03 | Crossroads | 2025-05-18 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001737 | 5621 | 73 | 77 | HB-S19-01 | Harbor | 2025-05-18 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-001738 | 6776 | 88 | 77 | PR-S13-01 | Prairie | 2025-05-18 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001739 | 39950 | 425 | 94 | PR-S14-01 | Prairie | 2025-05-18 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001740 | 17094 | 222 | 77 | CR-S16-05 | Crossroads | 2025-05-18 | 17 | Animal | Lateral fuse | Forced | None
OE-25-001741 | 107301 | 761 | 141 | CR-S15-01 | Crossroads | 2025-05-18 | 18 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001742 | 520 | 4 | 130 | CR-S20-03 | Crossroads | 2025-05-18 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001743 | 21978 | 666 | 33 | CR-S31-03 | Crossroads | 2025-05-18 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001744 | 1196 | 13 | 92 | PR-S01-02 | Prairie | 2025-05-18 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001745 | 32640 | 136 | 240 | CR-S21-03 | Crossroads | 2025-05-18 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001746 | 414 | 3 | 138 | PR-S07-03 | Prairie | 2025-05-18 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-001747 | 7440 | 93 | 80 | BY-S28-02 | Bayou | 2025-05-19 | 1 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001748 | 350 | 1 | 350 | BY-S19-02 | Bayou | 2025-05-19 | 6 | Weather - wind | Transformer fuse | Forced | None
OE-25-001749 | 906 | 6 | 151 | CR-S04-04 | Crossroads | 2025-05-19 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001750 | 8528 | 52 | 164 | BY-S10-02 | Bayou | 2025-05-19 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-001751 | 13494 | 519 | 26 | PR-S12-02 | Prairie | 2025-05-19 | 7 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-001752 | 1776 | 6 | 296 | CR-S02-01 | Crossroads | 2025-05-19 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001753 | 2275 | 13 | 175 | CR-S10-03 | Crossroads | 2025-05-19 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001754 | 12775 | 175 | 73 | CR-S30-02 | Crossroads | 2025-05-19 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001755 | 2816 | 22 | 128 | PR-S13-02 | Prairie | 2025-05-19 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001756 | 61307 | 607 | 101 | BY-S06-02 | Bayou | 2025-05-19 | 12 | Vegetation | IGSD-isolated section | Forced | None
OE-25-001757 | 25615 | 545 | 47 | BY-S14-03 | Bayou | 2025-05-19 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001758 | 1484 | 14 | 106 | CR-S10-02 | Crossroads | 2025-05-19 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001759 | 1482 | 13 | 114 | PR-S18-02 | Prairie | 2025-05-19 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001760 | 1971 | 9 | 219 | HB-S04-01 | Harbor | 2025-05-19 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001761 | 11180 | 43 | 260 | PR-S03-05 | Prairie | 2025-05-19 | 18 | Animal | Lateral fuse | Forced | None
OE-25-001762 | 1224 | 12 | 102 | HB-S20-01 | Harbor | 2025-05-19 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001763 | 136584 | 1084 | 126 | BY-S29-01 | Bayou | 2025-05-19 | 22 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-001764 | 22336 | 1396 | 16 | HB-S04-01 | Harbor | 2025-05-19 | 22 | Unknown | Substation breaker | Outside cause | None
OE-25-001765 | 27412 | 178 | 154 | CR-S28-04 | Crossroads | 2025-05-20 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001766 | 109068 | 732 | 149 | HB-S08-03 | Harbor | 2025-05-20 | 1 | Weather - wind | Substation breaker | Forced | None
OE-25-001767 | 106095 | 1929 | 55 | CR-S01-03 | Crossroads | 2025-05-20 | 5 | Weather - lightning | Substation breaker | Forced | None
OE-25-001768 | 6783 | 51 | 133 | PR-S10-03 | Prairie | 2025-05-20 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-001769 | 1547 | 13 | 119 | BY-S07-02 | Bayou | 2025-05-20 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001770 | 14190 | 66 | 215 | BY-S16-01 | Bayou | 2025-05-20 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-001771 | 1232 | 14 | 88 | BY-S18-06 | Bayou | 2025-05-20 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-001772 | 8856 | 164 | 54 | BY-S30-01 | Bayou | 2025-05-20 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-001773 | 141 | 1 | 141 | HB-S03-03 | Harbor | 2025-05-20 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001774 | 1456 | 8 | 182 | BY-S06-01 | Bayou | 2025-05-20 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001775 | 1540 | 35 | 44 | HB-S05-06 | Harbor | 2025-05-20 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-001776 | 876 | 6 | 146 | BY-S19-01 | Bayou | 2025-05-20 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-001777 | 13184 | 64 | 206 | BY-S19-02 | Bayou | 2025-05-20 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001778 | 4788 | 42 | 114 | BY-S26-02 | Bayou | 2025-05-20 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001779 | 35530 | 187 | 190 | BY-S26-03 | Bayou | 2025-05-20 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001780 | 40640 | 508 | 80 | CR-S30-06 | Crossroads | 2025-05-20 | 14 | Vehicle or public | Feeder recloser | Forced | None
OE-25-001781 | 1254 | 11 | 114 | HB-S01-05 | Harbor | 2025-05-20 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-001782 | 6480 | 72 | 90 | HB-S20-02 | Harbor | 2025-05-20 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001783 | 670 | 5 | 134 | PR-S18-06 | Prairie | 2025-05-20 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001784 | 7906 | 67 | 118 | CR-S09-02 | Crossroads | 2025-05-20 | 17 | Animal | Lateral fuse | Forced | None
OE-25-001785 | 2774 | 19 | 146 | CR-S13-06 | Crossroads | 2025-05-20 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001786 | 15222 | 86 | 177 | PR-S17-01 | Prairie | 2025-05-20 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-001787 | 4429 | 43 | 103 | HB-S12-01 | Harbor | 2025-05-21 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001788 | 704 | 4 | 176 | BY-S26-02 | Bayou | 2025-05-21 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-25-001789 | 832 | 13 | 64 | CR-S20-03 | Crossroads | 2025-05-21 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001790 | 8930 | 94 | 95 | HB-S13-01 | Harbor | 2025-05-21 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001791 | 11400 | 150 | 76 | CR-S27-04 | Crossroads | 2025-05-21 | 9 | Animal | Lateral fuse | Forced | None
OE-25-001792 | 1041 | 3 | 347 | PR-S02-02 | Prairie | 2025-05-21 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001793 | 2314 | 13 | 178 | BY-S07-06 | Bayou | 2025-05-21 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-25-001794 | 18286 | 82 | 223 | BY-S23-04 | Bayou | 2025-05-21 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001795 | 181712 | 1108 | 164 | HB-S06-02 | Harbor | 2025-05-21 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001796 | 52080 | 744 | 70 | CR-S14-05 | Crossroads | 2025-05-21 | 16 | Animal | Feeder recloser | Forced | None
OE-25-001797 | 5490 | 90 | 61 | PR-S03-03 | Prairie | 2025-05-21 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-001798 | 209207 | 1597 | 131 | PR-S08-02 | Prairie | 2025-05-21 | 20 | Weather - wind | Substation breaker | Forced | None
OE-25-001799 | 1053 | 13 | 81 | HB-S11-01 | Harbor | 2025-05-21 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-001800 | 300 | 5 | 60 | HB-S14-03 | Harbor | 2025-05-22 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-001801 | 2560 | 64 | 40 | BY-S13-04 | Bayou | 2025-05-22 | 1 | Vegetation | Lateral fuse | Forced | None
OE-25-001802 | 2256 | 48 | 47 | PR-S03-05 | Prairie | 2025-05-22 | 2 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001803 | 40369 | 553 | 73 | HB-S05-04 | Harbor | 2025-05-22 | 7 | Animal | Feeder recloser | Forced | None
OE-25-001804 | 4437 | 29 | 153 | BY-S02-02 | Bayou | 2025-05-22 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001805 | 4784 | 13 | 368 | BY-S15-03 | Bayou | 2025-05-22 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-001806 | 1316 | 7 | 188 | BY-S16-05 | Bayou | 2025-05-22 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001807 | 790 | 10 | 79 | PR-S14-04 | Prairie | 2025-05-22 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001808 | 4480 | 64 | 70 | BY-S07-05 | Bayou | 2025-05-22 | 12 | Animal | Lateral fuse | Forced | None
OE-25-001809 | 18328 | 316 | 58 | CR-S08-01 | Crossroads | 2025-05-22 | 12 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-001810 | 31050 | 690 | 45 | CR-S25-05 | Crossroads | 2025-05-22 | 13 | Animal | Feeder recloser | Forced | None
OE-25-001811 | 54140 | 2707 | 20 | CR-S09-01 | Crossroads | 2025-05-22 | 14 | Equipment - overhead | Substation breaker | Forced | None
OE-25-001812 | 216 | 3 | 72 | CR-S22-01 | Crossroads | 2025-05-22 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001813 | 12091 | 113 | 107 | CR-S24-04 | Crossroads | 2025-05-22 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001814 | 7930 | 61 | 130 | CR-S01-04 | Crossroads | 2025-05-22 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001815 | 171420 | 2857 | 60 | CR-S17-01 | Crossroads | 2025-05-22 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-001816 | 605 | 5 | 121 | CR-S15-03 | Crossroads | 2025-05-22 | 18 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001817 | 7168 | 112 | 64 | BY-S20-01 | Bayou | 2025-05-22 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-001818 | 91224 | 1448 | 63 | BY-S29-03 | Bayou | 2025-05-22 | 22 | Vegetation | Substation breaker | Forced | None
OE-25-001819 | 110 | 1 | 110 | PR-S07-06 | Prairie | 2025-05-22 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001820 | 11711 | 49 | 239 | HB-S11-01 | Harbor | 2025-05-22 | 23 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001821 | 48048 | 1232 | 39 | BY-S17-02 | Bayou | 2025-05-23 | 8 | Weather - lightning | Feeder recloser | Forced | None
OE-25-001822 | 82900 | 829 | 100 | CR-S07-03 | Crossroads | 2025-05-23 | 8 | Vehicle or public | IGSD-isolated section | Forced | None
OE-25-001823 | 1740 | 30 | 58 | PR-S01-05 | Prairie | 2025-05-23 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001824 | 5719 | 133 | 43 | BY-S16-03 | Bayou | 2025-05-23 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001825 | 474 | 3 | 158 | BY-S16-03 | Bayou | 2025-05-23 | 9 | Animal | Transformer fuse | Forced | None
OE-25-001826 | 880 | 11 | 80 | BY-S27-02 | Bayou | 2025-05-23 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001827 | 3360 | 42 | 80 | HB-S07-02 | Harbor | 2025-05-23 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001828 | 10494 | 66 | 159 | PR-S04-03 | Prairie | 2025-05-23 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001829 | 5428 | 23 | 236 | BY-S30-02 | Bayou | 2025-05-23 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001830 | 8235 | 61 | 135 | CR-S32-04 | Crossroads | 2025-05-23 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-001831 | 2340 | 12 | 195 | CR-S14-01 | Crossroads | 2025-05-23 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001832 | 8968 | 118 | 76 | BY-S17-04 | Bayou | 2025-05-23 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001833 | 1560 | 12 | 130 | CR-S05-05 | Crossroads | 2025-05-23 | 12 | Animal | Transformer fuse | Forced | None
OE-25-001834 | 6887 | 71 | 97 | HB-S01-05 | Harbor | 2025-05-23 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001835 | 5549 | 31 | 179 | HB-S03-01 | Harbor | 2025-05-23 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001836 | 400 | 4 | 100 | BY-S20-02 | Bayou | 2025-05-23 | 14 | Animal | Transformer fuse | Forced | None
OE-25-001837 | 675 | 5 | 135 | BY-S15-01 | Bayou | 2025-05-23 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001838 | 22338 | 146 | 153 | BY-S17-02 | Bayou | 2025-05-23 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001839 | 408 | 3 | 136 | BY-S24-03 | Bayou | 2025-05-23 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001840 | 624 | 6 | 104 | BY-S07-03 | Bayou | 2025-05-23 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001841 | 5000 | 50 | 100 | BY-S21-04 | Bayou | 2025-05-23 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001842 | 135680 | 1280 | 106 | BY-S19-02 | Bayou | 2025-05-23 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001843 | 968 | 8 | 121 | CR-S19-04 | Crossroads | 2025-05-23 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001844 | 18906 | 137 | 138 | CR-S21-01 | Crossroads | 2025-05-23 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001845 | 1122 | 11 | 102 | PR-S01-04 | Prairie | 2025-05-23 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001846 | 1248 | 6 | 208 | BY-S03-01 | Bayou | 2025-05-23 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001847 | 15197 | 91 | 167 | PR-S18-01 | Prairie | 2025-05-23 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001848 | 18270 | 105 | 174 | BY-S10-04 | Bayou | 2025-05-24 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-001849 | 1274 | 13 | 98 | BY-S30-03 | Bayou | 2025-05-24 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001850 | 320 | 1 | 320 | PR-S13-02 | Prairie | 2025-05-24 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001851 | 1719 | 9 | 191 | PR-S19-05 | Prairie | 2025-05-24 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-001852 | 120408 | 696 | 173 | BY-S06-02 | Bayou | 2025-05-24 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-001853 | 31263 | 613 | 51 | BY-S25-01 | Bayou | 2025-05-24 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001854 | 2871 | 11 | 261 | CR-S18-03 | Crossroads | 2025-05-24 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-25-001855 | 145 | 1 | 145 | BY-S12-02 | Bayou | 2025-05-24 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001856 | 509 | 1 | 509 | BY-S25-05 | Bayou | 2025-05-24 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-001857 | 19186 | 106 | 181 | PR-S03-06 | Prairie | 2025-05-24 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001858 | 276 | 6 | 46 | CR-S30-04 | Crossroads | 2025-05-24 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001859 | 50405 | 593 | 85 | CR-S31-01 | Crossroads | 2025-05-24 | 18 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-001860 | 31635 | 95 | 333 | BY-S27-06 | Bayou | 2025-05-24 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001861 | 1337 | 7 | 191 | CR-S19-01 | Crossroads | 2025-05-24 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001862 | 3375 | 9 | 375 | BY-S30-01 | Bayou | 2025-05-24 | 20 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001863 | 637 | 7 | 91 | CR-S16-05 | Crossroads | 2025-05-24 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001864 | 9676 | 59 | 164 | CR-S13-03 | Crossroads | 2025-05-24 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001865 | 1812 | 12 | 151 | BY-S18-04 | Bayou | 2025-05-25 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-25-001866 | 28124 | 178 | 158 | CR-S10-01 | Crossroads | 2025-05-25 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001867 | 1414 | 14 | 101 | CR-S11-01 | Crossroads | 2025-05-25 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001868 | 213446 | 779 | 274 | BY-S09-03 | Bayou | 2025-05-25 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001869 | 26362 | 538 | 49 | CR-S21-02 | Crossroads | 2025-05-25 | 12 | Weather - wind | Feeder recloser | Forced | None
OE-25-001870 | 850 | 5 | 170 | BY-S10-03 | Bayou | 2025-05-25 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-001871 | 4896 | 72 | 68 | HB-S09-04 | Harbor | 2025-05-25 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001872 | 681 | 3 | 227 | HB-S19-04 | Harbor | 2025-05-25 | 13 | Animal | Transformer fuse | Forced | None
OE-25-001873 | 2662 | 11 | 242 | PR-S03-03 | Prairie | 2025-05-25 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001874 | 204 | 2 | 102 | HB-S02-03 | Harbor | 2025-05-25 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001875 | 3066 | 42 | 73 | PR-S18-02 | Prairie | 2025-05-25 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001876 | 12144 | 276 | 44 | BY-S10-01 | Bayou | 2025-05-25 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001877 | 4256 | 56 | 76 | CR-S01-01 | Crossroads | 2025-05-25 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001878 | 95366 | 2326 | 41 | BY-S17-04 | Bayou | 2025-05-25 | 19 | Vegetation | Substation breaker | Forced | None
OE-25-001879 | 585 | 13 | 45 | HB-S12-02 | Harbor | 2025-05-25 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-001880 | 685 | 5 | 137 | BY-S16-01 | Bayou | 2025-05-25 | 22 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001881 | 3744 | 13 | 288 | BY-S24-02 | Bayou | 2025-05-26 | 11 | Animal | Transformer fuse | Forced | None
OE-25-001882 | 603 | 9 | 67 | BY-S23-05 | Bayou | 2025-05-26 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-001883 | 7881 | 71 | 111 | CR-S14-03 | Crossroads | 2025-05-26 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-001884 | 1806 | 14 | 129 | HB-S11-02 | Harbor | 2025-05-26 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-001885 | 9882 | 122 | 81 | CR-S27-04 | Crossroads | 2025-05-26 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001886 | 13719 | 51 | 269 | BY-S28-02 | Bayou | 2025-05-26 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-001887 | 1062 | 9 | 118 | HB-S12-03 | Harbor | 2025-05-26 | 15 | Animal | Transformer fuse | Forced | None
OE-25-001888 | 89326 | 1514 | 59 | PR-S08-02 | Prairie | 2025-05-26 | 16 | Weather - lightning | Substation breaker | Forced | None
OE-25-001889 | 1690 | 10 | 169 | PR-S10-03 | Prairie | 2025-05-26 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001890 | 14835 | 129 | 115 | HB-S11-01 | Harbor | 2025-05-26 | 18 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-001891 | 1845 | 9 | 205 | BY-S26-01 | Bayou | 2025-05-27 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001892 | 5457 | 51 | 107 | BY-S08-02 | Bayou | 2025-05-27 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001893 | 4884 | 37 | 132 | PR-S07-04 | Prairie | 2025-05-27 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001894 | 1920 | 10 | 192 | CR-S25-04 | Crossroads | 2025-05-27 | 12 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001895 | 5945 | 41 | 145 | PR-S18-02 | Prairie | 2025-05-27 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001896 | 102214 | 343 | 298 | CR-S26-04 | Crossroads | 2025-05-27 | 13 | Weather - lightning | Feeder recloser | Forced | None
OE-25-001897 | 134 | 1 | 134 | PR-S01-01 | Prairie | 2025-05-27 | 13 | Unknown | Transformer fuse | Forced | None
OE-25-001898 | 1600 | 8 | 200 | BY-S13-05 | Bayou | 2025-05-27 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-001899 | 1944 | 8 | 243 | HB-S03-02 | Harbor | 2025-05-27 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001900 | 1547 | 13 | 119 | PR-S04-02 | Prairie | 2025-05-27 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-001901 | 1755 | 9 | 195 | CR-S20-05 | Crossroads | 2025-05-27 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001902 | 3848 | 74 | 52 | PR-S10-01 | Prairie | 2025-05-27 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001903 | 805 | 7 | 115 | CR-S26-05 | Crossroads | 2025-05-27 | 18 | Animal | Transformer fuse | Forced | None
OE-25-001904 | 20066 | 79 | 254 | HB-S07-02 | Harbor | 2025-05-27 | 18 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001905 | 4181 | 37 | 113 | BY-S30-03 | Bayou | 2025-05-27 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-001906 | 15900 | 75 | 212 | BY-S02-01 | Bayou | 2025-05-27 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001907 | 25718 | 154 | 167 | BY-S18-03 | Bayou | 2025-05-27 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001908 | 780 | 10 | 78 | CR-S04-03 | Crossroads | 2025-05-27 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001909 | 197722 | 3409 | 58 | CR-S20-02 | Crossroads | 2025-05-28 | 6 | Vegetation | Substation breaker | Forced | None
OE-25-001910 | 7935 | 115 | 69 | PR-S03-05 | Prairie | 2025-05-28 | 6 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001911 | 5328 | 36 | 148 | BY-S11-01 | Bayou | 2025-05-28 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001912 | 564 | 4 | 141 | BY-S25-04 | Bayou | 2025-05-28 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001913 | 22380 | 373 | 60 | CR-S09-03 | Crossroads | 2025-05-28 | 8 | Equipment - underground | Feeder recloser | Forced | None
OE-25-001914 | 130977 | 1323 | 99 | HB-S15-03 | Harbor | 2025-05-28 | 9 | Animal | Feeder recloser | Forced | None
OE-25-001915 | 8064 | 72 | 112 | BY-S16-04 | Bayou | 2025-05-28 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001916 | 18360 | 170 | 108 | PR-S20-03 | Prairie | 2025-05-28 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-001917 | 640 | 8 | 80 | CR-S08-06 | Crossroads | 2025-05-28 | 14 | Animal | Transformer fuse | Forced | None
OE-25-001918 | 3705 | 65 | 57 | BY-S23-01 | Bayou | 2025-05-28 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001919 | 5530 | 70 | 79 | HB-S12-02 | Harbor | 2025-05-28 | 15 | Animal | Lateral fuse | Forced | None
OE-25-001920 | 2184 | 13 | 168 | CR-S14-03 | Crossroads | 2025-05-28 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001921 | 17954 | 94 | 191 | PR-S19-01 | Prairie | 2025-05-28 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-001922 | 1918 | 14 | 137 | PR-S09-01 | Prairie | 2025-05-28 | 23 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001923 | 490 | 5 | 98 | CR-S18-03 | Crossroads | 2025-05-29 | 0 | Animal | Transformer fuse | Forced | None
OE-25-001924 | 430 | 2 | 215 | BY-S16-01 | Bayou | 2025-05-29 | 2 | Vegetation | Transformer fuse | Forced | None
OE-25-001925 | 6161 | 101 | 61 | BY-S06-03 | Bayou | 2025-05-29 | 6 | Animal | Lateral fuse | Forced | None
OE-25-001926 | 1098 | 9 | 122 | BY-S13-04 | Bayou | 2025-05-29 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-001927 | 900 | 5 | 180 | PR-S18-04 | Prairie | 2025-05-29 | 9 | Animal | Transformer fuse | Forced | None
OE-25-001928 | 4488 | 44 | 102 | BY-S07-05 | Bayou | 2025-05-29 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001929 | 11816 | 56 | 211 | CR-S23-04 | Crossroads | 2025-05-29 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001930 | 2016 | 6 | 336 | BY-S06-02 | Bayou | 2025-05-29 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-001931 | 3312 | 24 | 138 | CR-S13-04 | Crossroads | 2025-05-29 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001932 | 1320 | 8 | 165 | PR-S19-02 | Prairie | 2025-05-29 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-25-001933 | 672 | 8 | 84 | CR-S02-03 | Crossroads | 2025-05-29 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001934 | 1885 | 29 | 65 | CR-S18-03 | Crossroads | 2025-05-29 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001935 | 186320 | 1370 | 136 | HB-S17-02 | Harbor | 2025-05-29 | 14 | Vehicle or public | Feeder recloser | Forced | None
OE-25-001936 | 54264 | 532 | 102 | BY-S23-01 | Bayou | 2025-05-29 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-001937 | 8036 | 49 | 164 | BY-S11-02 | Bayou | 2025-05-29 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-001938 | 4387 | 41 | 107 | HB-S05-04 | Harbor | 2025-05-29 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001939 | 1834 | 14 | 131 | CR-S16-05 | Crossroads | 2025-05-29 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001940 | 8165 | 71 | 115 | PR-S01-01 | Prairie | 2025-05-29 | 23 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001941 | 91 | 1 | 91 | CR-S27-02 | Crossroads | 2025-05-30 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-001942 | 940 | 10 | 94 | CR-S07-05 | Crossroads | 2025-05-30 | 10 | Animal | Transformer fuse | Forced | None
OE-25-001943 | 5832 | 36 | 162 | CR-S16-05 | Crossroads | 2025-05-30 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001944 | 1102 | 29 | 38 | BY-S14-02 | Bayou | 2025-05-30 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-001945 | 11374 | 47 | 242 | CR-S11-02 | Crossroads | 2025-05-30 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001946 | 6930 | 99 | 70 | PR-S18-05 | Prairie | 2025-05-30 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-001947 | 218 | 2 | 109 | HB-S09-03 | Harbor | 2025-05-30 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001948 | 9152 | 176 | 52 | BY-S30-02 | Bayou | 2025-05-30 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001949 | 334 | 2 | 167 | BY-S23-01 | Bayou | 2025-05-30 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001950 | 420 | 5 | 84 | CR-S30-06 | Crossroads | 2025-05-30 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-001951 | 60696 | 562 | 108 | HB-S04-01 | Harbor | 2025-05-30 | 17 | Vehicle or public | Feeder recloser | Forced | None
OE-25-001952 | 1392 | 29 | 48 | BY-S09-03 | Bayou | 2025-05-30 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-001953 | 3234 | 49 | 66 | BY-S29-04 | Bayou | 2025-05-30 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-001954 | 1014 | 6 | 169 | BY-S13-05 | Bayou | 2025-05-30 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-001955 | 37800 | 504 | 75 | BY-S26-01 | Bayou | 2025-05-30 | 23 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001956 | 41265 | 131 | 315 | PR-S18-04 | Prairie | 2025-05-30 | 23 | Vegetation | Lateral fuse | Forced | None
OE-25-001957 | 5208 | 56 | 93 | HB-S01-05 | Harbor | 2025-05-31 | 1 | Vegetation | Lateral fuse | Forced | None
OE-25-001958 | 2030 | 10 | 203 | BY-S19-01 | Bayou | 2025-05-31 | 4 | Vegetation | Transformer fuse | Forced | None
OE-25-001959 | 14560 | 112 | 130 | CR-S23-02 | Crossroads | 2025-05-31 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001960 | 370 | 5 | 74 | CR-S14-05 | Crossroads | 2025-05-31 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001961 | 1121 | 19 | 59 | CR-S27-03 | Crossroads | 2025-05-31 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-25-001962 | 25878 | 681 | 38 | HB-S10-01 | Harbor | 2025-05-31 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001963 | 74822 | 358 | 209 | PR-S09-02 | Prairie | 2025-05-31 | 7 | Weather - wind | Feeder recloser | Forced | None
OE-25-001964 | 46450 | 929 | 50 | HB-S01-03 | Harbor | 2025-05-31 | 8 | Unknown | Feeder recloser | Forced | None
OE-25-001965 | 2786 | 7 | 398 | PR-S07-01 | Prairie | 2025-05-31 | 9 | Animal | Transformer fuse | Forced | None
OE-25-001966 | 156 | 6 | 26 | HB-S13-01 | Harbor | 2025-05-31 | 10 | Animal | Transformer fuse | Forced | None
OE-25-001967 | 42460 | 386 | 110 | BY-S18-05 | Bayou | 2025-05-31 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-001968 | 15582 | 294 | 53 | CR-S04-04 | Crossroads | 2025-05-31 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-001969 | 544 | 4 | 136 | CR-S04-05 | Crossroads | 2025-05-31 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001970 | 11468 | 94 | 122 | CR-S19-03 | Crossroads | 2025-05-31 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-001971 | 2295 | 9 | 255 | BY-S15-01 | Bayou | 2025-05-31 | 17 | Animal | Transformer fuse | Forced | None
OE-25-001972 | 11368 | 58 | 196 | CR-S10-03 | Crossroads | 2025-05-31 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-001973 | 80800 | 505 | 160 | CR-S16-06 | Crossroads | 2025-05-31 | 17 | Weather - wind | Feeder recloser | Forced | None
OE-25-001974 | 975 | 5 | 195 | CR-S32-05 | Crossroads | 2025-05-31 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-001975 | 3036 | 33 | 92 | BY-S26-03 | Bayou | 2025-05-31 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-001976 | 264 | 4 | 66 | PR-S17-01 | Prairie | 2025-06-01 | 1 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001977 | 8150 | 50 | 163 | CR-S24-03 | Crossroads | 2025-06-01 | 3 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001978 | 184040 | 1720 | 107 | BY-S29-04 | Bayou | 2025-06-01 | 5 | Vegetation | Feeder recloser | Forced | None
OE-25-001979 | 660 | 10 | 66 | CR-S32-03 | Crossroads | 2025-06-01 | 7 | Unknown | Transformer fuse | Forced | None
OE-25-001980 | 2040 | 10 | 204 | BY-S27-06 | Bayou | 2025-06-01 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-25-001981 | 7884 | 73 | 108 | CR-S14-01 | Crossroads | 2025-06-01 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001982 | 128084 | 3124 | 41 | CR-S09-01 | Crossroads | 2025-06-01 | 11 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-001983 | 14432 | 82 | 176 | CR-S21-01 | Crossroads | 2025-06-01 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-001984 | 530 | 2 | 265 | BY-S19-03 | Bayou | 2025-06-01 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001985 | 1266 | 6 | 211 | HB-S13-02 | Harbor | 2025-06-01 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-001986 | 124 | 1 | 124 | CR-S07-05 | Crossroads | 2025-06-01 | 16 | Unknown | Transformer fuse | Forced | None
OE-25-001987 | 1812 | 12 | 151 | BY-S13-01 | Bayou | 2025-06-01 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-001988 | 8120 | 56 | 145 | PR-S20-01 | Prairie | 2025-06-01 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001989 | 13860 | 105 | 132 | PR-S12-01 | Prairie | 2025-06-01 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001990 | 1136 | 8 | 142 | BY-S25-05 | Bayou | 2025-06-01 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-001991 | 4960 | 40 | 124 | HB-S05-03 | Harbor | 2025-06-01 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001992 | 19071 | 117 | 163 | PR-S20-03 | Prairie | 2025-06-01 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-001993 | 1547 | 17 | 91 | CR-S10-02 | Crossroads | 2025-06-02 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001994 | 2184 | 12 | 182 | CR-S16-04 | Crossroads | 2025-06-02 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001995 | 32096 | 272 | 118 | CR-S23-01 | Crossroads | 2025-06-02 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-001996 | 3040 | 20 | 152 | CR-S05-01 | Crossroads | 2025-06-02 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-001997 | 57120 | 680 | 84 | BY-S18-06 | Bayou | 2025-06-02 | 14 | Weather - lightning | Feeder recloser | Forced | None
OE-25-001998 | 576 | 12 | 48 | BY-S28-03 | Bayou | 2025-06-02 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-001999 | 1196 | 13 | 92 | HB-S06-03 | Harbor | 2025-06-02 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002000 | 2860 | 10 | 286 | PR-S12-03 | Prairie | 2025-06-02 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-002001 | 616 | 8 | 77 | PR-S02-02 | Prairie | 2025-06-02 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-002002 | 1020 | 17 | 60 | CR-S06-03 | Crossroads | 2025-06-02 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002003 | 121002 | 1806 | 67 | HB-S10-03 | Harbor | 2025-06-02 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002004 | 780 | 12 | 65 | HB-S19-04 | Harbor | 2025-06-02 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-002005 | 1244 | 4 | 311 | PR-S19-03 | Prairie | 2025-06-02 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002006 | 2760 | 23 | 120 | BY-S26-03 | Bayou | 2025-06-02 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002007 | 6123 | 39 | 157 | CR-S13-06 | Crossroads | 2025-06-03 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002008 | 570 | 19 | 30 | CR-S12-02 | Crossroads | 2025-06-03 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-002009 | 7189 | 79 | 91 | CR-S05-06 | Crossroads | 2025-06-03 | 10 | Animal | Lateral fuse | Forced | None
OE-25-002010 | 29547 | 469 | 63 | CR-S03-02 | Crossroads | 2025-06-03 | 11 | Animal | IGSD-isolated section | Forced | None
OE-25-002011 | 5429 | 89 | 61 | CR-S18-05 | Crossroads | 2025-06-03 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-25-002012 | 648 | 9 | 72 | PR-S19-03 | Prairie | 2025-06-03 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002013 | 592 | 4 | 148 | BY-S17-01 | Bayou | 2025-06-03 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-002014 | 6290 | 74 | 85 | CR-S23-05 | Crossroads | 2025-06-03 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002015 | 2716 | 14 | 194 | BY-S21-05 | Bayou | 2025-06-03 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002016 | 340 | 4 | 85 | CR-S32-04 | Crossroads | 2025-06-04 | 5 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002017 | 784 | 7 | 112 | BY-S22-03 | Bayou | 2025-06-04 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002018 | 1050 | 6 | 175 | CR-S30-02 | Crossroads | 2025-06-04 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002019 | 147 | 1 | 147 | CR-S31-01 | Crossroads | 2025-06-04 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002020 | 8840 | 65 | 136 | BY-S03-03 | Bayou | 2025-06-04 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-002021 | 891 | 9 | 99 | BY-S25-04 | Bayou | 2025-06-04 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002022 | 828 | 6 | 138 | CR-S07-03 | Crossroads | 2025-06-04 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002023 | 4706 | 26 | 181 | HB-S12-01 | Harbor | 2025-06-04 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002024 | 1312 | 8 | 164 | BY-S07-02 | Bayou | 2025-06-04 | 13 | Unknown | Transformer fuse | Forced | None
OE-25-002025 | 1036 | 7 | 148 | CR-S14-03 | Crossroads | 2025-06-04 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002026 | 6561 | 81 | 81 | BY-S23-02 | Bayou | 2025-06-04 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002027 | 12080 | 80 | 151 | BY-S26-03 | Bayou | 2025-06-04 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002028 | 5980 | 46 | 130 | BY-S13-06 | Bayou | 2025-06-04 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002029 | 158002 | 767 | 206 | HB-S05-03 | Harbor | 2025-06-04 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002030 | 4982 | 47 | 106 | HB-S13-02 | Harbor | 2025-06-04 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002031 | 882 | 9 | 98 | BY-S13-06 | Bayou | 2025-06-04 | 20 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002032 | 159744 | 1024 | 156 | BY-S17-01 | Bayou | 2025-06-04 | 23 | Unknown | Feeder recloser | Forced | None
OE-25-002033 | 18582 | 163 | 114 | PR-S15-05 | Prairie | 2025-06-05 | 0 | Vegetation | Feeder recloser | Forced | None
OE-25-002034 | 15048 | 88 | 171 | HB-S14-04 | Harbor | 2025-06-05 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002035 | 76380 | 285 | 268 | PR-S13-05 | Prairie | 2025-06-05 | 6 | Weather - wind | Feeder recloser | Forced | None
OE-25-002036 | 3400 | 34 | 100 | CR-S08-01 | Crossroads | 2025-06-05 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002037 | 16821 | 189 | 89 | CR-S23-01 | Crossroads | 2025-06-05 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-002038 | 3429 | 27 | 127 | CR-S25-01 | Crossroads | 2025-06-05 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002039 | 1220 | 10 | 122 | BY-S23-03 | Bayou | 2025-06-05 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002040 | 3132 | 54 | 58 | BY-S27-04 | Bayou | 2025-06-05 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-002041 | 2415 | 7 | 345 | CR-S09-04 | Crossroads | 2025-06-05 | 12 | Unknown | Transformer fuse | Forced | None
OE-25-002042 | 1236 | 12 | 103 | PR-S01-06 | Prairie | 2025-06-05 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-002043 | 2684 | 11 | 244 | BY-S30-01 | Bayou | 2025-06-05 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002044 | 3520 | 88 | 40 | CR-S22-03 | Crossroads | 2025-06-05 | 14 | Unknown | Lateral fuse | Forced | None
OE-25-002045 | 4738 | 46 | 103 | CR-S14-02 | Crossroads | 2025-06-05 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002046 | 1115 | 5 | 223 | CR-S22-04 | Crossroads | 2025-06-05 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002047 | 20520 | 95 | 216 | PR-S20-01 | Prairie | 2025-06-05 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-002048 | 9782 | 134 | 73 | BY-S08-02 | Bayou | 2025-06-05 | 19 | Unknown | Lateral fuse | Forced | None
OE-25-002049 | 6533 | 47 | 139 | CR-S09-01 | Crossroads | 2025-06-05 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002050 | 4588 | 37 | 124 | BY-S13-02 | Bayou | 2025-06-05 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-002051 | 744 | 8 | 93 | BY-S07-01 | Bayou | 2025-06-05 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002052 | 16176 | 337 | 48 | HB-S10-02 | Harbor | 2025-06-05 | 22 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-002053 | 187 | 1 | 187 | HB-S11-01 | Harbor | 2025-06-05 | 22 | Unknown | Transformer fuse | Forced | None
OE-25-002054 | 8366 | 89 | 94 | BY-S05-02 | Bayou | 2025-06-06 | 4 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002055 | 165300 | 950 | 174 | CR-S25-03 | Crossroads | 2025-06-06 | 5 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002056 | 994 | 7 | 142 | CR-S14-02 | Crossroads | 2025-06-06 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-002057 | 3198 | 82 | 39 | BY-S11-03 | Bayou | 2025-06-06 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002058 | 4134 | 53 | 78 | PR-S07-05 | Prairie | 2025-06-06 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002059 | 1518 | 22 | 69 | BY-S20-03 | Bayou | 2025-06-06 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002060 | 2660 | 28 | 95 | BY-S13-02 | Bayou | 2025-06-06 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-002061 | 3801 | 21 | 181 | PR-S13-05 | Prairie | 2025-06-06 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002062 | 16240 | 116 | 140 | BY-S15-03 | Bayou | 2025-06-06 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002063 | 548 | 4 | 137 | BY-S23-01 | Bayou | 2025-06-06 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002064 | 5346 | 66 | 81 | BY-S18-06 | Bayou | 2025-06-06 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-002065 | 880 | 8 | 110 | PR-S01-05 | Prairie | 2025-06-06 | 17 | Animal | Transformer fuse | Forced | None
OE-25-002066 | 822 | 3 | 274 | PR-S14-04 | Prairie | 2025-06-06 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002067 | 33792 | 1056 | 32 | BY-S08-02 | Bayou | 2025-06-06 | 19 | Equipment - overhead | Substation breaker | Forced | None
OE-25-002068 | 2249 | 13 | 173 | CR-S02-03 | Crossroads | 2025-06-07 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-25-002069 | 12744 | 177 | 72 | HB-S12-03 | Harbor | 2025-06-07 | 7 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002070 | 6096 | 24 | 254 | HB-S05-04 | Harbor | 2025-06-07 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-002071 | 2331 | 37 | 63 | BY-S10-01 | Bayou | 2025-06-07 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002072 | 13056 | 102 | 128 | CR-S32-03 | Crossroads | 2025-06-07 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-002073 | 15022 | 203 | 74 | PR-S10-01 | Prairie | 2025-06-07 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-002074 | 3276 | 7 | 468 | PR-S18-01 | Prairie | 2025-06-07 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-002075 | 72500 | 1250 | 58 | CR-S20-03 | Crossroads | 2025-06-07 | 12 | Equipment - underground | Substation breaker | Forced | None
OE-25-002076 | 11850 | 150 | 79 | PR-S05-02 | Prairie | 2025-06-07 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002077 | 7040 | 22 | 320 | BY-S13-04 | Bayou | 2025-06-07 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-002078 | 48555 | 747 | 65 | PR-S07-03 | Prairie | 2025-06-07 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002079 | 10353 | 87 | 119 | BY-S10-03 | Bayou | 2025-06-07 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-002080 | 2380 | 35 | 68 | CR-S25-02 | Crossroads | 2025-06-07 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-002081 | 475 | 5 | 95 | CR-S30-07 | Crossroads | 2025-06-07 | 15 | Animal | Transformer fuse | Forced | None
OE-25-002082 | 1287 | 9 | 143 | BY-S06-01 | Bayou | 2025-06-07 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002083 | 158 | 2 | 79 | HB-S14-03 | Harbor | 2025-06-07 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-002084 | 1666 | 14 | 119 | BY-S23-05 | Bayou | 2025-06-07 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-002085 | 48495 | 795 | 61 | PR-S03-05 | Prairie | 2025-06-07 | 23 | Vegetation | Feeder recloser | Forced | None
OE-25-002086 | 4960 | 62 | 80 | BY-S15-02 | Bayou | 2025-06-08 | 2 | Vegetation | Lateral fuse | Forced | None
OE-25-002087 | 22080 | 138 | 160 | CR-S14-04 | Crossroads | 2025-06-08 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002088 | 822 | 6 | 137 | BY-S04-01 | Bayou | 2025-06-08 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-002089 | 155708 | 1162 | 134 | BY-S15-02 | Bayou | 2025-06-08 | 11 | Unknown | Feeder recloser | Forced | None
OE-25-002090 | 1344 | 32 | 42 | BY-S18-01 | Bayou | 2025-06-08 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002091 | 1170 | 6 | 195 | BY-S24-04 | Bayou | 2025-06-08 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002092 | 7566 | 78 | 97 | CR-S29-02 | Crossroads | 2025-06-08 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002093 | 10164 | 42 | 242 | PR-S13-03 | Prairie | 2025-06-08 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002094 | 7462 | 26 | 287 | BY-S19-02 | Bayou | 2025-06-08 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-002095 | 4606 | 98 | 47 | CR-S08-02 | Crossroads | 2025-06-08 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002096 | 7150 | 55 | 130 | BY-S06-02 | Bayou | 2025-06-08 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-002097 | 2548 | 14 | 182 | CR-S15-03 | Crossroads | 2025-06-08 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002098 | 236 | 4 | 59 | CR-S26-04 | Crossroads | 2025-06-09 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002099 | 13300 | 100 | 133 | HB-S03-02 | Harbor | 2025-06-09 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002100 | 5550 | 50 | 111 | CR-S06-02 | Crossroads | 2025-06-09 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002101 | 12879 | 159 | 81 | BY-S21-05 | Bayou | 2025-06-09 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002102 | 98800 | 988 | 100 | BY-S07-02 | Bayou | 2025-06-09 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002103 | 234 | 1 | 234 | PR-S10-02 | Prairie | 2025-06-09 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002104 | 18100 | 100 | 181 | BY-S18-01 | Bayou | 2025-06-09 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002105 | 4284 | 42 | 102 | PR-S18-02 | Prairie | 2025-06-09 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-002106 | 136 | 2 | 68 | CR-S09-05 | Crossroads | 2025-06-09 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-002107 | 2613 | 39 | 67 | CR-S30-04 | Crossroads | 2025-06-09 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-002108 | 1628 | 11 | 148 | HB-S18-03 | Harbor | 2025-06-09 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002109 | 10098 | 99 | 102 | PR-S07-02 | Prairie | 2025-06-09 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-002110 | 2088 | 12 | 174 | PR-S06-03 | Prairie | 2025-06-09 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-25-002111 | 30360 | 184 | 165 | PR-S07-03 | Prairie | 2025-06-09 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-002112 | 135030 | 1929 | 70 | HB-S14-04 | Harbor | 2025-06-10 | 2 | Equipment - underground | Substation breaker | Forced | None
OE-25-002113 | 1798 | 31 | 58 | CR-S09-05 | Crossroads | 2025-06-10 | 4 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002114 | 20944 | 476 | 44 | HB-S08-03 | Harbor | 2025-06-10 | 6 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002115 | 4446 | 39 | 114 | CR-S05-01 | Crossroads | 2025-06-10 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002116 | 168 | 3 | 56 | BY-S23-01 | Bayou | 2025-06-10 | 10 | Animal | Transformer fuse | Forced | None
OE-25-002117 | 329654 | 806 | 409 | BY-S05-02 | Bayou | 2025-06-10 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-002118 | 6360 | 106 | 60 | HB-S10-03 | Harbor | 2025-06-10 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-002119 | 2210 | 26 | 85 | BY-S21-05 | Bayou | 2025-06-10 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002120 | 29548 | 332 | 89 | PR-S19-02 | Prairie | 2025-06-10 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-25-002121 | 1120 | 10 | 112 | HB-S05-03 | Harbor | 2025-06-11 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-25-002122 | 715 | 13 | 55 | CR-S29-02 | Crossroads | 2025-06-11 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002123 | 41658 | 318 | 131 | PR-S05-03 | Prairie | 2025-06-11 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002124 | 432 | 6 | 72 | HB-S04-01 | Harbor | 2025-06-11 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002125 | 2392 | 13 | 184 | PR-S02-02 | Prairie | 2025-06-11 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002126 | 2628 | 12 | 219 | PR-S09-04 | Prairie | 2025-06-11 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002127 | 3990 | 70 | 57 | HB-S04-01 | Harbor | 2025-06-11 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-002128 | 690 | 3 | 230 | BY-S29-02 | Bayou | 2025-06-11 | 12 | Animal | Transformer fuse | Forced | None
OE-25-002129 | 59168 | 43 | 1376 | BY-S06-03 | Bayou | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002130 | 315665 | 311 | 1015 | BY-S10-04 | Bayou | 2025-06-11 | 14 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002131 | 101088 | 72 | 1404 | BY-S11-02 | Bayou | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002132 | 357576 | 188 | 1902 | BY-S18-01 | Bayou | 2025-06-11 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002133 | 750498 | 1169 | 642 | BY-S18-07 | Bayou | 2025-06-11 | 14 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002134 | 43056 | 104 | 414 | BY-S22-03 | Bayou | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002135 | 17568 | 32 | 549 | BY-S25-03 | Bayou | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002136 | 105764 | 193 | 548 | CR-S07-04 | Crossroads | 2025-06-11 | 14 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002137 | 22848 | 102 | 224 | CR-S30-03 | Crossroads | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002138 | 144396 | 108 | 1337 | PR-S01-01 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002139 | 99448 | 62 | 1604 | PR-S01-03 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002140 | 66633 | 133 | 501 | PR-S01-05 | Prairie | 2025-06-11 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002141 | 18600 | 30 | 620 | PR-S03-01 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002142 | 96099 | 103 | 933 | PR-S04-01 | Prairie | 2025-06-11 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002143 | 28126 | 49 | 574 | PR-S08-02 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002144 | 114739 | 179 | 641 | PR-S09-03 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002145 | 12425 | 25 | 497 | PR-S09-03 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002146 | 23544 | 54 | 436 | PR-S10-01 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002147 | 49134 | 38 | 1293 | PR-S10-02 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002148 | 196168 | 791 | 248 | PR-S13-02 | Prairie | 2025-06-11 | 14 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002149 | 14700 | 15 | 980 | PR-S13-05 | Prairie | 2025-06-11 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002150 | 7812 | 18 | 434 | PR-S16-04 | Prairie | 2025-06-11 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002151 | 58650 | 34 | 1725 | PR-S17-02 | Prairie | 2025-06-11 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002152 | 296846 | 206 | 1441 | PR-S18-01 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002153 | 120952 | 52 | 2326 | PR-S18-06 | Prairie | 2025-06-11 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002154 | 120000 | 64 | 1875 | PR-S19-02 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002155 | 352520 | 280 | 1259 | PR-S19-04 | Prairie | 2025-06-11 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002156 | 31752 | 63 | 504 | PR-S20-02 | Prairie | 2025-06-11 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002157 | 426478 | 611 | 698 | BY-S09-01 | Bayou | 2025-06-11 | 15 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002158 | 167979 | 399 | 421 | BY-S24-01 | Bayou | 2025-06-11 | 15 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002159 | 129455 | 85 | 1523 | BY-S30-01 | Bayou | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002160 | 35260 | 86 | 410 | CR-S05-06 | Crossroads | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002161 | 92272 | 158 | 584 | CR-S08-04 | Crossroads | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002162 | 64622 | 79 | 818 | CR-S22-03 | Crossroads | 2025-06-11 | 15 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002163 | 8320 | 208 | 40 | HB-S07-03 | Harbor | 2025-06-11 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-002164 | 57120 | 84 | 680 | PR-S02-01 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002165 | 53613 | 111 | 483 | PR-S04-03 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002166 | 17920 | 70 | 256 | PR-S06-02 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002167 | 33630 | 95 | 354 | PR-S07-03 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002168 | 93530 | 94 | 995 | PR-S08-02 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002169 | 403200 | 96 | 4200 | PR-S09-01 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002170 | 37524 | 118 | 318 | PR-S11-03 | Prairie | 2025-06-11 | 15 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002171 | 42812 | 139 | 308 | PR-S12-03 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002172 | 645344 | 344 | 1876 | PR-S14-02 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002173 | 66755 | 79 | 845 | PR-S14-03 | Prairie | 2025-06-11 | 15 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002174 | 56990 | 139 | 410 | PR-S16-02 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002175 | 462000 | 110 | 4200 | PR-S16-03 | Prairie | 2025-06-11 | 15 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002176 | 37162 | 34 | 1093 | PR-S16-05 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002177 | 6016 | 32 | 188 | PR-S17-01 | Prairie | 2025-06-11 | 15 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002178 | 342908 | 236 | 1453 | PR-S18-02 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002179 | 181940 | 220 | 827 | PR-S18-04 | Prairie | 2025-06-11 | 15 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002180 | 66608 | 46 | 1448 | PR-S19-01 | Prairie | 2025-06-11 | 15 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002181 | 89792 | 368 | 244 | PR-S20-01 | Prairie | 2025-06-11 | 15 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002182 | 144664 | 169 | 856 | PR-S20-03 | Prairie | 2025-06-11 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002183 | 881991 | 1359 | 649 | BY-S04-01 | Bayou | 2025-06-11 | 16 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002184 | 23180 | 61 | 380 | BY-S09-03 | Bayou | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002185 | 133665 | 57 | 2345 | BY-S09-04 | Bayou | 2025-06-11 | 16 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002186 | 81624 | 114 | 716 | BY-S19-01 | Bayou | 2025-06-11 | 16 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002187 | 174135 | 141 | 1235 | BY-S26-01 | Bayou | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002188 | 4590237 | 1671 | 2747 | CR-S03-01 | Crossroads | 2025-06-11 | 16 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002189 | 23736 | 86 | 276 | CR-S12-01 | Crossroads | 2025-06-11 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002190 | 72912 | 196 | 372 | CR-S23-04 | Crossroads | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002191 | 1970697 | 597 | 3301 | CR-S25-04 | Crossroads | 2025-06-11 | 16 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002192 | 4004 | 44 | 91 | CR-S31-03 | Crossroads | 2025-06-11 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-002193 | 6732 | 22 | 306 | PR-S02-01 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002194 | 60352 | 46 | 1312 | PR-S02-02 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002195 | 371349 | 279 | 1331 | PR-S02-03 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002196 | 24108 | 41 | 588 | PR-S03-04 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002197 | 16287 | 61 | 267 | PR-S05-03 | Prairie | 2025-06-11 | 16 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002198 | 108528 | 102 | 1064 | PR-S06-01 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002199 | 50489 | 29 | 1741 | PR-S06-03 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002200 | 124662 | 158 | 789 | PR-S07-01 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002201 | 57824 | 278 | 208 | PR-S08-03 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002202 | 163308 | 186 | 878 | PR-S11-02 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002203 | 48496 | 112 | 433 | PR-S12-02 | Prairie | 2025-06-11 | 16 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002204 | 8483 | 17 | 499 | PR-S12-02 | Prairie | 2025-06-11 | 16 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002205 | 14694 | 31 | 474 | PR-S12-03 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002206 | 103740 | 70 | 1482 | PR-S13-01 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002207 | 159870 | 146 | 1095 | PR-S13-03 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002208 | 121880 | 277 | 440 | PR-S13-05 | Prairie | 2025-06-11 | 16 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002209 | 87780 | 209 | 420 | PR-S13-05 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002210 | 154700 | 119 | 1300 | PR-S16-03 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002211 | 5661 | 17 | 333 | PR-S18-04 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002212 | 15904 | 56 | 284 | PR-S18-05 | Prairie | 2025-06-11 | 16 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002213 | 278306 | 193 | 1442 | PR-S18-06 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002214 | 51686 | 86 | 601 | PR-S19-04 | Prairie | 2025-06-11 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002215 | 41310 | 51 | 810 | PR-S20-04 | Prairie | 2025-06-11 | 16 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002216 | 957220 | 916 | 1045 | BY-S01-02 | Bayou | 2025-06-11 | 17 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002217 | 1188195 | 701 | 1695 | BY-S04-03 | Bayou | 2025-06-11 | 17 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002218 | 69687 | 29 | 2403 | BY-S07-04 | Bayou | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002219 | 941850 | 819 | 1150 | BY-S10-02 | Bayou | 2025-06-11 | 17 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002220 | 8924 | 23 | 388 | BY-S11-01 | Bayou | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002221 | 19089 | 27 | 707 | BY-S21-02 | Bayou | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002222 | 2002 | 13 | 154 | HB-S05-04 | Harbor | 2025-06-11 | 17 | Animal | Transformer fuse | Forced | None
OE-25-002223 | 25622 | 23 | 1114 | PR-S02-02 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002224 | 331817 | 853 | 389 | PR-S02-03 | Prairie | 2025-06-11 | 17 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002225 | 272764 | 703 | 388 | PR-S03-02 | Prairie | 2025-06-11 | 17 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002226 | 435456 | 576 | 756 | PR-S03-04 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002227 | 10416 | 31 | 336 | PR-S03-06 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002228 | 17340 | 68 | 255 | PR-S04-03 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002229 | 10327 | 23 | 449 | PR-S06-02 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002230 | 294294 | 286 | 1029 | PR-S07-01 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002231 | 19840 | 16 | 1240 | PR-S08-03 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002232 | 49011 | 31 | 1581 | PR-S09-03 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002233 | 268800 | 64 | 4200 | PR-S10-03 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002234 | 54630 | 90 | 607 | PR-S11-01 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002235 | 52650 | 18 | 2925 | PR-S11-01 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002236 | 26970 | 87 | 310 | PR-S13-01 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002237 | 29876 | 44 | 679 | PR-S13-03 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002238 | 70176 | 129 | 544 | PR-S14-02 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002239 | 1076160 | 760 | 1416 | PR-S14-04 | Prairie | 2025-06-11 | 17 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002240 | 32832 | 57 | 576 | PR-S15-01 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002241 | 107338 | 82 | 1309 | PR-S15-05 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002242 | 318060 | 465 | 684 | PR-S16-02 | Prairie | 2025-06-11 | 17 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002243 | 36771 | 103 | 357 | PR-S18-01 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002244 | 81600 | 85 | 960 | PR-S18-05 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002245 | 2470 | 13 | 190 | PR-S18-06 | Prairie | 2025-06-11 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-002246 | 215355 | 105 | 2051 | PR-S19-03 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002247 | 15840 | 88 | 180 | PR-S20-02 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002248 | 25864 | 61 | 424 | PR-S20-02 | Prairie | 2025-06-11 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002249 | 70740 | 45 | 1572 | PR-S20-03 | Prairie | 2025-06-11 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002250 | 738136 | 686 | 1076 | BY-S08-02 | Bayou | 2025-06-11 | 18 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002251 | 4243954 | 3146 | 1349 | BY-S15-02 | Bayou | 2025-06-11 | 18 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002252 | 84688 | 67 | 1264 | BY-S16-06 | Bayou | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002253 | 26037 | 99 | 263 | BY-S17-03 | Bayou | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002254 | 39380 | 55 | 716 | BY-S18-02 | Bayou | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002255 | 8346 | 13 | 642 | BY-S22-04 | Bayou | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002256 | 81512 | 92 | 886 | BY-S26-03 | Bayou | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002257 | 96012 | 381 | 252 | CR-S04-04 | Crossroads | 2025-06-11 | 18 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002258 | 30480 | 24 | 1270 | PR-S01-03 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002259 | 51216 | 97 | 528 | PR-S01-06 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002260 | 78470 | 133 | 590 | PR-S03-02 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002261 | 14722 | 17 | 866 | PR-S03-03 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002262 | 1682184 | 1736 | 969 | PR-S03-05 | Prairie | 2025-06-11 | 18 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002263 | 44697 | 141 | 317 | PR-S03-05 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002264 | 206011 | 169 | 1219 | PR-S03-06 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002265 | 161568 | 408 | 396 | PR-S04-03 | Prairie | 2025-06-11 | 18 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002266 | 91676 | 82 | 1118 | PR-S05-01 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002267 | 300564 | 828 | 363 | PR-S05-03 | Prairie | 2025-06-11 | 18 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002268 | 1308925 | 1025 | 1277 | PR-S07-04 | Prairie | 2025-06-11 | 18 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002269 | 151489 | 271 | 559 | PR-S07-04 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002270 | 228336 | 201 | 1136 | PR-S07-05 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002271 | 618510 | 530 | 1167 | PR-S08-02 | Prairie | 2025-06-11 | 18 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002272 | 25048 | 31 | 808 | PR-S09-01 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002273 | 408272 | 272 | 1501 | PR-S09-04 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002274 | 92250 | 90 | 1025 | PR-S10-02 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002275 | 24150 | 42 | 575 | PR-S10-03 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002276 | 24976 | 56 | 446 | PR-S12-03 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002277 | 329072 | 262 | 1256 | PR-S13-03 | Prairie | 2025-06-11 | 18 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002278 | 108040 | 74 | 1460 | PR-S13-04 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002279 | 475783 | 167 | 2849 | PR-S14-01 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002280 | 44608 | 136 | 328 | PR-S15-02 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002281 | 14652 | 74 | 198 | PR-S15-03 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002282 | 53815 | 47 | 1145 | PR-S16-05 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002283 | 17442 | 9 | 1938 | PR-S18-02 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002284 | 150954 | 181 | 834 | PR-S18-04 | Prairie | 2025-06-11 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002285 | 35640 | 90 | 396 | PR-S19-03 | Prairie | 2025-06-11 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002286 | 101442 | 159 | 638 | BY-S06-01 | Bayou | 2025-06-11 | 19 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002287 | 471420 | 873 | 540 | BY-S08-01 | Bayou | 2025-06-11 | 19 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002288 | 20601 | 27 | 763 | BY-S09-05 | Bayou | 2025-06-11 | 19 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002289 | 4261803 | 1407 | 3029 | BY-S16-04 | Bayou | 2025-06-11 | 19 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002290 | 65485 | 35 | 1871 | BY-S23-01 | Bayou | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002291 | 286848 | 576 | 498 | BY-S25-01 | Bayou | 2025-06-11 | 19 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002292 | 340490 | 790 | 431 | BY-S25-04 | Bayou | 2025-06-11 | 19 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002293 | 248970 | 579 | 430 | BY-S26-05 | Bayou | 2025-06-11 | 19 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002294 | 522477 | 333 | 1569 | CR-S05-04 | Crossroads | 2025-06-11 | 19 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002295 | 13446 | 81 | 166 | CR-S09-05 | Crossroads | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002296 | 179056 | 248 | 722 | CR-S27-03 | Crossroads | 2025-06-11 | 19 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002297 | 1052924 | 922 | 1142 | CR-S28-04 | Crossroads | 2025-06-11 | 19 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002298 | 23200 | 40 | 580 | CR-S29-01 | Crossroads | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002299 | 29744 | 44 | 676 | CR-S32-03 | Crossroads | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002300 | 847 | 11 | 77 | HB-S19-04 | Harbor | 2025-06-11 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002301 | 189970 | 242 | 785 | PR-S01-02 | Prairie | 2025-06-11 | 19 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002302 | 19040 | 17 | 1120 | PR-S03-02 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002303 | 12322 | 61 | 202 | PR-S03-03 | Prairie | 2025-06-11 | 19 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002304 | 18648 | 28 | 666 | PR-S04-02 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002305 | 26112 | 34 | 768 | PR-S07-02 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002306 | 25704 | 27 | 952 | PR-S09-04 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002307 | 70686 | 54 | 1309 | PR-S09-04 | Prairie | 2025-06-11 | 19 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002308 | 641190 | 870 | 737 | PR-S10-03 | Prairie | 2025-06-11 | 19 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002309 | 87857 | 163 | 539 | PR-S11-02 | Prairie | 2025-06-11 | 19 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002310 | 100958 | 143 | 706 | PR-S14-03 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002311 | 16807 | 49 | 343 | PR-S15-02 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002312 | 168000 | 40 | 4200 | PR-S15-03 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002313 | 7310 | 43 | 170 | PR-S15-04 | Prairie | 2025-06-11 | 19 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002314 | 100050 | 145 | 690 | PR-S15-06 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002315 | 84370 | 55 | 1534 | PR-S19-01 | Prairie | 2025-06-11 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002316 | 2433438 | 1869 | 1302 | BY-S01-01 | Bayou | 2025-06-11 | 20 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002317 | 572700 | 830 | 690 | BY-S07-03 | Bayou | 2025-06-11 | 20 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002318 | 29064 | 56 | 519 | BY-S07-05 | Bayou | 2025-06-11 | 20 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002319 | 4545086 | 1582 | 2873 | BY-S07-06 | Bayou | 2025-06-11 | 20 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002320 | 19024 | 82 | 232 | BY-S12-03 | Bayou | 2025-06-11 | 20 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002321 | 728604 | 1332 | 547 | BY-S21-05 | Bayou | 2025-06-11 | 20 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002322 | 400980 | 615 | 652 | BY-S29-03 | Bayou | 2025-06-11 | 20 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002323 | 56640 | 40 | 1416 | CR-S18-04 | Crossroads | 2025-06-11 | 20 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002324 | 50736 | 48 | 1057 | PR-S01-03 | Prairie | 2025-06-11 | 20 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002325 | 67830 | 17 | 3990 | PR-S01-05 | Prairie | 2025-06-11 | 20 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002326 | 72624 | 89 | 816 | PR-S05-01 | Prairie | 2025-06-11 | 20 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002327 | 29348 | 44 | 667 | PR-S08-03 | Prairie | 2025-06-11 | 20 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002328 | 79348 | 166 | 478 | PR-S11-03 | Prairie | 2025-06-11 | 20 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002329 | 44220 | 66 | 670 | PR-S12-02 | Prairie | 2025-06-11 | 20 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002330 | 78309 | 99 | 791 | PR-S13-04 | Prairie | 2025-06-11 | 20 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002331 | 146280 | 159 | 920 | PR-S14-04 | Prairie | 2025-06-11 | 20 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002332 | 413127 | 429 | 963 | PR-S15-04 | Prairie | 2025-06-11 | 20 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002333 | 422136 | 572 | 738 | PR-S18-03 | Prairie | 2025-06-11 | 20 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002334 | 909900 | 1348 | 675 | PR-S18-06 | Prairie | 2025-06-11 | 20 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002335 | 906440 | 620 | 1462 | BY-S02-02 | Bayou | 2025-06-11 | 21 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002336 | 119534 | 118 | 1013 | BY-S07-01 | Bayou | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002337 | 1629144 | 792 | 2057 | BY-S12-01 | Bayou | 2025-06-11 | 21 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002338 | 1129215 | 907 | 1245 | BY-S27-03 | Bayou | 2025-06-11 | 21 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002339 | 1489621 | 883 | 1687 | BY-S27-05 | Bayou | 2025-06-11 | 21 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002340 | 558740 | 307 | 1820 | BY-S28-01 | Bayou | 2025-06-11 | 21 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002341 | 40770 | 54 | 755 | PR-S02-02 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002342 | 20305 | 31 | 655 | PR-S03-03 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002343 | 15808 | 52 | 304 | PR-S05-03 | Prairie | 2025-06-11 | 21 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002344 | 27090 | 30 | 903 | PR-S07-02 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002345 | 124476 | 66 | 1886 | PR-S07-03 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002346 | 64064 | 154 | 416 | PR-S07-03 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002347 | 39104 | 52 | 752 | PR-S07-05 | Prairie | 2025-06-11 | 21 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002348 | 39474 | 43 | 918 | PR-S07-06 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002349 | 120543 | 69 | 1747 | PR-S07-06 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002350 | 545229 | 2089 | 261 | PR-S09-01 | Prairie | 2025-06-11 | 21 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002351 | 403236 | 974 | 414 | PR-S09-02 | Prairie | 2025-06-11 | 21 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002352 | 2046138 | 1718 | 1191 | PR-S11-02 | Prairie | 2025-06-11 | 21 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002353 | 65552 | 68 | 964 | PR-S12-01 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002354 | 24940 | 43 | 580 | PR-S13-02 | Prairie | 2025-06-11 | 21 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002355 | 94501 | 121 | 781 | PR-S14-04 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002356 | 13735 | 41 | 335 | PR-S16-05 | Prairie | 2025-06-11 | 21 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002357 | 38456 | 88 | 437 | PR-S17-01 | Prairie | 2025-06-11 | 21 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002358 | 27200 | 25 | 1088 | PR-S20-04 | Prairie | 2025-06-11 | 21 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002359 | 838266 | 977 | 858 | BY-S05-01 | Bayou | 2025-06-11 | 22 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002360 | 2339450 | 1775 | 1318 | BY-S05-02 | Bayou | 2025-06-11 | 22 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002361 | 57304 | 38 | 1508 | BY-S09-02 | Bayou | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002362 | 130011 | 861 | 151 | BY-S14-03 | Bayou | 2025-06-11 | 22 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002363 | 9605844 | 3132 | 3067 | BY-S19-02 | Bayou | 2025-06-11 | 22 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002364 | 55368 | 72 | 769 | BY-S20-03 | Bayou | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002365 | 11650 | 25 | 466 | BY-S22-01 | Bayou | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002366 | 483108 | 634 | 762 | CR-S02-02 | Crossroads | 2025-06-11 | 22 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002367 | 92904 | 84 | 1106 | CR-S13-04 | Crossroads | 2025-06-11 | 22 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002368 | 429174 | 339 | 1266 | CR-S17-02 | Crossroads | 2025-06-11 | 22 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002369 | 7140 | 105 | 68 | HB-S11-01 | Harbor | 2025-06-11 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-002370 | 20502 | 17 | 1206 | PR-S01-01 | Prairie | 2025-06-11 | 22 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002371 | 63792 | 48 | 1329 | PR-S01-02 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002372 | 346040 | 328 | 1055 | PR-S01-02 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002373 | 106600 | 200 | 533 | PR-S01-05 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002374 | 47142 | 27 | 1746 | PR-S02-03 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002375 | 109908 | 172 | 639 | PR-S05-01 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002376 | 233802 | 93 | 2514 | PR-S05-02 | Prairie | 2025-06-11 | 22 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002377 | 23940 | 42 | 570 | PR-S06-03 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002378 | 176080 | 284 | 620 | PR-S08-01 | Prairie | 2025-06-11 | 22 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002379 | 55977 | 47 | 1191 | PR-S09-02 | Prairie | 2025-06-11 | 22 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002380 | 31056 | 48 | 647 | PR-S13-02 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002381 | 164736 | 72 | 2288 | PR-S13-06 | Prairie | 2025-06-11 | 22 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002382 | 222370 | 370 | 601 | PR-S14-02 | Prairie | 2025-06-11 | 22 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002383 | 22533 | 21 | 1073 | PR-S15-03 | Prairie | 2025-06-11 | 22 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002384 | 45738 | 54 | 847 | PR-S18-03 | Prairie | 2025-06-11 | 22 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002385 | 32340 | 55 | 588 | PR-S19-05 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002386 | 133826 | 79 | 1694 | PR-S20-01 | Prairie | 2025-06-11 | 22 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002387 | 1445 | 5 | 289 | BY-S11-01 | Bayou | 2025-06-11 | 23 | Vegetation | Transformer fuse | Forced | None
OE-25-002388 | 183204 | 63 | 2908 | PR-S08-01 | Prairie | 2025-06-12 | 0 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002389 | 152515 | 59 | 2585 | PR-S10-01 | Prairie | 2025-06-12 | 0 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002390 | 378056 | 314 | 1204 | PR-S19-05 | Prairie | 2025-06-12 | 0 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002391 | 82205 | 41 | 2005 | BY-S10-01 | Bayou | 2025-06-12 | 1 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002392 | 678270 | 983 | 690 | BY-S22-02 | Bayou | 2025-06-12 | 1 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002393 | 17160 | 33 | 520 | PR-S01-06 | Prairie | 2025-06-12 | 1 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002394 | 104538 | 131 | 798 | PR-S07-06 | Prairie | 2025-06-12 | 1 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002395 | 37136 | 88 | 422 | PR-S14-01 | Prairie | 2025-06-12 | 1 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002396 | 13560 | 30 | 452 | PR-S19-05 | Prairie | 2025-06-12 | 1 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002397 | 68586 | 138 | 497 | PR-S20-03 | Prairie | 2025-06-12 | 1 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002398 | 1656471 | 1713 | 967 | BY-S02-01 | Bayou | 2025-06-12 | 2 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002399 | 9752 | 53 | 184 | BY-S10-05 | Bayou | 2025-06-12 | 2 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002400 | 43475 | 37 | 1175 | PR-S04-01 | Prairie | 2025-06-12 | 2 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002401 | 25567 | 37 | 691 | PR-S13-06 | Prairie | 2025-06-12 | 2 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002402 | 414312 | 566 | 732 | PR-S19-01 | Prairie | 2025-06-12 | 2 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002403 | 432936 | 252 | 1718 | PR-S01-04 | Prairie | 2025-06-12 | 3 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002404 | 46065 | 83 | 555 | PR-S13-01 | Prairie | 2025-06-12 | 3 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002405 | 213136 | 176 | 1211 | PR-S15-01 | Prairie | 2025-06-12 | 3 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002406 | 2059145 | 1291 | 1595 | PR-S19-04 | Prairie | 2025-06-12 | 3 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002407 | 160864 | 176 | 914 | PR-S20-04 | Prairie | 2025-06-12 | 3 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002408 | 52269 | 131 | 399 | PR-S10-01 | Prairie | 2025-06-12 | 4 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002409 | 82416 | 51 | 1616 | PR-S13-06 | Prairie | 2025-06-12 | 4 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002410 | 18625 | 25 | 745 | PR-S15-04 | Prairie | 2025-06-12 | 4 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002411 | 1336702 | 1294 | 1033 | PR-S15-06 | Prairie | 2025-06-12 | 4 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002412 | 13276200 | 3161 | 4200 | CR-S04-06 | Crossroads | 2025-06-12 | 5 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002413 | 41757 | 93 | 449 | CR-S30-01 | Crossroads | 2025-06-12 | 5 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002414 | 84216 | 232 | 363 | PR-S03-05 | Prairie | 2025-06-12 | 5 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002415 | 6707 | 19 | 353 | PR-S07-01 | Prairie | 2025-06-12 | 5 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002416 | 19266 | 6 | 3211 | PR-S12-01 | Prairie | 2025-06-12 | 5 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002417 | 878244 | 652 | 1347 | PR-S15-01 | Prairie | 2025-06-12 | 5 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002418 | 25500 | 85 | 300 | PR-S15-05 | Prairie | 2025-06-12 | 5 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002419 | 42624 | 36 | 1184 | PR-S15-05 | Prairie | 2025-06-12 | 5 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002420 | 57031 | 41 | 1391 | PR-S15-06 | Prairie | 2025-06-12 | 5 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002421 | 185370 | 370 | 501 | BY-S15-04 | Bayou | 2025-06-12 | 6 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002422 | 856 | 8 | 107 | BY-S26-06 | Bayou | 2025-06-12 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002423 | 185648 | 656 | 283 | BY-S29-05 | Bayou | 2025-06-12 | 6 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002424 | 83895 | 235 | 357 | CR-S06-01 | Crossroads | 2025-06-12 | 6 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002425 | 792 | 12 | 66 | HB-S05-06 | Harbor | 2025-06-12 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002426 | 80370 | 282 | 285 | PR-S19-02 | Prairie | 2025-06-12 | 6 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002427 | 500514 | 714 | 701 | BY-S23-05 | Bayou | 2025-06-12 | 7 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002428 | 10920 | 105 | 104 | BY-S25-04 | Bayou | 2025-06-12 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002429 | 71415 | 207 | 345 | BY-S30-02 | Bayou | 2025-06-12 | 7 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002430 | 21870 | 30 | 729 | PR-S16-01 | Prairie | 2025-06-12 | 7 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002431 | 20657 | 13 | 1589 | PR-S16-02 | Prairie | 2025-06-12 | 7 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002432 | 318750 | 510 | 625 | BY-S15-05 | Bayou | 2025-06-12 | 8 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002433 | 535558 | 662 | 809 | PR-S01-06 | Prairie | 2025-06-12 | 8 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002434 | 15392 | 32 | 481 | PR-S09-02 | Prairie | 2025-06-12 | 8 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002435 | 2005575 | 975 | 2057 | PR-S10-02 | Prairie | 2025-06-12 | 8 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002436 | 38394 | 81 | 474 | PR-S16-01 | Prairie | 2025-06-12 | 8 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002437 | 666978 | 1006 | 663 | BY-S04-02 | Bayou | 2025-06-12 | 9 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002438 | 3288120 | 1551 | 2120 | PR-S06-01 | Prairie | 2025-06-12 | 9 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002439 | 29158 | 122 | 239 | BY-S04-01 | Bayou | 2025-06-12 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002440 | 1107387 | 639 | 1733 | BY-S21-03 | Bayou | 2025-06-12 | 10 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002441 | 181830 | 209 | 870 | PR-S06-03 | Prairie | 2025-06-12 | 10 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002442 | 19470 | 55 | 354 | PR-S19-02 | Prairie | 2025-06-12 | 10 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002443 | 1410 | 47 | 30 | CR-S20-05 | Crossroads | 2025-06-12 | 11 | Animal | Lateral fuse | Forced | None
OE-25-002444 | 18240 | 960 | 19 | PR-S02-01 | Prairie | 2025-06-12 | 11 | Unknown | Substation breaker | Outside cause | None
OE-25-002445 | 273000 | 65 | 4200 | PR-S03-01 | Prairie | 2025-06-12 | 11 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002446 | 608529 | 579 | 1051 | PR-S07-02 | Prairie | 2025-06-12 | 11 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002447 | 512631 | 927 | 553 | PR-S14-01 | Prairie | 2025-06-12 | 11 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002448 | 21608 | 292 | 74 | CR-S14-05 | Crossroads | 2025-06-12 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002449 | 185776 | 136 | 1366 | PR-S02-01 | Prairie | 2025-06-12 | 12 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002450 | 75992 | 161 | 472 | PR-S02-03 | Prairie | 2025-06-12 | 12 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002451 | 71558 | 74 | 967 | PR-S04-02 | Prairie | 2025-06-12 | 12 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002452 | 40830 | 30 | 1361 | PR-S05-02 | Prairie | 2025-06-12 | 12 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002453 | 65379 | 31 | 2109 | PR-S12-01 | Prairie | 2025-06-12 | 12 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002454 | 80997 | 147 | 551 | PR-S13-04 | Prairie | 2025-06-12 | 12 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002455 | 14724 | 36 | 409 | PR-S18-05 | Prairie | 2025-06-12 | 12 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002456 | 936 | 9 | 104 | BY-S30-01 | Bayou | 2025-06-12 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002457 | 9920 | 124 | 80 | CR-S13-05 | Crossroads | 2025-06-12 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-25-002458 | 10494 | 66 | 159 | HB-S10-01 | Harbor | 2025-06-12 | 13 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002459 | 3525 | 47 | 75 | PR-S09-01 | Prairie | 2025-06-12 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-25-002460 | 108675 | 45 | 2415 | PR-S16-01 | Prairie | 2025-06-12 | 13 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002461 | 22914 | 19 | 1206 | PR-S17-02 | Prairie | 2025-06-12 | 13 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002462 | 8787 | 101 | 87 | BY-S14-02 | Bayou | 2025-06-12 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002463 | 18084 | 44 | 411 | BY-S26-06 | Bayou | 2025-06-12 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002464 | 72405 | 45 | 1609 | CR-S08-06 | Crossroads | 2025-06-12 | 14 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002465 | 600 | 4 | 150 | CR-S30-02 | Crossroads | 2025-06-12 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002466 | 834 | 6 | 139 | PR-S13-06 | Prairie | 2025-06-12 | 14 | Animal | Transformer fuse | Forced | None
OE-25-002467 | 23471 | 49 | 479 | PR-S17-01 | Prairie | 2025-06-12 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002468 | 812592 | 1026 | 792 | PR-S18-02 | Prairie | 2025-06-12 | 14 | Weather - wind | Substation breaker | Major event | June 2025 wind event
OE-25-002469 | 160875 | 375 | 429 | BY-S12-02 | Bayou | 2025-06-12 | 15 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002470 | 2712096 | 876 | 3096 | PR-S06-02 | Prairie | 2025-06-12 | 15 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002471 | 11826 | 18 | 657 | PR-S11-03 | Prairie | 2025-06-12 | 15 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002472 | 3042 | 13 | 234 | PR-S13-04 | Prairie | 2025-06-12 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002473 | 497651 | 253 | 1967 | PR-S18-03 | Prairie | 2025-06-12 | 15 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002474 | 22484 | 77 | 292 | BY-S03-03 | Bayou | 2025-06-12 | 16 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002475 | 111555 | 67 | 1665 | BY-S07-02 | Bayou | 2025-06-12 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002476 | 20474 | 29 | 706 | PR-S03-01 | Prairie | 2025-06-12 | 17 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002477 | 278775 | 413 | 675 | PR-S16-04 | Prairie | 2025-06-12 | 17 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002478 | 153090 | 315 | 486 | PR-S01-01 | Prairie | 2025-06-12 | 18 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002479 | 181548 | 369 | 492 | PR-S01-04 | Prairie | 2025-06-12 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002480 | 16722 | 18 | 929 | PR-S11-01 | Prairie | 2025-06-12 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002481 | 134355 | 65 | 2067 | PR-S16-04 | Prairie | 2025-06-12 | 18 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002482 | 2248 | 8 | 281 | BY-S10-04 | Bayou | 2025-06-12 | 19 | Animal | Transformer fuse | Forced | None
OE-25-002483 | 586791 | 211 | 2781 | CR-S14-03 | Crossroads | 2025-06-12 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002484 | 124135 | 185 | 671 | PR-S03-04 | Prairie | 2025-06-12 | 19 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002485 | 7175 | 25 | 287 | PR-S16-03 | Prairie | 2025-06-12 | 19 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002486 | 56457 | 123 | 459 | CR-S12-02 | Crossroads | 2025-06-12 | 20 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002487 | 47816 | 86 | 556 | PR-S07-04 | Prairie | 2025-06-12 | 20 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002488 | 35175 | 75 | 469 | PR-S08-01 | Prairie | 2025-06-12 | 20 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002489 | 123695 | 865 | 143 | PR-S16-05 | Prairie | 2025-06-12 | 20 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002490 | 4403 | 37 | 119 | HB-S12-01 | Harbor | 2025-06-12 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002491 | 1560 | 8 | 195 | BY-S25-02 | Bayou | 2025-06-12 | 23 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002492 | 42340 | 73 | 580 | CR-S14-02 | Crossroads | 2025-06-13 | 0 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002493 | 39087 | 101 | 387 | PR-S18-01 | Prairie | 2025-06-13 | 0 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002494 | 51475 | 71 | 725 | PR-S20-01 | Prairie | 2025-06-13 | 2 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002495 | 37791 | 57 | 663 | CR-S18-05 | Crossroads | 2025-06-13 | 3 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002496 | 125280 | 144 | 870 | PR-S06-01 | Prairie | 2025-06-13 | 4 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002497 | 20992 | 82 | 256 | PR-S07-05 | Prairie | 2025-06-13 | 4 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002498 | 1324790 | 1370 | 967 | BY-S23-02 | Bayou | 2025-06-13 | 5 | Vegetation | Feeder recloser | Major event | June 2025 wind event
OE-25-002499 | 89880 | 105 | 856 | PR-S03-06 | Prairie | 2025-06-13 | 6 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002500 | 6111 | 63 | 97 | CR-S23-05 | Crossroads | 2025-06-13 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002501 | 468 | 6 | 78 | HB-S13-02 | Harbor | 2025-06-13 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-25-002502 | 624 | 13 | 48 | CR-S17-02 | Crossroads | 2025-06-13 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002503 | 734424 | 1724 | 426 | PR-S14-03 | Prairie | 2025-06-13 | 10 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002504 | 49876 | 74 | 674 | CR-S13-02 | Crossroads | 2025-06-13 | 11 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002505 | 2480 | 40 | 62 | BY-S03-01 | Bayou | 2025-06-13 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-002506 | 3774 | 34 | 111 | BY-S18-04 | Bayou | 2025-06-13 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002507 | 48600 | 100 | 486 | CR-S06-03 | Crossroads | 2025-06-13 | 12 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002508 | 2710 | 10 | 271 | PR-S08-03 | Prairie | 2025-06-13 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002509 | 13530 | 330 | 41 | PR-S11-01 | Prairie | 2025-06-13 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-002510 | 24986 | 403 | 62 | PR-S17-02 | Prairie | 2025-06-13 | 12 | Weather - lightning | Feeder recloser | Forced | None
OE-25-002511 | 503100 | 258 | 1950 | PR-S17-02 | Prairie | 2025-06-13 | 12 | Weather - wind | Feeder recloser | Major event | June 2025 wind event
OE-25-002512 | 1820 | 14 | 130 | BY-S29-05 | Bayou | 2025-06-13 | 13 | Animal | Transformer fuse | Forced | None
OE-25-002513 | 645535 | 1067 | 605 | PR-S19-03 | Prairie | 2025-06-13 | 13 | Vegetation | Substation breaker | Major event | June 2025 wind event
OE-25-002514 | 18204 | 37 | 492 | BY-S15-06 | Bayou | 2025-06-13 | 14 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002515 | 1050 | 7 | 150 | PR-S19-04 | Prairie | 2025-06-13 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002516 | 5184 | 48 | 108 | BY-S02-01 | Bayou | 2025-06-13 | 16 | Animal | Lateral fuse | Forced | None
OE-25-002517 | 1001 | 13 | 77 | HB-S15-02 | Harbor | 2025-06-13 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002518 | 8172 | 18 | 454 | PR-S04-02 | Prairie | 2025-06-13 | 16 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002519 | 162 | 3 | 54 | PR-S13-05 | Prairie | 2025-06-13 | 17 | Animal | Transformer fuse | Forced | None
OE-25-002520 | 11521 | 41 | 281 | PR-S15-02 | Prairie | 2025-06-13 | 17 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002521 | 58290 | 670 | 87 | CR-S13-01 | Crossroads | 2025-06-13 | 18 | Vehicle or public | Feeder recloser | Forced | None
OE-25-002522 | 2030 | 29 | 70 | CR-S31-03 | Crossroads | 2025-06-13 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002523 | 34486 | 86 | 401 | PR-S01-04 | Prairie | 2025-06-13 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002524 | 75231 | 39 | 1929 | PR-S04-01 | Prairie | 2025-06-13 | 18 | Weather - wind | Lateral fuse | Major event | June 2025 wind event
OE-25-002525 | 3224 | 13 | 248 | BY-S12-01 | Bayou | 2025-06-13 | 19 | Animal | Transformer fuse | Forced | None
OE-25-002526 | 2256 | 12 | 188 | CR-S27-04 | Crossroads | 2025-06-13 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002527 | 200 | 2 | 100 | CR-S25-01 | Crossroads | 2025-06-13 | 20 | Animal | Transformer fuse | Forced | None
OE-25-002528 | 16566 | 33 | 502 | PR-S05-02 | Prairie | 2025-06-13 | 20 | Vegetation | Lateral fuse | Major event | June 2025 wind event
OE-25-002529 | 803 | 11 | 73 | BY-S14-02 | Bayou | 2025-06-13 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-002530 | 536 | 4 | 134 | HB-S18-03 | Harbor | 2025-06-14 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-25-002531 | 126750 | 845 | 150 | PR-S11-03 | Prairie | 2025-06-14 | 8 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002532 | 2900 | 100 | 29 | CR-S28-01 | Crossroads | 2025-06-14 | 9 | Animal | Lateral fuse | Forced | None
OE-25-002533 | 18960 | 316 | 60 | PR-S07-02 | Prairie | 2025-06-14 | 9 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002534 | 168 | 2 | 84 | CR-S01-04 | Crossroads | 2025-06-14 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002535 | 1435 | 7 | 205 | HB-S04-01 | Harbor | 2025-06-14 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-002536 | 330 | 1 | 330 | CR-S16-02 | Crossroads | 2025-06-14 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-002537 | 1360 | 8 | 170 | CR-S13-03 | Crossroads | 2025-06-14 | 13 | Animal | Transformer fuse | Forced | None
OE-25-002538 | 220 | 1 | 220 | PR-S09-03 | Prairie | 2025-06-14 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-25-002539 | 22752 | 288 | 79 | BY-S01-02 | Bayou | 2025-06-14 | 15 | Animal | Lateral fuse | Forced | None
OE-25-002540 | 96960 | 320 | 303 | PR-S05-03 | Prairie | 2025-06-14 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002541 | 936 | 12 | 78 | CR-S31-03 | Crossroads | 2025-06-14 | 19 | Animal | Transformer fuse | Forced | None
OE-25-002542 | 3100 | 31 | 100 | CR-S30-04 | Crossroads | 2025-06-15 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-25-002543 | 352 | 4 | 88 | PR-S10-03 | Prairie | 2025-06-15 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002544 | 35046 | 1062 | 33 | CR-S13-02 | Crossroads | 2025-06-15 | 10 | Vegetation | Substation breaker | Forced | None
OE-25-002545 | 12480 | 160 | 78 | CR-S24-01 | Crossroads | 2025-06-15 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002546 | 8120 | 56 | 145 | HB-S07-04 | Harbor | 2025-06-15 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-002547 | 728 | 7 | 104 | HB-S13-02 | Harbor | 2025-06-15 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-002548 | 15295 | 95 | 161 | PR-S07-03 | Prairie | 2025-06-15 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-002549 | 1524 | 12 | 127 | PR-S03-01 | Prairie | 2025-06-15 | 15 | Unknown | Transformer fuse | Forced | None
OE-25-002550 | 1417 | 13 | 109 | BY-S11-03 | Bayou | 2025-06-15 | 17 | Animal | Transformer fuse | Forced | None
OE-25-002551 | 1344 | 12 | 112 | CR-S17-03 | Crossroads | 2025-06-15 | 17 | Animal | Transformer fuse | Forced | None
OE-25-002552 | 516 | 4 | 129 | CR-S31-02 | Crossroads | 2025-06-15 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002553 | 5376 | 28 | 192 | PR-S16-01 | Prairie | 2025-06-15 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-002554 | 2754 | 34 | 81 | PR-S17-01 | Prairie | 2025-06-15 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002555 | 1005 | 15 | 67 | PR-S08-03 | Prairie | 2025-06-15 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002556 | 52358 | 1114 | 47 | BY-S18-07 | Bayou | 2025-06-15 | 20 | Vegetation | Substation breaker | Forced | None
OE-25-002557 | 644 | 7 | 92 | HB-S09-05 | Harbor | 2025-06-15 | 20 | Animal | Transformer fuse | Forced | None
OE-25-002558 | 1368 | 12 | 114 | PR-S13-01 | Prairie | 2025-06-15 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002559 | 2550 | 10 | 255 | HB-S06-03 | Harbor | 2025-06-15 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-002560 | 17750 | 250 | 71 | BY-S08-02 | Bayou | 2025-06-15 | 22 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002561 | 6806 | 166 | 41 | PR-S12-03 | Prairie | 2025-06-16 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002562 | 648 | 9 | 72 | BY-S01-01 | Bayou | 2025-06-16 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002563 | 41375 | 125 | 331 | BY-S26-05 | Bayou | 2025-06-16 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002564 | 1020 | 12 | 85 | CR-S13-01 | Crossroads | 2025-06-16 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002565 | 1045 | 11 | 95 | BY-S16-01 | Bayou | 2025-06-16 | 13 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002566 | 4424 | 28 | 158 | CR-S29-01 | Crossroads | 2025-06-16 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002567 | 928 | 8 | 116 | HB-S17-03 | Harbor | 2025-06-16 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-002568 | 650 | 13 | 50 | CR-S05-03 | Crossroads | 2025-06-16 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002569 | 83 | 1 | 83 | BY-S16-03 | Bayou | 2025-06-16 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-002570 | 603 | 3 | 201 | PR-S14-04 | Prairie | 2025-06-16 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-002571 | 12474 | 54 | 231 | CR-S06-01 | Crossroads | 2025-06-16 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-002572 | 12768 | 112 | 114 | BY-S07-02 | Bayou | 2025-06-16 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-002573 | 2706 | 33 | 82 | BY-S15-05 | Bayou | 2025-06-16 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-002574 | 9604 | 49 | 196 | CR-S02-04 | Crossroads | 2025-06-16 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002575 | 1729 | 13 | 133 | CR-S07-03 | Crossroads | 2025-06-16 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002576 | 16380 | 126 | 130 | CR-S12-01 | Crossroads | 2025-06-16 | 20 | Animal | Lateral fuse | Forced | None
OE-25-002577 | 2574 | 13 | 198 | PR-S19-03 | Prairie | 2025-06-16 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002578 | 464 | 4 | 116 | HB-S12-03 | Harbor | 2025-06-16 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-002579 | 1919 | 19 | 101 | BY-S23-02 | Bayou | 2025-06-16 | 22 | Animal | Lateral fuse | Forced | None
OE-25-002580 | 8880 | 40 | 222 | PR-S13-02 | Prairie | 2025-06-17 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002581 | 328 | 2 | 164 | CR-S30-05 | Crossroads | 2025-06-17 | 7 | Animal | Transformer fuse | Forced | None
OE-25-002582 | 20965 | 599 | 35 | PR-S18-05 | Prairie | 2025-06-17 | 7 | Weather - wind | Feeder recloser | Forced | None
OE-25-002583 | 1510 | 10 | 151 | CR-S17-01 | Crossroads | 2025-06-17 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002584 | 13268 | 124 | 107 | BY-S24-05 | Bayou | 2025-06-17 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002585 | 8137 | 79 | 103 | CR-S10-03 | Crossroads | 2025-06-17 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-002586 | 876 | 6 | 146 | CR-S30-01 | Crossroads | 2025-06-17 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002587 | 19304 | 254 | 76 | CR-S17-01 | Crossroads | 2025-06-17 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002588 | 1410 | 15 | 94 | HB-S20-04 | Harbor | 2025-06-17 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002589 | 4082 | 13 | 314 | BY-S08-02 | Bayou | 2025-06-17 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-002590 | 240 | 5 | 48 | BY-S26-05 | Bayou | 2025-06-17 | 15 | Animal | Transformer fuse | Forced | None
OE-25-002591 | 221320 | 2012 | 110 | HB-S01-05 | Harbor | 2025-06-17 | 15 | Weather - wind | Feeder recloser | Forced | None
OE-25-002592 | 2176 | 17 | 128 | BY-S11-01 | Bayou | 2025-06-17 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-002593 | 42788 | 563 | 76 | CR-S24-01 | Crossroads | 2025-06-17 | 17 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-002594 | 99 | 1 | 99 | HB-S10-02 | Harbor | 2025-06-17 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002595 | 672 | 14 | 48 | BY-S01-02 | Bayou | 2025-06-17 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-002596 | 3212 | 11 | 292 | PR-S07-02 | Prairie | 2025-06-17 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-002597 | 96930 | 1077 | 90 | BY-S19-03 | Bayou | 2025-06-17 | 22 | Animal | Feeder recloser | Forced | None
OE-25-002598 | 649 | 11 | 59 | PR-S13-06 | Prairie | 2025-06-17 | 22 | Weather - wind | Transformer fuse | Forced | None
OE-25-002599 | 161555 | 2045 | 79 | HB-S12-02 | Harbor | 2025-06-18 | 8 | Animal | Feeder recloser | Forced | None
OE-25-002600 | 7722 | 78 | 99 | PR-S08-02 | Prairie | 2025-06-18 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-002601 | 1980 | 12 | 165 | BY-S14-02 | Bayou | 2025-06-18 | 11 | Animal | Transformer fuse | Forced | None
OE-25-002602 | 1638 | 42 | 39 | HB-S19-03 | Harbor | 2025-06-18 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-002603 | 972 | 9 | 108 | CR-S03-03 | Crossroads | 2025-06-18 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002604 | 848 | 8 | 106 | HB-S19-02 | Harbor | 2025-06-18 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002605 | 3404 | 37 | 92 | CR-S32-03 | Crossroads | 2025-06-18 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002606 | 30627 | 369 | 83 | CR-S24-02 | Crossroads | 2025-06-18 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-25-002607 | 1060 | 5 | 212 | PR-S13-04 | Prairie | 2025-06-18 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002608 | 5440 | 64 | 85 | PR-S03-03 | Prairie | 2025-06-18 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-002609 | 32488 | 131 | 248 | BY-S09-03 | Bayou | 2025-06-18 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002610 | 17934 | 122 | 147 | BY-S08-02 | Bayou | 2025-06-18 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002611 | 4753 | 49 | 97 | BY-S13-03 | Bayou | 2025-06-18 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002612 | 2100 | 14 | 150 | PR-S17-02 | Prairie | 2025-06-18 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002613 | 315 | 3 | 105 | BY-S08-03 | Bayou | 2025-06-18 | 23 | Vegetation | Transformer fuse | Forced | None
OE-25-002614 | 222 | 3 | 74 | CR-S26-03 | Crossroads | 2025-06-18 | 23 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002615 | 34680 | 1156 | 30 | CR-S32-05 | Crossroads | 2025-06-19 | 2 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-002616 | 81605 | 859 | 95 | BY-S15-02 | Bayou | 2025-06-19 | 6 | Vegetation | Feeder recloser | Forced | None
OE-25-002617 | 456 | 2 | 228 | PR-S13-03 | Prairie | 2025-06-19 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002618 | 28768 | 58 | 496 | PR-S18-02 | Prairie | 2025-06-19 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002619 | 110428 | 1453 | 76 | CR-S22-02 | Crossroads | 2025-06-19 | 9 | Equipment - overhead | Substation breaker | Forced | None
OE-25-002620 | 31360 | 392 | 80 | PR-S06-02 | Prairie | 2025-06-19 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-002621 | 65072 | 392 | 166 | PR-S08-02 | Prairie | 2025-06-19 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002622 | 43 | 1 | 43 | BY-S25-02 | Bayou | 2025-06-19 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002623 | 16958 | 278 | 61 | BY-S23-04 | Bayou | 2025-06-19 | 15 | Vegetation | IGSD-isolated section | Forced | None
OE-25-002624 | 4590 | 27 | 170 | BY-S09-03 | Bayou | 2025-06-19 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-002625 | 143412 | 1292 | 111 | BY-S16-06 | Bayou | 2025-06-19 | 17 | Weather - lightning | Feeder recloser | Forced | None
OE-25-002626 | 310 | 2 | 155 | HB-S09-03 | Harbor | 2025-06-19 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-002627 | 37320 | 1555 | 24 | PR-S15-03 | Prairie | 2025-06-19 | 17 | Unknown | Substation breaker | Outside cause | None
OE-25-002628 | 23183 | 97 | 239 | PR-S20-04 | Prairie | 2025-06-19 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-002629 | 585 | 5 | 117 | CR-S18-04 | Crossroads | 2025-06-19 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-002630 | 80768 | 1262 | 64 | BY-S04-01 | Bayou | 2025-06-19 | 20 | Vegetation | Substation breaker | Forced | None
OE-25-002631 | 8580 | 78 | 110 | BY-S29-01 | Bayou | 2025-06-19 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002632 | 949 | 13 | 73 | BY-S21-04 | Bayou | 2025-06-19 | 22 | Animal | Transformer fuse | Forced | None
OE-25-002633 | 6407 | 43 | 149 | HB-S01-05 | Harbor | 2025-06-19 | 22 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002634 | 4200 | 42 | 100 | CR-S05-03 | Crossroads | 2025-06-19 | 23 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002635 | 53568 | 992 | 54 | BY-S08-02 | Bayou | 2025-06-20 | 2 | Animal | Substation breaker | Forced | None
OE-25-002636 | 3816 | 24 | 159 | BY-S25-04 | Bayou | 2025-06-20 | 5 | Unknown | Lateral fuse | Forced | None
OE-25-002637 | 3699 | 27 | 137 | CR-S19-04 | Crossroads | 2025-06-20 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002638 | 1512 | 14 | 108 | BY-S03-03 | Bayou | 2025-06-20 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002639 | 825 | 11 | 75 | CR-S04-01 | Crossroads | 2025-06-20 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002640 | 2750 | 55 | 50 | CR-S07-04 | Crossroads | 2025-06-20 | 8 | Animal | Lateral fuse | Forced | None
OE-25-002641 | 15990 | 123 | 130 | CR-S08-01 | Crossroads | 2025-06-20 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002642 | 236 | 1 | 236 | BY-S23-01 | Bayou | 2025-06-20 | 9 | Unknown | Transformer fuse | Forced | None
OE-25-002643 | 3382 | 38 | 89 | BY-S23-03 | Bayou | 2025-06-20 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-002644 | 343 | 7 | 49 | CR-S28-03 | Crossroads | 2025-06-20 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002645 | 46529 | 289 | 161 | CR-S14-06 | Crossroads | 2025-06-20 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002646 | 7552 | 59 | 128 | BY-S21-05 | Bayou | 2025-06-20 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-002647 | 22862 | 994 | 23 | CR-S28-03 | Crossroads | 2025-06-20 | 17 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-002648 | 8190 | 91 | 90 | CR-S22-01 | Crossroads | 2025-06-20 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002649 | 2960 | 10 | 296 | PR-S19-03 | Prairie | 2025-06-20 | 22 | Animal | Transformer fuse | Forced | None
OE-25-002650 | 259 | 1 | 259 | PR-S19-02 | Prairie | 2025-06-21 | 5 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002651 | 3668 | 28 | 131 | BY-S16-04 | Bayou | 2025-06-21 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002652 | 12126 | 47 | 258 | PR-S19-04 | Prairie | 2025-06-21 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-002653 | 11266 | 86 | 131 | HB-S17-03 | Harbor | 2025-06-21 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002654 | 3612 | 86 | 42 | PR-S19-01 | Prairie | 2025-06-21 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002655 | 1400 | 7 | 200 | CR-S13-01 | Crossroads | 2025-06-21 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002656 | 6205 | 85 | 73 | HB-S18-01 | Harbor | 2025-06-21 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002657 | 1859 | 11 | 169 | BY-S18-02 | Bayou | 2025-06-21 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002658 | 17112 | 93 | 184 | HB-S05-01 | Harbor | 2025-06-21 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-002659 | 28611 | 867 | 33 | CR-S04-06 | Crossroads | 2025-06-21 | 21 | Animal | Feeder recloser | Forced | None
OE-25-002660 | 9588 | 282 | 34 | HB-S17-02 | Harbor | 2025-06-22 | 2 | Vegetation | Lateral fuse | Forced | None
OE-25-002661 | 28392 | 156 | 182 | BY-S26-04 | Bayou | 2025-06-22 | 8 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002662 | 1560 | 12 | 130 | CR-S28-03 | Crossroads | 2025-06-22 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002663 | 4503 | 57 | 79 | BY-S13-05 | Bayou | 2025-06-22 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002664 | 70760 | 1220 | 58 | PR-S04-01 | Prairie | 2025-06-22 | 10 | Equipment - underground | Substation breaker | Forced | None
OE-25-002665 | 83 | 1 | 83 | BY-S23-03 | Bayou | 2025-06-22 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-002666 | 22776 | 219 | 104 | HB-S07-02 | Harbor | 2025-06-22 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002667 | 959 | 7 | 137 | BY-S09-05 | Bayou | 2025-06-23 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002668 | 6500 | 65 | 100 | CR-S03-01 | Crossroads | 2025-06-23 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-002669 | 1561 | 7 | 223 | HB-S18-02 | Harbor | 2025-06-23 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002670 | 1826 | 11 | 166 | PR-S01-01 | Prairie | 2025-06-23 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002671 | 170 | 1 | 170 | CR-S26-03 | Crossroads | 2025-06-23 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-002672 | 954 | 6 | 159 | PR-S01-04 | Prairie | 2025-06-23 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002673 | 979 | 11 | 89 | PR-S17-01 | Prairie | 2025-06-23 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002674 | 1422 | 9 | 158 | HB-S02-01 | Harbor | 2025-06-23 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002675 | 2044 | 14 | 146 | BY-S08-02 | Bayou | 2025-06-23 | 16 | Animal | Transformer fuse | Forced | None
OE-25-002676 | 3472 | 14 | 248 | HB-S06-02 | Harbor | 2025-06-23 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002677 | 17113 | 109 | 157 | CR-S19-03 | Crossroads | 2025-06-23 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-002678 | 580 | 10 | 58 | CR-S26-06 | Crossroads | 2025-06-23 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002679 | 2340 | 13 | 180 | PR-S15-03 | Prairie | 2025-06-23 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-002680 | 1392 | 12 | 116 | BY-S23-03 | Bayou | 2025-06-23 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-002681 | 1435 | 7 | 205 | BY-S02-01 | Bayou | 2025-06-23 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002682 | 294 | 1 | 294 | CR-S27-03 | Crossroads | 2025-06-24 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002683 | 11556 | 108 | 107 | BY-S01-01 | Bayou | 2025-06-24 | 4 | Vegetation | Lateral fuse | Forced | None
OE-25-002684 | 10776 | 24 | 449 | BY-S20-01 | Bayou | 2025-06-24 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-002685 | 16192 | 64 | 253 | PR-S11-03 | Prairie | 2025-06-24 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-002686 | 6004 | 76 | 79 | BY-S17-01 | Bayou | 2025-06-24 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002687 | 16356 | 87 | 188 | CR-S18-01 | Crossroads | 2025-06-24 | 9 | Animal | Lateral fuse | Forced | None
OE-25-002688 | 615 | 5 | 123 | BY-S12-03 | Bayou | 2025-06-24 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-25-002689 | 16302 | 209 | 78 | BY-S30-03 | Bayou | 2025-06-24 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-002690 | 1870 | 11 | 170 | HB-S04-02 | Harbor | 2025-06-24 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-002691 | 128 | 2 | 64 | HB-S16-05 | Harbor | 2025-06-24 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-002692 | 99960 | 245 | 408 | PR-S17-02 | Prairie | 2025-06-24 | 11 | Weather - lightning | Feeder recloser | Forced | None
OE-25-002693 | 4085 | 19 | 215 | BY-S15-06 | Bayou | 2025-06-24 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002694 | 83 | 1 | 83 | BY-S23-01 | Bayou | 2025-06-24 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002695 | 22916 | 68 | 337 | PR-S19-01 | Prairie | 2025-06-24 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002696 | 432 | 4 | 108 | BY-S24-05 | Bayou | 2025-06-24 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-002697 | 3705 | 39 | 95 | BY-S06-02 | Bayou | 2025-06-24 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-002698 | 34560 | 90 | 384 | BY-S24-01 | Bayou | 2025-06-24 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-002699 | 3672 | 68 | 54 | HB-S03-02 | Harbor | 2025-06-24 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002700 | 16188 | 76 | 213 | PR-S04-01 | Prairie | 2025-06-24 | 16 | Animal | Lateral fuse | Forced | None
OE-25-002701 | 460 | 5 | 92 | BY-S21-02 | Bayou | 2025-06-24 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002702 | 6900 | 75 | 92 | CR-S17-01 | Crossroads | 2025-06-24 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002703 | 253935 | 1215 | 209 | CR-S26-02 | Crossroads | 2025-06-24 | 18 | Weather - lightning | Feeder recloser | Forced | None
OE-25-002704 | 14559 | 69 | 211 | BY-S16-01 | Bayou | 2025-06-24 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002705 | 4902 | 43 | 114 | BY-S13-02 | Bayou | 2025-06-24 | 23 | Vegetation | Lateral fuse | Forced | None
OE-25-002706 | 489 | 3 | 163 | CR-S17-01 | Crossroads | 2025-06-25 | 5 | Weather - wind | Transformer fuse | Forced | None
OE-25-002707 | 7168 | 32 | 224 | PR-S12-01 | Prairie | 2025-06-25 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002708 | 37874 | 653 | 58 | PR-S13-02 | Prairie | 2025-06-25 | 12 | Weather - wind | Feeder recloser | Forced | None
OE-25-002709 | 784 | 7 | 112 | BY-S18-01 | Bayou | 2025-06-25 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002710 | 2460 | 12 | 205 | CR-S29-02 | Crossroads | 2025-06-25 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-002711 | 1210 | 11 | 110 | BY-S13-05 | Bayou | 2025-06-25 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-002712 | 65286 | 1053 | 62 | CR-S07-05 | Crossroads | 2025-06-25 | 18 | Equipment - underground | Feeder recloser | Forced | None
OE-25-002713 | 27391 | 637 | 43 | CR-S22-04 | Crossroads | 2025-06-25 | 18 | Animal | Feeder recloser | Forced | None
OE-25-002714 | 425 | 5 | 85 | BY-S10-04 | Bayou | 2025-06-26 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002715 | 41013 | 279 | 147 | BY-S13-04 | Bayou | 2025-06-26 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002716 | 454 | 2 | 227 | BY-S23-01 | Bayou | 2025-06-26 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002717 | 30008 | 484 | 62 | CR-S08-05 | Crossroads | 2025-06-26 | 9 | Animal | Feeder recloser | Forced | None
OE-25-002718 | 19596 | 213 | 92 | PR-S15-01 | Prairie | 2025-06-26 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002719 | 180 | 1 | 180 | BY-S08-02 | Bayou | 2025-06-26 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002720 | 30600 | 300 | 102 | PR-S13-03 | Prairie | 2025-06-26 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-002721 | 75735 | 891 | 85 | CR-S25-04 | Crossroads | 2025-06-26 | 13 | Animal | Substation breaker | Forced | None
OE-25-002722 | 1050 | 25 | 42 | BY-S16-06 | Bayou | 2025-06-26 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-002723 | 1066 | 13 | 82 | CR-S27-04 | Crossroads | 2025-06-26 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002724 | 9940 | 142 | 70 | BY-S13-04 | Bayou | 2025-06-26 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002725 | 8236 | 58 | 142 | BY-S16-04 | Bayou | 2025-06-26 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002726 | 248 | 2 | 124 | BY-S26-06 | Bayou | 2025-06-26 | 21 | Animal | Transformer fuse | Forced | None
OE-25-002727 | 1029 | 7 | 147 | BY-S19-03 | Bayou | 2025-06-26 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002728 | 1284 | 6 | 214 | HB-S03-01 | Harbor | 2025-06-27 | 3 | Vegetation | Transformer fuse | Forced | None
OE-25-002729 | 1890 | 14 | 135 | CR-S16-05 | Crossroads | 2025-06-27 | 6 | Animal | Transformer fuse | Forced | None
OE-25-002730 | 1890 | 18 | 105 | BY-S09-05 | Bayou | 2025-06-27 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002731 | 4475 | 25 | 179 | HB-S19-02 | Harbor | 2025-06-27 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002732 | 2774 | 38 | 73 | CR-S07-03 | Crossroads | 2025-06-27 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002733 | 38412 | 194 | 198 | PR-S07-06 | Prairie | 2025-06-27 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-002734 | 52650 | 650 | 81 | BY-S22-02 | Bayou | 2025-06-27 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-002735 | 2967 | 23 | 129 | HB-S17-03 | Harbor | 2025-06-27 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002736 | 8299 | 43 | 193 | HB-S14-02 | Harbor | 2025-06-27 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-002737 | 4625 | 25 | 185 | BY-S30-01 | Bayou | 2025-06-27 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-002738 | 418692 | 3772 | 111 | CR-S16-02 | Crossroads | 2025-06-27 | 16 | Equipment - overhead | Substation breaker | Forced | None
OE-25-002739 | 5544 | 33 | 168 | CR-S04-06 | Crossroads | 2025-06-27 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-002740 | 18788 | 122 | 154 | PR-S18-04 | Prairie | 2025-06-27 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-002741 | 468 | 6 | 78 | PR-S11-02 | Prairie | 2025-06-27 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-002742 | 42720 | 890 | 48 | CR-S02-05 | Crossroads | 2025-06-27 | 23 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002743 | 6084 | 39 | 156 | PR-S14-04 | Prairie | 2025-06-28 | 0 | Unknown | Lateral fuse | Forced | None
OE-25-002744 | 8740 | 190 | 46 | BY-S29-01 | Bayou | 2025-06-28 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002745 | 882 | 6 | 147 | PR-S19-01 | Prairie | 2025-06-28 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002746 | 17850 | 75 | 238 | BY-S30-03 | Bayou | 2025-06-28 | 14 | Animal | Lateral fuse | Forced | None
OE-25-002747 | 854 | 7 | 122 | HB-S08-04 | Harbor | 2025-06-28 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-002748 | 1978 | 43 | 46 | HB-S09-03 | Harbor | 2025-06-28 | 18 | Unknown | Lateral fuse | Forced | None
OE-25-002749 | 74936 | 1102 | 68 | CR-S04-03 | Crossroads | 2025-06-28 | 19 | Vegetation | Feeder recloser | Forced | None
OE-25-002750 | 11005 | 71 | 155 | CR-S04-05 | Crossroads | 2025-06-28 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-002751 | 34804 | 226 | 154 | BY-S02-02 | Bayou | 2025-06-28 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-002752 | 312 | 3 | 104 | BY-S25-02 | Bayou | 2025-06-29 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002753 | 7638 | 38 | 201 | BY-S19-04 | Bayou | 2025-06-29 | 2 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002754 | 4176 | 58 | 72 | PR-S07-05 | Prairie | 2025-06-29 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002755 | 97686 | 1458 | 67 | BY-S20-01 | Bayou | 2025-06-29 | 14 | Equipment - underground | Substation breaker | Forced | None
OE-25-002756 | 5244 | 46 | 114 | PR-S01-02 | Prairie | 2025-06-29 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-002757 | 3690 | 45 | 82 | PR-S13-02 | Prairie | 2025-06-29 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002758 | 3732 | 12 | 311 | CR-S04-05 | Crossroads | 2025-06-29 | 17 | Animal | Transformer fuse | Forced | None
OE-25-002759 | 2148 | 12 | 179 | CR-S09-04 | Crossroads | 2025-06-29 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002760 | 4453 | 61 | 73 | CR-S25-04 | Crossroads | 2025-06-29 | 17 | Animal | Lateral fuse | Forced | None
OE-25-002761 | 3953 | 67 | 59 | HB-S14-01 | Harbor | 2025-06-29 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002762 | 11500 | 125 | 92 | PR-S07-05 | Prairie | 2025-06-29 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002763 | 1584 | 11 | 144 | HB-S01-05 | Harbor | 2025-06-29 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002764 | 1012 | 11 | 92 | CR-S04-06 | Crossroads | 2025-06-29 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002765 | 6348 | 92 | 69 | HB-S17-02 | Harbor | 2025-06-29 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-002766 | 11480 | 56 | 205 | PR-S06-01 | Prairie | 2025-06-29 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-002767 | 3813 | 41 | 93 | BY-S22-04 | Bayou | 2025-06-29 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002768 | 855 | 9 | 95 | CR-S02-04 | Crossroads | 2025-06-29 | 23 | Animal | Transformer fuse | Forced | None
OE-25-002769 | 4422 | 67 | 66 | HB-S01-01 | Harbor | 2025-06-29 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002770 | 1200 | 6 | 200 | PR-S05-03 | Prairie | 2025-06-29 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002771 | 36540 | 140 | 261 | BY-S09-02 | Bayou | 2025-06-30 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-002772 | 6012 | 167 | 36 | CR-S04-02 | Crossroads | 2025-06-30 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002773 | 707 | 7 | 101 | BY-S12-03 | Bayou | 2025-06-30 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002774 | 30864 | 1286 | 24 | CR-S02-03 | Crossroads | 2025-06-30 | 7 | Equipment - underground | Feeder recloser | Forced | None
OE-25-002775 | 429 | 13 | 33 | BY-S03-02 | Bayou | 2025-06-30 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002776 | 6400 | 32 | 200 | BY-S22-03 | Bayou | 2025-06-30 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-002777 | 1548 | 12 | 129 | PR-S10-02 | Prairie | 2025-06-30 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002778 | 10622 | 47 | 226 | BY-S22-04 | Bayou | 2025-06-30 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002779 | 33 | 1 | 33 | CR-S13-06 | Crossroads | 2025-06-30 | 12 | Animal | Transformer fuse | Forced | None
OE-25-002780 | 15910 | 86 | 185 | PR-S01-03 | Prairie | 2025-06-30 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002781 | 1100 | 4 | 275 | BY-S02-01 | Bayou | 2025-06-30 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-002782 | 104166 | 1286 | 81 | CR-S27-04 | Crossroads | 2025-06-30 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-25-002783 | 6854 | 149 | 46 | HB-S10-01 | Harbor | 2025-06-30 | 13 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002784 | 3696 | 33 | 112 | PR-S06-01 | Prairie | 2025-06-30 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002785 | 3692 | 26 | 142 | BY-S11-01 | Bayou | 2025-06-30 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002786 | 7392 | 66 | 112 | CR-S29-01 | Crossroads | 2025-06-30 | 14 | Animal | Lateral fuse | Forced | None
OE-25-002787 | 1188 | 22 | 54 | PR-S03-04 | Prairie | 2025-06-30 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002788 | 16416 | 171 | 96 | PR-S16-05 | Prairie | 2025-06-30 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002789 | 2730 | 7 | 390 | BY-S06-01 | Bayou | 2025-06-30 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-002790 | 475 | 5 | 95 | HB-S15-02 | Harbor | 2025-07-01 | 0 | Unknown | Transformer fuse | Forced | None
OE-25-002791 | 4324 | 23 | 188 | PR-S13-06 | Prairie | 2025-07-01 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-002792 | 1820 | 13 | 140 | HB-S11-03 | Harbor | 2025-07-01 | 2 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002793 | 931 | 7 | 133 | PR-S18-02 | Prairie | 2025-07-01 | 6 | Unknown | Transformer fuse | Forced | None
OE-25-002794 | 17280 | 128 | 135 | HB-S04-02 | Harbor | 2025-07-01 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002795 | 1968 | 12 | 164 | HB-S03-03 | Harbor | 2025-07-01 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002796 | 15330 | 438 | 35 | PR-S05-02 | Prairie | 2025-07-01 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-002797 | 7068 | 38 | 186 | BY-S26-03 | Bayou | 2025-07-01 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002798 | 4732 | 26 | 182 | BY-S04-01 | Bayou | 2025-07-01 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002799 | 3136 | 64 | 49 | BY-S24-03 | Bayou | 2025-07-01 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002800 | 5152 | 46 | 112 | PR-S12-02 | Prairie | 2025-07-01 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002801 | 476 | 7 | 68 | BY-S08-03 | Bayou | 2025-07-01 | 14 | Animal | Transformer fuse | Forced | None
OE-25-002802 | 1668 | 12 | 139 | BY-S12-03 | Bayou | 2025-07-01 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-002803 | 5810 | 83 | 70 | HB-S07-04 | Harbor | 2025-07-01 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-002804 | 26290 | 478 | 55 | PR-S01-03 | Prairie | 2025-07-01 | 15 | Weather - lightning | Feeder recloser | Forced | None
OE-25-002805 | 16038 | 297 | 54 | PR-S08-03 | Prairie | 2025-07-01 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-002806 | 5280 | 44 | 120 | BY-S17-01 | Bayou | 2025-07-01 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-002807 | 17976 | 214 | 84 | CR-S07-03 | Crossroads | 2025-07-01 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002808 | 3752 | 56 | 67 | HB-S02-02 | Harbor | 2025-07-02 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002809 | 3822 | 42 | 91 | HB-S10-01 | Harbor | 2025-07-02 | 4 | Weather - wind | Lateral fuse | Forced | None
OE-25-002810 | 27864 | 162 | 172 | PR-S18-01 | Prairie | 2025-07-02 | 4 | Vegetation | Lateral fuse | Forced | None
OE-25-002811 | 11895 | 65 | 183 | CR-S09-01 | Crossroads | 2025-07-02 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002812 | 4756 | 41 | 116 | PR-S19-01 | Prairie | 2025-07-02 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002813 | 5780 | 34 | 170 | CR-S03-02 | Crossroads | 2025-07-02 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002814 | 1272 | 12 | 106 | PR-S18-04 | Prairie | 2025-07-02 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002815 | 11310 | 78 | 145 | CR-S03-03 | Crossroads | 2025-07-02 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002816 | 2150 | 86 | 25 | CR-S28-03 | Crossroads | 2025-07-02 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002817 | 2567 | 17 | 151 | CR-S08-02 | Crossroads | 2025-07-02 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002818 | 2496 | 48 | 52 | PR-S12-01 | Prairie | 2025-07-02 | 10 | Animal | Lateral fuse | Forced | None
OE-25-002819 | 4148 | 68 | 61 | BY-S01-01 | Bayou | 2025-07-02 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-002820 | 4321 | 29 | 149 | CR-S25-02 | Crossroads | 2025-07-02 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002821 | 3071 | 37 | 83 | HB-S08-03 | Harbor | 2025-07-02 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002822 | 10406 | 86 | 121 | BY-S15-03 | Bayou | 2025-07-02 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002823 | 2100 | 30 | 70 | BY-S26-03 | Bayou | 2025-07-02 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-002824 | 1352 | 4 | 338 | PR-S17-01 | Prairie | 2025-07-02 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-002825 | 520 | 5 | 104 | HB-S19-04 | Harbor | 2025-07-02 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002826 | 20562 | 69 | 298 | PR-S20-02 | Prairie | 2025-07-02 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002827 | 7552 | 59 | 128 | PR-S09-04 | Prairie | 2025-07-03 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002828 | 1305 | 29 | 45 | CR-S14-02 | Crossroads | 2025-07-03 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002829 | 18768 | 782 | 24 | HB-S10-01 | Harbor | 2025-07-03 | 10 | Vegetation | Feeder recloser | Forced | None
OE-25-002830 | 12168 | 72 | 169 | CR-S16-03 | Crossroads | 2025-07-03 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002831 | 8584 | 232 | 37 | CR-S26-06 | Crossroads | 2025-07-03 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002832 | 4560 | 40 | 114 | BY-S29-05 | Bayou | 2025-07-03 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002833 | 11470 | 185 | 62 | CR-S06-01 | Crossroads | 2025-07-03 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-002834 | 94824 | 1317 | 72 | BY-S15-06 | Bayou | 2025-07-03 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002835 | 73920 | 1680 | 44 | HB-S06-02 | Harbor | 2025-07-03 | 15 | Equipment - underground | Substation breaker | Forced | None
OE-25-002836 | 553 | 7 | 79 | PR-S13-03 | Prairie | 2025-07-03 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-002837 | 336 | 7 | 48 | CR-S07-07 | Crossroads | 2025-07-03 | 19 | Animal | Transformer fuse | Forced | None
OE-25-002838 | 22050 | 175 | 126 | HB-S05-03 | Harbor | 2025-07-03 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002839 | 4029 | 51 | 79 | HB-S10-01 | Harbor | 2025-07-04 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-002840 | 1794 | 13 | 138 | PR-S18-06 | Prairie | 2025-07-04 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002841 | 4326 | 103 | 42 | BY-S24-04 | Bayou | 2025-07-04 | 12 | Animal | Lateral fuse | Forced | None
OE-25-002842 | 6946 | 46 | 151 | CR-S32-04 | Crossroads | 2025-07-04 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002843 | 1540 | 10 | 154 | HB-S12-03 | Harbor | 2025-07-04 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002844 | 7268 | 92 | 79 | BY-S21-01 | Bayou | 2025-07-04 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002845 | 1148 | 14 | 82 | CR-S15-03 | Crossroads | 2025-07-04 | 15 | Animal | Transformer fuse | Forced | None
OE-25-002846 | 27192 | 132 | 206 | CR-S31-01 | Crossroads | 2025-07-04 | 16 | Animal | Lateral fuse | Forced | None
OE-25-002847 | 875 | 7 | 125 | PR-S03-03 | Prairie | 2025-07-04 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002848 | 1501 | 19 | 79 | PR-S04-03 | Prairie | 2025-07-04 | 16 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002849 | 294 | 3 | 98 | BY-S21-04 | Bayou | 2025-07-04 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002850 | 14444 | 92 | 157 | BY-S29-03 | Bayou | 2025-07-04 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002851 | 33231 | 1007 | 33 | BY-S18-02 | Bayou | 2025-07-04 | 18 | Weather - lightning | Feeder recloser | Forced | None
OE-25-002852 | 2580 | 12 | 215 | BY-S12-02 | Bayou | 2025-07-04 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002853 | 4335 | 51 | 85 | CR-S07-05 | Crossroads | 2025-07-04 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-002854 | 10836 | 84 | 129 | CR-S31-02 | Crossroads | 2025-07-04 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002855 | 6726 | 57 | 118 | CR-S26-06 | Crossroads | 2025-07-05 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002856 | 8850 | 150 | 59 | HB-S05-03 | Harbor | 2025-07-05 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002857 | 15714 | 194 | 81 | PR-S15-06 | Prairie | 2025-07-05 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002858 | 296 | 2 | 148 | CR-S23-03 | Crossroads | 2025-07-05 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002859 | 1980 | 11 | 180 | BY-S15-04 | Bayou | 2025-07-05 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002860 | 178056 | 2473 | 72 | BY-S29-02 | Bayou | 2025-07-05 | 15 | Vegetation | Substation breaker | Forced | None
OE-25-002861 | 107616 | 608 | 177 | CR-S16-05 | Crossroads | 2025-07-05 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002862 | 890 | 5 | 178 | BY-S27-04 | Bayou | 2025-07-05 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-002863 | 2340 | 13 | 180 | BY-S25-04 | Bayou | 2025-07-05 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002864 | 53041 | 899 | 59 | CR-S04-02 | Crossroads | 2025-07-05 | 20 | Vegetation | Feeder recloser | Forced | None
OE-25-002865 | 1444 | 19 | 76 | BY-S30-03 | Bayou | 2025-07-05 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002866 | 4453 | 73 | 61 | CR-S10-02 | Crossroads | 2025-07-06 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-002867 | 868 | 14 | 62 | BY-S04-03 | Bayou | 2025-07-06 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002868 | 520 | 10 | 52 | BY-S19-02 | Bayou | 2025-07-06 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-25-002869 | 65322 | 1146 | 57 | CR-S07-07 | Crossroads | 2025-07-06 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002870 | 10080 | 90 | 112 | CR-S02-03 | Crossroads | 2025-07-06 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-002871 | 11480 | 205 | 56 | BY-S17-02 | Bayou | 2025-07-06 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002872 | 58366 | 379 | 154 | HB-S04-02 | Harbor | 2025-07-06 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-002873 | 56100 | 561 | 100 | BY-S23-03 | Bayou | 2025-07-06 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002874 | 786 | 6 | 131 | BY-S21-04 | Bayou | 2025-07-06 | 17 | Animal | Transformer fuse | Forced | None
OE-25-002875 | 5424 | 48 | 113 | BY-S16-03 | Bayou | 2025-07-06 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-002876 | 27984 | 176 | 159 | BY-S15-05 | Bayou | 2025-07-06 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-002877 | 4290 | 33 | 130 | HB-S17-02 | Harbor | 2025-07-06 | 19 | Animal | Lateral fuse | Forced | None
OE-25-002878 | 6486 | 46 | 141 | PR-S07-02 | Prairie | 2025-07-06 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-002879 | 645 | 5 | 129 | CR-S20-05 | Crossroads | 2025-07-06 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002880 | 25947 | 279 | 93 | PR-S13-03 | Prairie | 2025-07-07 | 3 | Animal | Feeder recloser | Forced | None
OE-25-002881 | 90678 | 714 | 127 | CR-S22-04 | Crossroads | 2025-07-07 | 5 | Unknown | Feeder recloser | Forced | None
OE-25-002882 | 666 | 9 | 74 | HB-S13-02 | Harbor | 2025-07-07 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-002883 | 620 | 5 | 124 | PR-S16-02 | Prairie | 2025-07-07 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-25-002884 | 4488 | 374 | 12 | HB-S04-02 | Harbor | 2025-07-07 | 9 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002885 | 8364 | 41 | 204 | CR-S05-02 | Crossroads | 2025-07-07 | 11 | Animal | Lateral fuse | Forced | None
OE-25-002886 | 3969 | 63 | 63 | PR-S07-02 | Prairie | 2025-07-07 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002887 | 4238 | 26 | 163 | HB-S01-01 | Harbor | 2025-07-07 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002888 | 56588 | 2021 | 28 | BY-S17-04 | Bayou | 2025-07-07 | 13 | Weather - wind | Substation breaker | Forced | None
OE-25-002889 | 2492 | 14 | 178 | BY-S25-04 | Bayou | 2025-07-07 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002890 | 2875 | 23 | 125 | BY-S30-03 | Bayou | 2025-07-07 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002891 | 7712 | 32 | 241 | CR-S23-03 | Crossroads | 2025-07-07 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002892 | 6592 | 64 | 103 | BY-S09-02 | Bayou | 2025-07-07 | 14 | Animal | Lateral fuse | Forced | None
OE-25-002893 | 959 | 7 | 137 | BY-S15-02 | Bayou | 2025-07-07 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-002894 | 2304 | 24 | 96 | BY-S18-04 | Bayou | 2025-07-07 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-002895 | 165568 | 1592 | 104 | BY-S23-02 | Bayou | 2025-07-07 | 16 | Unknown | Feeder recloser | Forced | None
OE-25-002896 | 95703 | 1387 | 69 | BY-S29-02 | Bayou | 2025-07-07 | 16 | Unknown | Feeder recloser | Forced | None
OE-25-002897 | 362 | 2 | 181 | CR-S14-05 | Crossroads | 2025-07-07 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002898 | 20221 | 277 | 73 | HB-S02-03 | Harbor | 2025-07-07 | 16 | Animal | Lateral fuse | Forced | None
OE-25-002899 | 17514 | 139 | 126 | CR-S07-07 | Crossroads | 2025-07-07 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002900 | 1250 | 10 | 125 | CR-S19-01 | Crossroads | 2025-07-07 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002901 | 30492 | 132 | 231 | HB-S15-03 | Harbor | 2025-07-07 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002902 | 7800 | 104 | 75 | BY-S22-04 | Bayou | 2025-07-07 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002903 | 38420 | 170 | 226 | PR-S18-04 | Prairie | 2025-07-07 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-002904 | 9968 | 56 | 178 | BY-S26-01 | Bayou | 2025-07-08 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002905 | 1145 | 5 | 229 | BY-S13-06 | Bayou | 2025-07-08 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002906 | 8040 | 60 | 134 | BY-S23-05 | Bayou | 2025-07-08 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002907 | 10336 | 68 | 152 | PR-S01-05 | Prairie | 2025-07-08 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002908 | 1024 | 8 | 128 | PR-S13-03 | Prairie | 2025-07-08 | 9 | Unknown | Transformer fuse | Forced | None
OE-25-002909 | 1212 | 12 | 101 | BY-S24-03 | Bayou | 2025-07-08 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002910 | 7134 | 29 | 246 | PR-S16-05 | Prairie | 2025-07-08 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002911 | 2400 | 12 | 200 | PR-S02-02 | Prairie | 2025-07-08 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002912 | 1924 | 13 | 148 | HB-S16-03 | Harbor | 2025-07-08 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002913 | 2626 | 13 | 202 | BY-S28-03 | Bayou | 2025-07-08 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002914 | 201 | 3 | 67 | CR-S08-02 | Crossroads | 2025-07-08 | 16 | Animal | Transformer fuse | Forced | None
OE-25-002915 | 15010 | 190 | 79 | CR-S01-03 | Crossroads | 2025-07-08 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002916 | 1120 | 14 | 80 | CR-S19-01 | Crossroads | 2025-07-08 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002917 | 12816 | 356 | 36 | CR-S31-03 | Crossroads | 2025-07-08 | 23 | Vegetation | Feeder recloser | Forced | None
OE-25-002918 | 60066 | 846 | 71 | HB-S15-01 | Harbor | 2025-07-09 | 7 | Equipment - underground | Substation breaker | Forced | None
OE-25-002919 | 19557 | 53 | 369 | BY-S16-03 | Bayou | 2025-07-09 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-002920 | 51920 | 1298 | 40 | BY-S25-03 | Bayou | 2025-07-09 | 8 | Vegetation | Substation breaker | Forced | None
OE-25-002921 | 2448 | 9 | 272 | HB-S03-03 | Harbor | 2025-07-09 | 8 | Animal | Transformer fuse | Forced | None
OE-25-002922 | 4859 | 43 | 113 | CR-S30-02 | Crossroads | 2025-07-09 | 10 | Unknown | Lateral fuse | Forced | None
OE-25-002923 | 59850 | 1425 | 42 | HB-S09-03 | Harbor | 2025-07-09 | 10 | Weather - lightning | Substation breaker | Forced | None
OE-25-002924 | 1820 | 13 | 140 | PR-S06-03 | Prairie | 2025-07-09 | 12 | Animal | Transformer fuse | Forced | None
OE-25-002925 | 1600 | 16 | 100 | BY-S16-04 | Bayou | 2025-07-09 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002926 | 119692 | 1301 | 92 | CR-S31-02 | Crossroads | 2025-07-09 | 13 | Vegetation | Feeder recloser | Forced | None
OE-25-002927 | 21090 | 114 | 185 | HB-S09-02 | Harbor | 2025-07-09 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002928 | 267 | 3 | 89 | BY-S17-02 | Bayou | 2025-07-09 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-002929 | 14868 | 59 | 252 | CR-S02-02 | Crossroads | 2025-07-09 | 17 | Animal | Lateral fuse | Forced | None
OE-25-002930 | 1080 | 12 | 90 | BY-S09-04 | Bayou | 2025-07-09 | 19 | Animal | Transformer fuse | Forced | None
OE-25-002931 | 52838 | 911 | 58 | PR-S02-01 | Prairie | 2025-07-09 | 19 | Equipment - overhead | Substation breaker | Forced | None
OE-25-002932 | 2898 | 69 | 42 | PR-S19-01 | Prairie | 2025-07-09 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-002933 | 11025 | 75 | 147 | CR-S12-01 | Crossroads | 2025-07-09 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002934 | 15340 | 65 | 236 | PR-S18-02 | Prairie | 2025-07-09 | 20 | Animal | Lateral fuse | Forced | None
OE-25-002935 | 2574 | 9 | 286 | PR-S19-05 | Prairie | 2025-07-09 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002936 | 136012 | 919 | 148 | CR-S01-03 | Crossroads | 2025-07-09 | 22 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002937 | 9860 | 29 | 340 | BY-S18-04 | Bayou | 2025-07-09 | 23 | Vegetation | Lateral fuse | Forced | None
OE-25-002938 | 1690 | 13 | 130 | BY-S25-04 | Bayou | 2025-07-10 | 5 | Vegetation | Transformer fuse | Forced | None
OE-25-002939 | 595 | 7 | 85 | BY-S13-04 | Bayou | 2025-07-10 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002940 | 4015 | 55 | 73 | BY-S01-01 | Bayou | 2025-07-10 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-002941 | 2988 | 12 | 249 | PR-S01-02 | Prairie | 2025-07-10 | 9 | Animal | Transformer fuse | Forced | None
OE-25-002942 | 980 | 10 | 98 | CR-S05-05 | Crossroads | 2025-07-10 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-002943 | 4508 | 46 | 98 | BY-S03-02 | Bayou | 2025-07-10 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002944 | 32766 | 381 | 86 | CR-S22-02 | Crossroads | 2025-07-10 | 14 | Vegetation | IGSD-isolated section | Forced | None
OE-25-002945 | 612 | 6 | 102 | HB-S08-01 | Harbor | 2025-07-10 | 16 | Unknown | Transformer fuse | Forced | None
OE-25-002946 | 14960 | 170 | 88 | PR-S01-04 | Prairie | 2025-07-10 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002947 | 11532 | 124 | 93 | BY-S18-06 | Bayou | 2025-07-10 | 22 | Unknown | Lateral fuse | Forced | None
OE-25-002948 | 284 | 2 | 142 | BY-S19-02 | Bayou | 2025-07-10 | 23 | Animal | Transformer fuse | Forced | None
OE-25-002949 | 3399 | 33 | 103 | BY-S30-01 | Bayou | 2025-07-10 | 23 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002950 | 1470 | 10 | 147 | PR-S19-03 | Prairie | 2025-07-11 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002951 | 3969 | 27 | 147 | PR-S10-02 | Prairie | 2025-07-11 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-25-002952 | 186 | 2 | 93 | BY-S25-04 | Bayou | 2025-07-11 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-25-002953 | 1196 | 23 | 52 | BY-S21-04 | Bayou | 2025-07-11 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002954 | 2268 | 28 | 81 | HB-S12-01 | Harbor | 2025-07-11 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-002955 | 954 | 6 | 159 | PR-S20-01 | Prairie | 2025-07-11 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-002956 | 238206 | 3219 | 74 | CR-S04-06 | Crossroads | 2025-07-11 | 19 | Unknown | Substation breaker | Outside cause | None
OE-25-002957 | 821791 | 3527 | 233 | CR-S14-02 | Crossroads | 2025-07-11 | 20 | Vehicle or public | Substation breaker | Forced | None
OE-25-002958 | 6298 | 94 | 67 | BY-S13-02 | Bayou | 2025-07-11 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002959 | 775 | 5 | 155 | BY-S23-02 | Bayou | 2025-07-11 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002960 | 43785 | 417 | 105 | BY-S16-02 | Bayou | 2025-07-12 | 6 | Animal | IGSD-isolated section | Forced | None
OE-25-002961 | 1323 | 7 | 189 | PR-S04-01 | Prairie | 2025-07-12 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-002962 | 148960 | 1120 | 133 | CR-S31-02 | Crossroads | 2025-07-12 | 9 | Equipment - underground | Feeder recloser | Forced | None
OE-25-002963 | 45008 | 776 | 58 | CR-S01-04 | Crossroads | 2025-07-12 | 10 | Vegetation | Substation breaker | Forced | None
OE-25-002964 | 792 | 6 | 132 | BY-S29-05 | Bayou | 2025-07-12 | 11 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002965 | 3471 | 39 | 89 | CR-S28-03 | Crossroads | 2025-07-12 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-25-002966 | 632 | 4 | 158 | PR-S10-02 | Prairie | 2025-07-12 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-25-002967 | 113940 | 2110 | 54 | BY-S17-02 | Bayou | 2025-07-12 | 13 | Weather - wind | Substation breaker | Forced | None
OE-25-002968 | 810 | 10 | 81 | BY-S23-03 | Bayou | 2025-07-12 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-25-002969 | 66976 | 728 | 92 | PR-S06-01 | Prairie | 2025-07-12 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-002970 | 2556 | 36 | 71 | CR-S13-05 | Crossroads | 2025-07-12 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-002971 | 21528 | 598 | 36 | BY-S02-01 | Bayou | 2025-07-12 | 17 | Animal | Feeder recloser | Forced | None
OE-25-002972 | 1560 | 26 | 60 | BY-S26-01 | Bayou | 2025-07-12 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-002973 | 592 | 4 | 148 | CR-S04-01 | Crossroads | 2025-07-12 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002974 | 2448 | 12 | 204 | CR-S11-01 | Crossroads | 2025-07-12 | 20 | Animal | Transformer fuse | Forced | None
OE-25-002975 | 832 | 8 | 104 | PR-S15-06 | Prairie | 2025-07-12 | 23 | Animal | Transformer fuse | Forced | None
OE-25-002976 | 13203 | 81 | 163 | BY-S09-04 | Bayou | 2025-07-13 | 0 | Unknown | Lateral fuse | Forced | None
OE-25-002977 | 1768 | 34 | 52 | HB-S09-03 | Harbor | 2025-07-13 | 4 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002978 | 21879 | 221 | 99 | BY-S25-03 | Bayou | 2025-07-13 | 6 | Animal | Lateral fuse | Forced | None
OE-25-002979 | 9240 | 60 | 154 | CR-S32-01 | Crossroads | 2025-07-13 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-002980 | 29016 | 186 | 156 | HB-S16-03 | Harbor | 2025-07-13 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002981 | 5610 | 33 | 170 | CR-S28-04 | Crossroads | 2025-07-13 | 8 | Animal | Lateral fuse | Forced | None
OE-25-002982 | 2448 | 12 | 204 | BY-S07-02 | Bayou | 2025-07-13 | 11 | Animal | Transformer fuse | Forced | None
OE-25-002983 | 46530 | 705 | 66 | BY-S28-03 | Bayou | 2025-07-13 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-25-002984 | 612 | 6 | 102 | BY-S17-01 | Bayou | 2025-07-13 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002985 | 2301 | 13 | 177 | HB-S03-03 | Harbor | 2025-07-13 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-002986 | 1143 | 9 | 127 | BY-S10-03 | Bayou | 2025-07-13 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-002987 | 5428 | 92 | 59 | HB-S11-01 | Harbor | 2025-07-13 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-002988 | 4070 | 55 | 74 | PR-S14-04 | Prairie | 2025-07-13 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-25-002989 | 678 | 6 | 113 | CR-S11-01 | Crossroads | 2025-07-13 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-002990 | 49312 | 368 | 134 | HB-S16-04 | Harbor | 2025-07-13 | 17 | Unknown | Lateral fuse | Forced | None
OE-25-002991 | 44545 | 151 | 295 | PR-S03-01 | Prairie | 2025-07-13 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-002992 | 5586 | 14 | 399 | CR-S23-04 | Crossroads | 2025-07-13 | 18 | Animal | Transformer fuse | Forced | None
OE-25-002993 | 367540 | 3910 | 94 | HB-S17-02 | Harbor | 2025-07-13 | 20 | Weather - lightning | Substation breaker | Forced | None
OE-25-002994 | 144 | 1 | 144 | BY-S01-01 | Bayou | 2025-07-13 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-002995 | 4945 | 115 | 43 | PR-S03-01 | Prairie | 2025-07-14 | 4 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-002996 | 1298 | 22 | 59 | CR-S21-02 | Crossroads | 2025-07-14 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-25-002997 | 1909 | 23 | 83 | CR-S25-01 | Crossroads | 2025-07-14 | 6 | Vegetation | Lateral fuse | Forced | None
OE-25-002998 | 8201 | 59 | 139 | BY-S21-02 | Bayou | 2025-07-14 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-002999 | 2130 | 10 | 213 | PR-S07-04 | Prairie | 2025-07-14 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003000 | 8816 | 76 | 116 | HB-S17-01 | Harbor | 2025-07-14 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003001 | 3219 | 37 | 87 | BY-S29-05 | Bayou | 2025-07-14 | 13 | Unknown | Lateral fuse | Forced | None
OE-25-003002 | 1071 | 7 | 153 | PR-S07-06 | Prairie | 2025-07-14 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-003003 | 80884 | 554 | 146 | BY-S15-06 | Bayou | 2025-07-14 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-003004 | 1918 | 14 | 137 | BY-S04-03 | Bayou | 2025-07-14 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-003005 | 132328 | 2363 | 56 | CR-S20-02 | Crossroads | 2025-07-14 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-003006 | 5559 | 51 | 109 | PR-S19-05 | Prairie | 2025-07-14 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003007 | 13695 | 83 | 165 | PR-S04-01 | Prairie | 2025-07-15 | 4 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003008 | 2938 | 13 | 226 | HB-S11-01 | Harbor | 2025-07-15 | 5 | Vegetation | Transformer fuse | Forced | None
OE-25-003009 | 30294 | 81 | 374 | BY-S14-01 | Bayou | 2025-07-15 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003010 | 448 | 4 | 112 | BY-S15-02 | Bayou | 2025-07-15 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003011 | 294 | 2 | 147 | CR-S15-02 | Crossroads | 2025-07-15 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003012 | 11687 | 377 | 31 | BY-S27-02 | Bayou | 2025-07-15 | 9 | Animal | Feeder recloser | Forced | None
OE-25-003013 | 202675 | 335 | 605 | BY-S28-03 | Bayou | 2025-07-15 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003014 | 29056 | 128 | 227 | PR-S18-04 | Prairie | 2025-07-15 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003015 | 48039 | 239 | 201 | PR-S16-04 | Prairie | 2025-07-15 | 14 | Animal | Feeder recloser | Forced | None
OE-25-003016 | 1248 | 8 | 156 | BY-S06-03 | Bayou | 2025-07-15 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003017 | 528 | 8 | 66 | BY-S07-01 | Bayou | 2025-07-15 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003018 | 14194 | 151 | 94 | BY-S12-02 | Bayou | 2025-07-15 | 15 | Animal | Lateral fuse | Forced | None
OE-25-003019 | 47918 | 494 | 97 | CR-S23-03 | Crossroads | 2025-07-15 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-003020 | 1026 | 9 | 114 | CR-S24-03 | Crossroads | 2025-07-15 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003021 | 5481 | 87 | 63 | BY-S17-03 | Bayou | 2025-07-15 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-003022 | 8316 | 66 | 126 | CR-S06-03 | Crossroads | 2025-07-15 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003023 | 4140 | 69 | 60 | BY-S22-04 | Bayou | 2025-07-15 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003024 | 6370 | 70 | 91 | CR-S14-03 | Crossroads | 2025-07-15 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-003025 | 10146 | 114 | 89 | CR-S19-01 | Crossroads | 2025-07-15 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003026 | 945 | 9 | 105 | BY-S11-02 | Bayou | 2025-07-16 | 0 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003027 | 49260 | 821 | 60 | CR-S30-01 | Crossroads | 2025-07-16 | 2 | Vegetation | Feeder recloser | Forced | None
OE-25-003028 | 1700 | 10 | 170 | BY-S12-02 | Bayou | 2025-07-16 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003029 | 17028 | 198 | 86 | CR-S16-02 | Crossroads | 2025-07-16 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003030 | 21208 | 241 | 88 | CR-S03-01 | Crossroads | 2025-07-16 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003031 | 266 | 2 | 133 | CR-S13-06 | Crossroads | 2025-07-16 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003032 | 940 | 5 | 188 | BY-S23-03 | Bayou | 2025-07-16 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003033 | 1200 | 10 | 120 | BY-S29-05 | Bayou | 2025-07-16 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003034 | 1344 | 14 | 96 | HB-S17-01 | Harbor | 2025-07-16 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003035 | 5143 | 37 | 139 | BY-S27-06 | Bayou | 2025-07-16 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003036 | 696 | 12 | 58 | BY-S09-05 | Bayou | 2025-07-16 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-003037 | 2088 | 9 | 232 | BY-S15-02 | Bayou | 2025-07-16 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-003038 | 6500 | 26 | 250 | CR-S29-01 | Crossroads | 2025-07-16 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003039 | 3520 | 88 | 40 | CR-S28-03 | Crossroads | 2025-07-16 | 18 | Animal | Lateral fuse | Forced | None
OE-25-003040 | 121218 | 1362 | 89 | CR-S13-04 | Crossroads | 2025-07-17 | 6 | Animal | Substation breaker | Forced | None
OE-25-003041 | 1059 | 3 | 353 | PR-S10-01 | Prairie | 2025-07-17 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003042 | 2581 | 29 | 89 | HB-S16-05 | Harbor | 2025-07-17 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003043 | 585 | 3 | 195 | BY-S05-03 | Bayou | 2025-07-17 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-003044 | 840 | 10 | 84 | PR-S19-03 | Prairie | 2025-07-17 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003045 | 36512 | 652 | 56 | PR-S01-02 | Prairie | 2025-07-17 | 9 | Animal | Feeder recloser | Forced | None
OE-25-003046 | 2288 | 13 | 176 | CR-S24-03 | Crossroads | 2025-07-17 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-25-003047 | 4396 | 14 | 314 | HB-S03-02 | Harbor | 2025-07-17 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003048 | 2743 | 13 | 211 | PR-S09-03 | Prairie | 2025-07-17 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003049 | 325 | 5 | 65 | BY-S27-02 | Bayou | 2025-07-17 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003050 | 3475 | 25 | 139 | BY-S26-02 | Bayou | 2025-07-17 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003051 | 1276 | 22 | 58 | BY-S29-01 | Bayou | 2025-07-17 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003052 | 110 | 1 | 110 | BY-S09-05 | Bayou | 2025-07-17 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003053 | 903 | 3 | 301 | PR-S14-01 | Prairie | 2025-07-17 | 17 | Animal | Transformer fuse | Forced | None
OE-25-003054 | 28067 | 221 | 127 | PR-S13-04 | Prairie | 2025-07-17 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-003055 | 14664 | 564 | 26 | CR-S23-01 | Crossroads | 2025-07-17 | 22 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003056 | 3744 | 96 | 39 | HB-S01-05 | Harbor | 2025-07-18 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003057 | 18249 | 237 | 77 | BY-S13-04 | Bayou | 2025-07-18 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-003058 | 5220 | 45 | 116 | BY-S23-02 | Bayou | 2025-07-18 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003059 | 676 | 4 | 169 | CR-S24-02 | Crossroads | 2025-07-18 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003060 | 9514 | 71 | 134 | PR-S03-03 | Prairie | 2025-07-18 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003061 | 1425 | 5 | 285 | CR-S24-03 | Crossroads | 2025-07-18 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003062 | 26962 | 122 | 221 | CR-S25-01 | Crossroads | 2025-07-18 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003063 | 880 | 10 | 88 | PR-S08-03 | Prairie | 2025-07-18 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-003064 | 26208 | 208 | 126 | BY-S24-04 | Bayou | 2025-07-18 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-003065 | 3750 | 25 | 150 | CR-S07-03 | Crossroads | 2025-07-18 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-003066 | 15075 | 225 | 67 | CR-S14-05 | Crossroads | 2025-07-18 | 18 | Animal | Lateral fuse | Forced | None
OE-25-003067 | 1001 | 11 | 91 | BY-S09-01 | Bayou | 2025-07-18 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-003068 | 1708 | 14 | 122 | PR-S05-03 | Prairie | 2025-07-18 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003069 | 11952 | 83 | 144 | BY-S27-02 | Bayou | 2025-07-18 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-003070 | 10080 | 105 | 96 | PR-S07-01 | Prairie | 2025-07-18 | 23 | Animal | Lateral fuse | Forced | None
OE-25-003071 | 460 | 5 | 92 | CR-S20-05 | Crossroads | 2025-07-19 | 1 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003072 | 19908 | 316 | 63 | BY-S06-02 | Bayou | 2025-07-19 | 3 | Animal | Lateral fuse | Forced | None
OE-25-003073 | 7104 | 74 | 96 | BY-S26-05 | Bayou | 2025-07-19 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003074 | 648 | 8 | 81 | CR-S02-03 | Crossroads | 2025-07-19 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003075 | 2392 | 13 | 184 | PR-S01-04 | Prairie | 2025-07-19 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003076 | 14320 | 179 | 80 | PR-S03-05 | Prairie | 2025-07-19 | 8 | Unknown | Lateral fuse | Forced | None
OE-25-003077 | 5206 | 38 | 137 | PR-S16-01 | Prairie | 2025-07-19 | 8 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003078 | 616 | 7 | 88 | CR-S15-03 | Crossroads | 2025-07-19 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003079 | 103 | 1 | 103 | HB-S02-02 | Harbor | 2025-07-19 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003080 | 101659 | 367 | 277 | PR-S09-02 | Prairie | 2025-07-19 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003081 | 105939 | 711 | 149 | CR-S22-04 | Crossroads | 2025-07-19 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-003082 | 83961 | 1473 | 57 | CR-S14-01 | Crossroads | 2025-07-19 | 14 | Vehicle or public | Substation breaker | Forced | None
OE-25-003083 | 9594 | 117 | 82 | HB-S06-05 | Harbor | 2025-07-19 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003084 | 1463 | 11 | 133 | HB-S09-02 | Harbor | 2025-07-19 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-003085 | 9894 | 97 | 102 | CR-S04-01 | Crossroads | 2025-07-19 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003086 | 1199 | 11 | 109 | BY-S27-03 | Bayou | 2025-07-19 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-003087 | 4788 | 63 | 76 | BY-S08-02 | Bayou | 2025-07-19 | 19 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003088 | 3822 | 14 | 273 | CR-S04-03 | Crossroads | 2025-07-19 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003089 | 2904 | 11 | 264 | PR-S18-01 | Prairie | 2025-07-19 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003090 | 702 | 6 | 117 | BY-S30-01 | Bayou | 2025-07-20 | 3 | Weather - wind | Transformer fuse | Forced | None
OE-25-003091 | 10250 | 82 | 125 | BY-S21-05 | Bayou | 2025-07-20 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-003092 | 832 | 13 | 64 | BY-S23-02 | Bayou | 2025-07-20 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-003093 | 864 | 8 | 108 | CR-S07-03 | Crossroads | 2025-07-20 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003094 | 203322 | 4326 | 47 | HB-S12-02 | Harbor | 2025-07-20 | 9 | Weather - lightning | Substation breaker | Forced | None
OE-25-003095 | 1950 | 13 | 150 | CR-S30-03 | Crossroads | 2025-07-20 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003096 | 2146 | 58 | 37 | BY-S13-06 | Bayou | 2025-07-20 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003097 | 3382 | 38 | 89 | HB-S12-01 | Harbor | 2025-07-20 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003098 | 10730 | 74 | 145 | PR-S02-03 | Prairie | 2025-07-20 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-25-003099 | 7137 | 39 | 183 | PR-S02-03 | Prairie | 2025-07-20 | 12 | Animal | Lateral fuse | Forced | None
OE-25-003100 | 122159 | 809 | 151 | CR-S19-04 | Crossroads | 2025-07-20 | 13 | Animal | Feeder recloser | Forced | None
OE-25-003101 | 1397 | 11 | 127 | BY-S17-01 | Bayou | 2025-07-20 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-003102 | 3024 | 14 | 216 | BY-S23-01 | Bayou | 2025-07-20 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003103 | 285 | 3 | 95 | HB-S01-05 | Harbor | 2025-07-20 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003104 | 31680 | 330 | 96 | HB-S13-01 | Harbor | 2025-07-20 | 16 | Animal | IGSD-isolated section | Forced | None
OE-25-003105 | 19855 | 209 | 95 | CR-S20-01 | Crossroads | 2025-07-20 | 18 | Vegetation | IGSD-isolated section | Forced | None
OE-25-003106 | 572 | 11 | 52 | CR-S24-04 | Crossroads | 2025-07-20 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003107 | 27125 | 217 | 125 | HB-S05-05 | Harbor | 2025-07-20 | 18 | Animal | Lateral fuse | Forced | None
OE-25-003108 | 7755 | 141 | 55 | PR-S16-02 | Prairie | 2025-07-20 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-003109 | 61100 | 940 | 65 | PR-S08-03 | Prairie | 2025-07-20 | 21 | Vegetation | Feeder recloser | Forced | None
OE-25-003110 | 1728 | 12 | 144 | PR-S16-01 | Prairie | 2025-07-20 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003111 | 7747 | 127 | 61 | BY-S24-05 | Bayou | 2025-07-20 | 23 | Unknown | Lateral fuse | Forced | None
OE-25-003112 | 2470 | 19 | 130 | CR-S08-02 | Crossroads | 2025-07-21 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003113 | 2366 | 13 | 182 | BY-S04-01 | Bayou | 2025-07-21 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003114 | 15041 | 169 | 89 | PR-S13-02 | Prairie | 2025-07-21 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003115 | 19095 | 285 | 67 | PR-S16-02 | Prairie | 2025-07-21 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003116 | 621 | 9 | 69 | BY-S01-01 | Bayou | 2025-07-21 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-003117 | 5270 | 31 | 170 | BY-S29-03 | Bayou | 2025-07-21 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003118 | 31866 | 678 | 47 | HB-S06-04 | Harbor | 2025-07-21 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003119 | 1768 | 13 | 136 | HB-S11-03 | Harbor | 2025-07-21 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003120 | 6264 | 232 | 27 | HB-S08-04 | Harbor | 2025-07-21 | 14 | Animal | Lateral fuse | Forced | None
OE-25-003121 | 1932 | 14 | 138 | PR-S01-04 | Prairie | 2025-07-21 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003122 | 121770 | 297 | 410 | BY-S05-01 | Bayou | 2025-07-21 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003123 | 17520 | 240 | 73 | BY-S18-04 | Bayou | 2025-07-21 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003124 | 800 | 5 | 160 | HB-S10-03 | Harbor | 2025-07-21 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003125 | 118656 | 1236 | 96 | CR-S17-03 | Crossroads | 2025-07-21 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-25-003126 | 328 | 1 | 328 | HB-S06-05 | Harbor | 2025-07-21 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-003127 | 1536 | 8 | 192 | BY-S07-05 | Bayou | 2025-07-21 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-003128 | 490 | 5 | 98 | CR-S24-01 | Crossroads | 2025-07-21 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003129 | 2040 | 12 | 170 | CR-S26-05 | Crossroads | 2025-07-21 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003130 | 924 | 6 | 154 | HB-S12-02 | Harbor | 2025-07-21 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003131 | 728 | 7 | 104 | PR-S04-02 | Prairie | 2025-07-21 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003132 | 102339 | 1233 | 83 | PR-S02-02 | Prairie | 2025-07-21 | 20 | Weather - lightning | Substation breaker | Forced | None
OE-25-003133 | 25137 | 441 | 57 | HB-S03-02 | Harbor | 2025-07-21 | 22 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003134 | 51040 | 319 | 160 | PR-S15-03 | Prairie | 2025-07-21 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003135 | 10502 | 59 | 178 | BY-S29-02 | Bayou | 2025-07-21 | 23 | Vegetation | Lateral fuse | Forced | None
OE-25-003136 | 1132 | 4 | 283 | HB-S09-03 | Harbor | 2025-07-22 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003137 | 7182 | 42 | 171 | PR-S09-01 | Prairie | 2025-07-22 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-003138 | 182648 | 1343 | 136 | CR-S05-03 | Crossroads | 2025-07-22 | 2 | Vegetation | Substation breaker | Forced | None
OE-25-003139 | 2160 | 12 | 180 | BY-S25-04 | Bayou | 2025-07-22 | 6 | Animal | Transformer fuse | Forced | None
OE-25-003140 | 22200 | 150 | 148 | CR-S28-03 | Crossroads | 2025-07-22 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003141 | 1456 | 14 | 104 | BY-S19-03 | Bayou | 2025-07-22 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-003142 | 30644 | 188 | 163 | CR-S08-02 | Crossroads | 2025-07-22 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003143 | 1748 | 38 | 46 | BY-S29-03 | Bayou | 2025-07-22 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-003144 | 260 | 2 | 130 | HB-S08-02 | Harbor | 2025-07-22 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-003145 | 144 | 1 | 144 | PR-S04-01 | Prairie | 2025-07-22 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003146 | 10659 | 51 | 209 | HB-S05-02 | Harbor | 2025-07-22 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003147 | 612 | 2 | 306 | PR-S15-01 | Prairie | 2025-07-22 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-003148 | 2330 | 10 | 233 | PR-S19-02 | Prairie | 2025-07-22 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003149 | 68327 | 301 | 227 | PR-S01-05 | Prairie | 2025-07-22 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-003150 | 826 | 14 | 59 | CR-S26-05 | Crossroads | 2025-07-22 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003151 | 7772 | 58 | 134 | BY-S25-02 | Bayou | 2025-07-22 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-003152 | 1566 | 29 | 54 | BY-S27-06 | Bayou | 2025-07-22 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-003153 | 1991 | 11 | 181 | CR-S30-07 | Crossroads | 2025-07-23 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003154 | 18300 | 100 | 183 | CR-S14-02 | Crossroads | 2025-07-23 | 2 | Animal | Lateral fuse | Forced | None
OE-25-003155 | 62006 | 301 | 206 | HB-S07-05 | Harbor | 2025-07-23 | 5 | Vegetation | IGSD-isolated section | Forced | None
OE-25-003156 | 11440 | 80 | 143 | HB-S10-01 | Harbor | 2025-07-23 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-25-003157 | 2359 | 7 | 337 | BY-S19-02 | Bayou | 2025-07-23 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003158 | 1029 | 7 | 147 | CR-S08-01 | Crossroads | 2025-07-23 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003159 | 924 | 6 | 154 | CR-S20-05 | Crossroads | 2025-07-23 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003160 | 91 | 1 | 91 | BY-S04-01 | Bayou | 2025-07-23 | 11 | Animal | Transformer fuse | Forced | None
OE-25-003161 | 3432 | 24 | 143 | PR-S07-06 | Prairie | 2025-07-23 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-25-003162 | 385 | 5 | 77 | PR-S01-05 | Prairie | 2025-07-23 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003163 | 31500 | 252 | 125 | BY-S18-06 | Bayou | 2025-07-23 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003164 | 1200 | 4 | 300 | HB-S20-03 | Harbor | 2025-07-23 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003165 | 7392 | 32 | 231 | BY-S16-05 | Bayou | 2025-07-23 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003166 | 12192 | 96 | 127 | CR-S16-03 | Crossroads | 2025-07-23 | 19 | Animal | Lateral fuse | Forced | None
OE-25-003167 | 909 | 9 | 101 | PR-S01-05 | Prairie | 2025-07-23 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-25-003168 | 450 | 10 | 45 | BY-S29-05 | Bayou | 2025-07-23 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-003169 | 696 | 12 | 58 | CR-S25-04 | Crossroads | 2025-07-23 | 22 | Animal | Transformer fuse | Forced | None
OE-25-003170 | 1030 | 10 | 103 | CR-S07-03 | Crossroads | 2025-07-23 | 23 | Vegetation | Transformer fuse | Forced | None
OE-25-003171 | 2145 | 13 | 165 | CR-S13-04 | Crossroads | 2025-07-24 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-003172 | 312 | 8 | 39 | CR-S18-02 | Crossroads | 2025-07-24 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003173 | 1568 | 7 | 224 | BY-S13-05 | Bayou | 2025-07-24 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003174 | 110955 | 569 | 195 | CR-S17-03 | Crossroads | 2025-07-24 | 8 | Unknown | Lateral fuse | Forced | None
OE-25-003175 | 7182 | 42 | 171 | HB-S16-04 | Harbor | 2025-07-24 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003176 | 4785 | 55 | 87 | BY-S30-03 | Bayou | 2025-07-24 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-003177 | 1400 | 8 | 175 | CR-S22-03 | Crossroads | 2025-07-24 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003178 | 1326 | 6 | 221 | PR-S19-03 | Prairie | 2025-07-24 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003179 | 26080 | 326 | 80 | BY-S26-02 | Bayou | 2025-07-24 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-003180 | 2310 | 14 | 165 | CR-S21-03 | Crossroads | 2025-07-24 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-003181 | 3655 | 43 | 85 | BY-S25-04 | Bayou | 2025-07-24 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003182 | 1414 | 14 | 101 | BY-S21-03 | Bayou | 2025-07-24 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-003183 | 1768 | 13 | 136 | HB-S17-02 | Harbor | 2025-07-25 | 4 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003184 | 1947 | 11 | 177 | BY-S12-02 | Bayou | 2025-07-25 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-25-003185 | 424 | 4 | 106 | CR-S04-05 | Crossroads | 2025-07-25 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003186 | 6848 | 64 | 107 | PR-S18-01 | Prairie | 2025-07-25 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003187 | 25277 | 1099 | 23 | BY-S26-02 | Bayou | 2025-07-25 | 12 | Vehicle or public | Feeder recloser | Forced | None
OE-25-003188 | 2691 | 13 | 207 | BY-S13-06 | Bayou | 2025-07-25 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-003189 | 14100 | 705 | 20 | HB-S09-05 | Harbor | 2025-07-25 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-25-003190 | 720 | 8 | 90 | BY-S17-03 | Bayou | 2025-07-25 | 14 | Animal | Transformer fuse | Forced | None
OE-25-003191 | 5680 | 71 | 80 | CR-S13-02 | Crossroads | 2025-07-25 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-003192 | 640 | 8 | 80 | CR-S21-03 | Crossroads | 2025-07-25 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-003193 | 774 | 3 | 258 | BY-S27-02 | Bayou | 2025-07-25 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003194 | 5341 | 49 | 109 | BY-S18-02 | Bayou | 2025-07-25 | 20 | Unknown | Lateral fuse | Forced | None
OE-25-003195 | 1840 | 10 | 184 | CR-S07-07 | Crossroads | 2025-07-25 | 20 | Animal | Transformer fuse | Forced | None
OE-25-003196 | 4864 | 32 | 152 | PR-S13-04 | Prairie | 2025-07-25 | 20 | Unknown | Lateral fuse | Forced | None
OE-25-003197 | 4966 | 13 | 382 | BY-S21-03 | Bayou | 2025-07-25 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003198 | 53912 | 586 | 92 | BY-S06-01 | Bayou | 2025-07-25 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-003199 | 2214 | 54 | 41 | CR-S06-02 | Crossroads | 2025-07-25 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003200 | 895 | 5 | 179 | BY-S05-01 | Bayou | 2025-07-26 | 1 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003201 | 38308 | 314 | 122 | PR-S12-03 | Prairie | 2025-07-26 | 2 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003202 | 10792 | 152 | 71 | CR-S09-05 | Crossroads | 2025-07-26 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003203 | 540 | 10 | 54 | CR-S21-03 | Crossroads | 2025-07-26 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003204 | 1920 | 12 | 160 | BY-S06-01 | Bayou | 2025-07-26 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003205 | 208468 | 4009 | 52 | CR-S21-03 | Crossroads | 2025-07-26 | 8 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-003206 | 60786 | 614 | 99 | PR-S07-03 | Prairie | 2025-07-26 | 8 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003207 | 298 | 2 | 149 | HB-S05-03 | Harbor | 2025-07-26 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-003208 | 1452 | 33 | 44 | CR-S21-01 | Crossroads | 2025-07-26 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003209 | 2457 | 13 | 189 | PR-S01-01 | Prairie | 2025-07-26 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003210 | 710 | 10 | 71 | BY-S21-04 | Bayou | 2025-07-26 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-003211 | 1924 | 13 | 148 | PR-S03-02 | Prairie | 2025-07-26 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003212 | 10176 | 48 | 212 | BY-S18-03 | Bayou | 2025-07-26 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003213 | 4752 | 27 | 176 | HB-S20-03 | Harbor | 2025-07-26 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003214 | 222 | 2 | 111 | BY-S10-03 | Bayou | 2025-07-26 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-003215 | 79862 | 547 | 146 | CR-S13-06 | Crossroads | 2025-07-26 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003216 | 11536 | 103 | 112 | BY-S23-02 | Bayou | 2025-07-26 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-003217 | 3990 | 42 | 95 | HB-S19-02 | Harbor | 2025-07-26 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-003218 | 1680 | 5 | 336 | PR-S13-03 | Prairie | 2025-07-26 | 18 | Animal | Transformer fuse | Forced | None
OE-25-003219 | 38232 | 354 | 108 | BY-S10-05 | Bayou | 2025-07-26 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-003220 | 1464 | 12 | 122 | PR-S05-03 | Prairie | 2025-07-26 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003221 | 324 | 4 | 81 | BY-S03-03 | Bayou | 2025-07-26 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-003222 | 8008 | 91 | 88 | PR-S11-02 | Prairie | 2025-07-27 | 6 | Weather - wind | Lateral fuse | Forced | None
OE-25-003223 | 37944 | 153 | 248 | BY-S07-05 | Bayou | 2025-07-27 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-25-003224 | 861 | 7 | 123 | CR-S06-03 | Crossroads | 2025-07-27 | 7 | Unknown | Transformer fuse | Forced | None
OE-25-003225 | 1638 | 14 | 117 | PR-S13-06 | Prairie | 2025-07-27 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003226 | 2790 | 31 | 90 | BY-S12-02 | Bayou | 2025-07-27 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003227 | 10682 | 49 | 218 | CR-S28-02 | Crossroads | 2025-07-27 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003228 | 2184 | 42 | 52 | HB-S05-01 | Harbor | 2025-07-27 | 13 | Unknown | Lateral fuse | Forced | None
OE-25-003229 | 4425 | 25 | 177 | PR-S03-05 | Prairie | 2025-07-27 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003230 | 25632 | 48 | 534 | BY-S27-01 | Bayou | 2025-07-27 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003231 | 2112 | 12 | 176 | BY-S29-01 | Bayou | 2025-07-27 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-003232 | 8679 | 263 | 33 | BY-S02-02 | Bayou | 2025-07-27 | 15 | Weather - wind | Feeder recloser | Forced | None
OE-25-003233 | 200 | 1 | 200 | HB-S19-04 | Harbor | 2025-07-27 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003234 | 299 | 1 | 299 | PR-S04-03 | Prairie | 2025-07-27 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-003235 | 137 | 1 | 137 | CR-S25-06 | Crossroads | 2025-07-27 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003236 | 1710 | 10 | 171 | HB-S02-01 | Harbor | 2025-07-27 | 19 | Animal | Transformer fuse | Forced | None
OE-25-003237 | 17372 | 172 | 101 | BY-S13-04 | Bayou | 2025-07-27 | 22 | Weather - wind | Lateral fuse | Forced | None
OE-25-003238 | 29632 | 64 | 463 | BY-S27-06 | Bayou | 2025-07-28 | 5 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003239 | 12495 | 85 | 147 | CR-S28-01 | Crossroads | 2025-07-28 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003240 | 80230 | 226 | 355 | HB-S18-02 | Harbor | 2025-07-28 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003241 | 45570 | 735 | 62 | BY-S20-01 | Bayou | 2025-07-28 | 8 | Weather - wind | Feeder recloser | Forced | None
OE-25-003242 | 103 | 1 | 103 | CR-S06-01 | Crossroads | 2025-07-28 | 8 | Unknown | Transformer fuse | Forced | None
OE-25-003243 | 1834 | 14 | 131 | BY-S17-01 | Bayou | 2025-07-28 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003244 | 2450 | 25 | 98 | CR-S25-06 | Crossroads | 2025-07-28 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003245 | 5070 | 13 | 390 | BY-S19-02 | Bayou | 2025-07-28 | 11 | Animal | Transformer fuse | Forced | None
OE-25-003246 | 16236 | 66 | 246 | BY-S15-02 | Bayou | 2025-07-28 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-25-003247 | 990 | 6 | 165 | HB-S11-01 | Harbor | 2025-07-28 | 13 | Animal | Transformer fuse | Forced | None
OE-25-003248 | 1694 | 14 | 121 | HB-S18-01 | Harbor | 2025-07-28 | 14 | Animal | Transformer fuse | Forced | None
OE-25-003249 | 2044 | 14 | 146 | PR-S13-01 | Prairie | 2025-07-28 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003250 | 948 | 4 | 237 | BY-S17-02 | Bayou | 2025-07-28 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-003251 | 19291 | 101 | 191 | BY-S15-05 | Bayou | 2025-07-29 | 2 | Vegetation | Lateral fuse | Forced | None
OE-25-003252 | 1612 | 13 | 124 | BY-S23-03 | Bayou | 2025-07-29 | 2 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003253 | 34038 | 366 | 93 | PR-S06-01 | Prairie | 2025-07-29 | 6 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-003254 | 8056 | 53 | 152 | BY-S02-01 | Bayou | 2025-07-29 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003255 | 904 | 8 | 113 | HB-S07-02 | Harbor | 2025-07-29 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-003256 | 9222 | 58 | 159 | HB-S07-02 | Harbor | 2025-07-29 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003257 | 5159 | 67 | 77 | PR-S18-01 | Prairie | 2025-07-29 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003258 | 17205 | 185 | 93 | BY-S27-04 | Bayou | 2025-07-29 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003259 | 141 | 1 | 141 | HB-S02-02 | Harbor | 2025-07-29 | 13 | Animal | Transformer fuse | Forced | None
OE-25-003260 | 9345 | 105 | 89 | CR-S32-01 | Crossroads | 2025-07-29 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003261 | 9765 | 279 | 35 | BY-S03-01 | Bayou | 2025-07-29 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003262 | 9612 | 178 | 54 | PR-S17-01 | Prairie | 2025-07-29 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-003263 | 7128 | 36 | 198 | BY-S28-01 | Bayou | 2025-07-29 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003264 | 12696 | 24 | 529 | PR-S15-01 | Prairie | 2025-07-29 | 20 | Animal | Lateral fuse | Forced | None
OE-25-003265 | 1464 | 4 | 366 | BY-S05-01 | Bayou | 2025-07-29 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003266 | 3731 | 41 | 91 | PR-S12-01 | Prairie | 2025-07-29 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-003267 | 384 | 8 | 48 | CR-S22-01 | Crossroads | 2025-07-30 | 3 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003268 | 855 | 19 | 45 | BY-S24-05 | Bayou | 2025-07-30 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-003269 | 702 | 9 | 78 | PR-S14-01 | Prairie | 2025-07-30 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-003270 | 2163 | 21 | 103 | BY-S14-02 | Bayou | 2025-07-30 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003271 | 19068 | 681 | 28 | BY-S25-04 | Bayou | 2025-07-30 | 10 | Vegetation | Feeder recloser | Forced | None
OE-25-003272 | 582 | 6 | 97 | HB-S01-03 | Harbor | 2025-07-30 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-25-003273 | 486 | 3 | 162 | BY-S15-01 | Bayou | 2025-07-30 | 14 | Animal | Transformer fuse | Forced | None
OE-25-003274 | 30096 | 176 | 171 | BY-S20-01 | Bayou | 2025-07-30 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003275 | 636 | 6 | 106 | PR-S19-03 | Prairie | 2025-07-30 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003276 | 126720 | 880 | 144 | BY-S13-05 | Bayou | 2025-07-30 | 15 | Animal | Feeder recloser | Forced | None
OE-25-003277 | 2881 | 67 | 43 | CR-S22-01 | Crossroads | 2025-07-30 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003278 | 3477 | 57 | 61 | HB-S05-06 | Harbor | 2025-07-30 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003279 | 1062 | 6 | 177 | BY-S23-05 | Bayou | 2025-07-30 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-003280 | 3159 | 13 | 243 | PR-S19-03 | Prairie | 2025-07-30 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003281 | 413 | 7 | 59 | CR-S28-01 | Crossroads | 2025-07-30 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003282 | 1005 | 5 | 201 | CR-S23-01 | Crossroads | 2025-07-30 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-003283 | 8436 | 74 | 114 | PR-S14-04 | Prairie | 2025-07-31 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003284 | 45468 | 1684 | 27 | PR-S14-03 | Prairie | 2025-07-31 | 1 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-003285 | 720 | 12 | 60 | BY-S10-03 | Bayou | 2025-07-31 | 4 | Vegetation | Transformer fuse | Forced | None
OE-25-003286 | 2091 | 51 | 41 | HB-S07-04 | Harbor | 2025-07-31 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003287 | 4056 | 39 | 104 | HB-S05-05 | Harbor | 2025-07-31 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003288 | 13620 | 60 | 227 | BY-S09-04 | Bayou | 2025-07-31 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003289 | 285 | 5 | 57 | CR-S10-03 | Crossroads | 2025-07-31 | 13 | Unknown | Transformer fuse | Forced | None
OE-25-003290 | 388 | 2 | 194 | CR-S14-05 | Crossroads | 2025-07-31 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003291 | 1260 | 6 | 210 | BY-S10-01 | Bayou | 2025-07-31 | 15 | Animal | Transformer fuse | Forced | None
OE-25-003292 | 2268 | 14 | 162 | HB-S17-02 | Harbor | 2025-07-31 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-003293 | 35235 | 261 | 135 | PR-S14-04 | Prairie | 2025-07-31 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003294 | 31196 | 709 | 44 | BY-S27-06 | Bayou | 2025-07-31 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-003295 | 32188 | 52 | 619 | PR-S18-02 | Prairie | 2025-07-31 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003296 | 2016 | 18 | 112 | CR-S01-01 | Crossroads | 2025-07-31 | 18 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003297 | 1344 | 14 | 96 | CR-S01-01 | Crossroads | 2025-07-31 | 18 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003298 | 1400 | 20 | 70 | PR-S20-01 | Prairie | 2025-07-31 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003299 | 33264 | 308 | 108 | HB-S07-04 | Harbor | 2025-07-31 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003300 | 11174 | 302 | 37 | CR-S09-02 | Crossroads | 2025-08-01 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003301 | 936 | 8 | 117 | PR-S04-01 | Prairie | 2025-08-01 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003302 | 1072 | 8 | 134 | PR-S15-06 | Prairie | 2025-08-01 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003303 | 11041 | 61 | 181 | BY-S21-02 | Bayou | 2025-08-01 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-003304 | 1270 | 10 | 127 | CR-S08-02 | Crossroads | 2025-08-01 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003305 | 162 | 3 | 54 | CR-S19-01 | Crossroads | 2025-08-01 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003306 | 7140 | 68 | 105 | BY-S09-04 | Bayou | 2025-08-01 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003307 | 6593 | 19 | 347 | CR-S21-03 | Crossroads | 2025-08-01 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003308 | 16485 | 157 | 105 | HB-S12-02 | Harbor | 2025-08-01 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003309 | 6666 | 66 | 101 | HB-S17-02 | Harbor | 2025-08-01 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003310 | 9702 | 63 | 154 | BY-S01-01 | Bayou | 2025-08-01 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003311 | 14858 | 23 | 646 | PR-S17-02 | Prairie | 2025-08-01 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003312 | 3588 | 52 | 69 | BY-S18-07 | Bayou | 2025-08-01 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003313 | 1292 | 4 | 323 | CR-S09-05 | Crossroads | 2025-08-02 | 7 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003314 | 14467 | 391 | 37 | PR-S04-03 | Prairie | 2025-08-02 | 7 | Equipment - overhead | Substation breaker | Forced | None
OE-25-003315 | 1683 | 33 | 51 | CR-S06-03 | Crossroads | 2025-08-02 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003316 | 2165 | 5 | 433 | PR-S06-01 | Prairie | 2025-08-02 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-003317 | 11300 | 100 | 113 | PR-S01-05 | Prairie | 2025-08-02 | 9 | Animal | Lateral fuse | Forced | None
OE-25-003318 | 2574 | 26 | 99 | PR-S11-01 | Prairie | 2025-08-02 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003319 | 4991 | 31 | 161 | CR-S25-03 | Crossroads | 2025-08-02 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003320 | 3288 | 12 | 274 | PR-S18-01 | Prairie | 2025-08-02 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-003321 | 238625 | 2075 | 115 | HB-S18-03 | Harbor | 2025-08-02 | 17 | Equipment - overhead | Substation breaker | Forced | None
OE-25-003322 | 5773 | 23 | 251 | BY-S20-02 | Bayou | 2025-08-02 | 18 | Animal | Lateral fuse | Forced | None
OE-25-003323 | 497 | 7 | 71 | PR-S08-01 | Prairie | 2025-08-02 | 18 | Animal | Transformer fuse | Forced | None
OE-25-003324 | 3094 | 34 | 91 | BY-S14-02 | Bayou | 2025-08-02 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003325 | 68356 | 743 | 92 | HB-S08-04 | Harbor | 2025-08-02 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-003326 | 8190 | 63 | 130 | PR-S20-04 | Prairie | 2025-08-02 | 23 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-003327 | 3016 | 26 | 116 | BY-S24-01 | Bayou | 2025-08-03 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003328 | 1107 | 9 | 123 | BY-S21-05 | Bayou | 2025-08-03 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003329 | 259965 | 1635 | 159 | HB-S20-01 | Harbor | 2025-08-03 | 7 | Weather - lightning | Substation breaker | Forced | None
OE-25-003330 | 1170 | 6 | 195 | HB-S11-01 | Harbor | 2025-08-03 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-25-003331 | 4012 | 118 | 34 | BY-S18-07 | Bayou | 2025-08-03 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-003332 | 328 | 2 | 164 | CR-S14-03 | Crossroads | 2025-08-03 | 9 | Animal | Transformer fuse | Forced | None
OE-25-003333 | 1925 | 7 | 275 | BY-S16-01 | Bayou | 2025-08-03 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003334 | 1305 | 9 | 145 | CR-S26-03 | Crossroads | 2025-08-03 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003335 | 2268 | 21 | 108 | BY-S24-04 | Bayou | 2025-08-03 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003336 | 6132 | 84 | 73 | CR-S22-03 | Crossroads | 2025-08-03 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003337 | 98280 | 819 | 120 | HB-S04-01 | Harbor | 2025-08-03 | 14 | Animal | Feeder recloser | Forced | None
OE-25-003338 | 188 | 2 | 94 | CR-S08-01 | Crossroads | 2025-08-03 | 15 | Animal | Transformer fuse | Forced | None
OE-25-003339 | 294 | 7 | 42 | CR-S02-01 | Crossroads | 2025-08-03 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003340 | 2871 | 29 | 99 | PR-S20-03 | Prairie | 2025-08-03 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003341 | 1232 | 7 | 176 | CR-S07-05 | Crossroads | 2025-08-04 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003342 | 46360 | 488 | 95 | HB-S16-03 | Harbor | 2025-08-04 | 0 | Animal | Feeder recloser | Forced | None
OE-25-003343 | 1203 | 3 | 401 | PR-S18-03 | Prairie | 2025-08-04 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-25-003344 | 8905 | 65 | 137 | BY-S07-01 | Bayou | 2025-08-04 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003345 | 1716 | 12 | 143 | BY-S21-05 | Bayou | 2025-08-04 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003346 | 6162 | 13 | 474 | BY-S07-02 | Bayou | 2025-08-04 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003347 | 196 | 2 | 98 | BY-S23-01 | Bayou | 2025-08-04 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003348 | 690 | 5 | 138 | PR-S14-02 | Prairie | 2025-08-04 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003349 | 17296 | 94 | 184 | BY-S13-02 | Bayou | 2025-08-04 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003350 | 726 | 6 | 121 | CR-S24-03 | Crossroads | 2025-08-04 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003351 | 22630 | 155 | 146 | CR-S22-03 | Crossroads | 2025-08-04 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003352 | 17145 | 135 | 127 | CR-S23-04 | Crossroads | 2025-08-04 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003353 | 11096 | 76 | 146 | BY-S21-04 | Bayou | 2025-08-04 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-003354 | 7597 | 71 | 107 | CR-S07-03 | Crossroads | 2025-08-04 | 14 | Animal | Lateral fuse | Forced | None
OE-25-003355 | 6419 | 49 | 131 | CR-S21-01 | Crossroads | 2025-08-04 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003356 | 3993 | 11 | 363 | BY-S30-01 | Bayou | 2025-08-04 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003357 | 11160 | 62 | 180 | PR-S18-01 | Prairie | 2025-08-04 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003358 | 238 | 7 | 34 | BY-S17-03 | Bayou | 2025-08-04 | 17 | Animal | Lateral fuse | Forced | None
OE-25-003359 | 2034 | 9 | 226 | BY-S13-03 | Bayou | 2025-08-04 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-003360 | 1079 | 13 | 83 | PR-S13-06 | Prairie | 2025-08-04 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003361 | 19030 | 173 | 110 | HB-S17-01 | Harbor | 2025-08-04 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003362 | 3440 | 43 | 80 | HB-S04-01 | Harbor | 2025-08-05 | 2 | Animal | Lateral fuse | Forced | None
OE-25-003363 | 1014 | 6 | 169 | HB-S12-03 | Harbor | 2025-08-05 | 6 | Animal | Transformer fuse | Forced | None
OE-25-003364 | 114770 | 2495 | 46 | BY-S13-06 | Bayou | 2025-08-05 | 7 | Weather - wind | Substation breaker | Forced | None
OE-25-003365 | 225582 | 1722 | 131 | CR-S19-03 | Crossroads | 2025-08-05 | 7 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003366 | 1463 | 11 | 133 | BY-S18-03 | Bayou | 2025-08-05 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003367 | 52350 | 698 | 75 | BY-S29-02 | Bayou | 2025-08-05 | 10 | Weather - lightning | Feeder recloser | Forced | None
OE-25-003368 | 404 | 2 | 202 | CR-S25-04 | Crossroads | 2025-08-05 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003369 | 2937 | 11 | 267 | CR-S04-05 | Crossroads | 2025-08-05 | 11 | Animal | Transformer fuse | Forced | None
OE-25-003370 | 16104 | 183 | 88 | BY-S12-02 | Bayou | 2025-08-05 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003371 | 952 | 14 | 68 | BY-S12-03 | Bayou | 2025-08-05 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-25-003372 | 760 | 5 | 152 | BY-S21-01 | Bayou | 2025-08-05 | 12 | Animal | Transformer fuse | Forced | None
OE-25-003373 | 980 | 10 | 98 | CR-S30-07 | Crossroads | 2025-08-05 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-003374 | 13860 | 132 | 105 | HB-S01-05 | Harbor | 2025-08-05 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003375 | 133848 | 572 | 234 | PR-S01-06 | Prairie | 2025-08-05 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003376 | 2485 | 7 | 355 | PR-S06-03 | Prairie | 2025-08-05 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003377 | 1560 | 13 | 120 | PR-S17-02 | Prairie | 2025-08-05 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003378 | 704 | 11 | 64 | HB-S07-05 | Harbor | 2025-08-05 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003379 | 12210 | 111 | 110 | BY-S04-02 | Bayou | 2025-08-06 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003380 | 46431 | 67 | 693 | BY-S08-03 | Bayou | 2025-08-06 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003381 | 693 | 7 | 99 | BY-S08-01 | Bayou | 2025-08-06 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003382 | 7728 | 46 | 168 | CR-S26-06 | Crossroads | 2025-08-06 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003383 | 40464 | 562 | 72 | BY-S29-03 | Bayou | 2025-08-06 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-003384 | 6364 | 74 | 86 | BY-S06-01 | Bayou | 2025-08-06 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-003385 | 1210 | 11 | 110 | PR-S07-06 | Prairie | 2025-08-06 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003386 | 1540 | 11 | 140 | BY-S10-03 | Bayou | 2025-08-06 | 15 | Animal | Transformer fuse | Forced | None
OE-25-003387 | 1560 | 13 | 120 | CR-S24-02 | Crossroads | 2025-08-06 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003388 | 294 | 6 | 49 | CR-S15-02 | Crossroads | 2025-08-06 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003389 | 88896 | 926 | 96 | CR-S12-01 | Crossroads | 2025-08-06 | 21 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003390 | 1128 | 12 | 94 | CR-S29-01 | Crossroads | 2025-08-06 | 21 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003391 | 900 | 10 | 90 | PR-S07-04 | Prairie | 2025-08-07 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-003392 | 2146 | 29 | 74 | HB-S04-01 | Harbor | 2025-08-07 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003393 | 12935 | 199 | 65 | HB-S06-05 | Harbor | 2025-08-07 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003394 | 26000 | 260 | 100 | HB-S15-03 | Harbor | 2025-08-07 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003395 | 244280 | 1970 | 124 | CR-S04-03 | Crossroads | 2025-08-07 | 9 | Unknown | Substation breaker | Forced | None
OE-25-003396 | 912 | 2 | 456 | HB-S16-04 | Harbor | 2025-08-07 | 9 | Unknown | Transformer fuse | Forced | None
OE-25-003397 | 26892 | 332 | 81 | CR-S04-05 | Crossroads | 2025-08-07 | 10 | Vegetation | Feeder recloser | Forced | None
OE-25-003398 | 7843 | 31 | 253 | CR-S23-04 | Crossroads | 2025-08-07 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003399 | 10455 | 41 | 255 | CR-S30-07 | Crossroads | 2025-08-07 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003400 | 7056 | 48 | 147 | BY-S27-02 | Bayou | 2025-08-07 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003401 | 2123 | 11 | 193 | PR-S17-01 | Prairie | 2025-08-07 | 12 | Animal | Transformer fuse | Forced | None
OE-25-003402 | 4340 | 35 | 124 | BY-S24-04 | Bayou | 2025-08-07 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003403 | 294 | 3 | 98 | CR-S02-02 | Crossroads | 2025-08-07 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003404 | 18676 | 58 | 322 | BY-S11-03 | Bayou | 2025-08-07 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003405 | 18291 | 273 | 67 | BY-S30-02 | Bayou | 2025-08-07 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003406 | 30602 | 214 | 143 | CR-S05-04 | Crossroads | 2025-08-07 | 15 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-003407 | 13311 | 493 | 27 | BY-S29-05 | Bayou | 2025-08-07 | 16 | Animal | Feeder recloser | Forced | None
OE-25-003408 | 5712 | 42 | 136 | CR-S09-01 | Crossroads | 2025-08-07 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-003409 | 5084 | 41 | 124 | HB-S01-01 | Harbor | 2025-08-07 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-003410 | 183792 | 1094 | 168 | BY-S24-04 | Bayou | 2025-08-07 | 21 | Animal | Substation breaker | Forced | None
OE-25-003411 | 1140 | 5 | 228 | CR-S18-05 | Crossroads | 2025-08-07 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003412 | 693 | 9 | 77 | BY-S15-02 | Bayou | 2025-08-08 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003413 | 3627 | 13 | 279 | BY-S18-04 | Bayou | 2025-08-08 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003414 | 1264 | 16 | 79 | HB-S09-04 | Harbor | 2025-08-08 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003415 | 665 | 5 | 133 | HB-S10-01 | Harbor | 2025-08-08 | 11 | Animal | Transformer fuse | Forced | None
OE-25-003416 | 155 | 1 | 155 | BY-S15-01 | Bayou | 2025-08-08 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003417 | 8024 | 136 | 59 | CR-S09-01 | Crossroads | 2025-08-08 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003418 | 74130 | 210 | 353 | BY-S27-03 | Bayou | 2025-08-08 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003419 | 7860 | 60 | 131 | CR-S31-03 | Crossroads | 2025-08-08 | 14 | Animal | Lateral fuse | Forced | None
OE-25-003420 | 315 | 3 | 105 | CR-S09-04 | Crossroads | 2025-08-08 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003421 | 1038 | 6 | 173 | CR-S12-01 | Crossroads | 2025-08-08 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003422 | 1232 | 14 | 88 | BY-S06-02 | Bayou | 2025-08-08 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003423 | 1080 | 10 | 108 | CR-S27-02 | Crossroads | 2025-08-08 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003424 | 8832 | 184 | 48 | PR-S03-03 | Prairie | 2025-08-08 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003425 | 55338 | 802 | 69 | BY-S06-01 | Bayou | 2025-08-08 | 20 | Vegetation | Feeder recloser | Forced | None
OE-25-003426 | 550 | 11 | 50 | CR-S05-05 | Crossroads | 2025-08-09 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003427 | 3838 | 38 | 101 | CR-S12-01 | Crossroads | 2025-08-09 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003428 | 24108 | 588 | 41 | BY-S07-01 | Bayou | 2025-08-09 | 8 | Vegetation | Feeder recloser | Forced | None
OE-25-003429 | 16132 | 218 | 74 | CR-S26-02 | Crossroads | 2025-08-09 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003430 | 960 | 12 | 80 | PR-S13-03 | Prairie | 2025-08-09 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003431 | 20838 | 302 | 69 | PR-S06-02 | Prairie | 2025-08-09 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003432 | 14924 | 82 | 182 | BY-S16-01 | Bayou | 2025-08-09 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003433 | 161406 | 1281 | 126 | PR-S16-05 | Prairie | 2025-08-09 | 11 | Vehicle or public | Substation breaker | Forced | None
OE-25-003434 | 7008 | 96 | 73 | CR-S18-05 | Crossroads | 2025-08-09 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003435 | 1140 | 12 | 95 | CR-S07-01 | Crossroads | 2025-08-09 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003436 | 4158 | 22 | 189 | BY-S13-05 | Bayou | 2025-08-09 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003437 | 4352 | 64 | 68 | CR-S20-05 | Crossroads | 2025-08-09 | 17 | Animal | Lateral fuse | Forced | None
OE-25-003438 | 58188 | 746 | 78 | CR-S30-03 | Crossroads | 2025-08-09 | 17 | Unknown | Feeder recloser | Forced | None
OE-25-003439 | 47841 | 1293 | 37 | HB-S20-02 | Harbor | 2025-08-09 | 17 | Weather - wind | Substation breaker | Forced | None
OE-25-003440 | 12220 | 94 | 130 | BY-S10-02 | Bayou | 2025-08-09 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-003441 | 11661 | 169 | 69 | PR-S05-03 | Prairie | 2025-08-09 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-003442 | 62836 | 1366 | 46 | PR-S13-01 | Prairie | 2025-08-09 | 19 | Weather - lightning | Feeder recloser | Forced | None
OE-25-003443 | 8432 | 68 | 124 | PR-S13-06 | Prairie | 2025-08-09 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003444 | 57722 | 589 | 98 | PR-S14-03 | Prairie | 2025-08-09 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-003445 | 890 | 5 | 178 | BY-S11-03 | Bayou | 2025-08-10 | 6 | Weather - wind | Transformer fuse | Forced | None
OE-25-003446 | 1421 | 29 | 49 | CR-S21-02 | Crossroads | 2025-08-10 | 8 | Animal | Lateral fuse | Forced | None
OE-25-003447 | 52 | 1 | 52 | CR-S11-01 | Crossroads | 2025-08-10 | 9 | Animal | Transformer fuse | Forced | None
OE-25-003448 | 1584 | 9 | 176 | PR-S03-01 | Prairie | 2025-08-10 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003449 | 29904 | 112 | 267 | BY-S03-02 | Bayou | 2025-08-10 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003450 | 13604 | 76 | 179 | BY-S24-02 | Bayou | 2025-08-10 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003451 | 1944 | 6 | 324 | PR-S09-02 | Prairie | 2025-08-10 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003452 | 3760 | 10 | 376 | BY-S10-05 | Bayou | 2025-08-10 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003453 | 466 | 2 | 233 | PR-S06-03 | Prairie | 2025-08-10 | 14 | Animal | Transformer fuse | Forced | None
OE-25-003454 | 2070 | 45 | 46 | PR-S18-03 | Prairie | 2025-08-10 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003455 | 1085 | 7 | 155 | CR-S09-01 | Crossroads | 2025-08-10 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-25-003456 | 2210 | 13 | 170 | CR-S12-01 | Crossroads | 2025-08-10 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003457 | 16560 | 144 | 115 | PR-S20-04 | Prairie | 2025-08-10 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-003458 | 20698 | 79 | 262 | CR-S12-01 | Crossroads | 2025-08-10 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003459 | 3768 | 12 | 314 | PR-S13-03 | Prairie | 2025-08-10 | 23 | Weather - wind | Transformer fuse | Forced | None
OE-25-003460 | 9075 | 75 | 121 | CR-S31-03 | Crossroads | 2025-08-11 | 2 | Animal | Lateral fuse | Forced | None
OE-25-003461 | 16632 | 198 | 84 | HB-S01-02 | Harbor | 2025-08-11 | 7 | Vegetation | Feeder recloser | Forced | None
OE-25-003462 | 9348 | 114 | 82 | PR-S05-02 | Prairie | 2025-08-11 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-003463 | 1032 | 8 | 129 | HB-S12-02 | Harbor | 2025-08-11 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-25-003464 | 612 | 6 | 102 | CR-S20-02 | Crossroads | 2025-08-11 | 11 | Animal | Transformer fuse | Forced | None
OE-25-003465 | 3146 | 13 | 242 | PR-S07-02 | Prairie | 2025-08-11 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-25-003466 | 1730 | 10 | 173 | HB-S19-02 | Harbor | 2025-08-11 | 15 | Animal | Transformer fuse | Forced | None
OE-25-003467 | 3682 | 14 | 263 | PR-S08-01 | Prairie | 2025-08-11 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-003468 | 660 | 10 | 66 | BY-S17-01 | Bayou | 2025-08-11 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003469 | 13032 | 724 | 18 | CR-S17-03 | Crossroads | 2025-08-11 | 17 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003470 | 3429 | 27 | 127 | BY-S14-02 | Bayou | 2025-08-11 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003471 | 12054 | 82 | 147 | BY-S29-02 | Bayou | 2025-08-11 | 19 | Animal | Lateral fuse | Forced | None
OE-25-003472 | 560 | 4 | 140 | CR-S17-01 | Crossroads | 2025-08-11 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-003473 | 60143 | 439 | 137 | CR-S23-03 | Crossroads | 2025-08-11 | 19 | Animal | Feeder recloser | Forced | None
OE-25-003474 | 31073 | 193 | 161 | PR-S10-01 | Prairie | 2025-08-11 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003475 | 36190 | 470 | 77 | HB-S14-02 | Harbor | 2025-08-11 | 21 | Animal | Substation breaker | Forced | None
OE-25-003476 | 11832 | 68 | 174 | PR-S04-02 | Prairie | 2025-08-11 | 22 | Unknown | Lateral fuse | Forced | None
OE-25-003477 | 640 | 5 | 128 | PR-S14-03 | Prairie | 2025-08-11 | 22 | Animal | Transformer fuse | Forced | None
OE-25-003478 | 400 | 10 | 40 | CR-S01-04 | Crossroads | 2025-08-12 | 0 | Animal | Transformer fuse | Forced | None
OE-25-003479 | 6058 | 13 | 466 | BY-S27-03 | Bayou | 2025-08-12 | 5 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003480 | 22718 | 74 | 307 | PR-S12-01 | Prairie | 2025-08-12 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003481 | 92495 | 1423 | 65 | PR-S14-04 | Prairie | 2025-08-12 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003482 | 1970 | 10 | 197 | BY-S12-01 | Bayou | 2025-08-12 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003483 | 2223 | 39 | 57 | PR-S14-04 | Prairie | 2025-08-12 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-003484 | 84105 | 945 | 89 | CR-S04-01 | Crossroads | 2025-08-12 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003485 | 2020 | 5 | 404 | PR-S05-02 | Prairie | 2025-08-12 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003486 | 10396 | 46 | 226 | BY-S26-06 | Bayou | 2025-08-12 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003487 | 1048 | 8 | 131 | PR-S05-03 | Prairie | 2025-08-12 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003488 | 790 | 10 | 79 | HB-S07-02 | Harbor | 2025-08-12 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003489 | 124611 | 569 | 219 | HB-S18-02 | Harbor | 2025-08-12 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-003490 | 9027 | 51 | 177 | BY-S18-06 | Bayou | 2025-08-12 | 17 | Unknown | Lateral fuse | Forced | None
OE-25-003491 | 10336 | 68 | 152 | PR-S10-03 | Prairie | 2025-08-12 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003492 | 78 | 1 | 78 | CR-S03-01 | Crossroads | 2025-08-12 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003493 | 89979 | 1011 | 89 | BY-S25-05 | Bayou | 2025-08-13 | 4 | Equipment - overhead | Substation breaker | Forced | None
OE-25-003494 | 5911 | 23 | 257 | BY-S15-04 | Bayou | 2025-08-13 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003495 | 10147 | 73 | 139 | PR-S15-05 | Prairie | 2025-08-13 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-003496 | 11067 | 93 | 119 | BY-S26-06 | Bayou | 2025-08-13 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003497 | 3157 | 41 | 77 | BY-S26-03 | Bayou | 2025-08-13 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-003498 | 5175 | 45 | 115 | HB-S07-03 | Harbor | 2025-08-13 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003499 | 7128 | 81 | 88 | BY-S15-05 | Bayou | 2025-08-13 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003500 | 1635 | 5 | 327 | HB-S03-01 | Harbor | 2025-08-14 | 2 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003501 | 7161 | 77 | 93 | CR-S07-05 | Crossroads | 2025-08-14 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003502 | 276 | 4 | 69 | CR-S30-05 | Crossroads | 2025-08-14 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003503 | 1781 | 13 | 137 | BY-S26-06 | Bayou | 2025-08-14 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-003504 | 420 | 3 | 140 | PR-S13-06 | Prairie | 2025-08-14 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003505 | 11935 | 155 | 77 | BY-S11-02 | Bayou | 2025-08-14 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003506 | 3569 | 43 | 83 | PR-S18-06 | Prairie | 2025-08-14 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003507 | 714 | 7 | 102 | PR-S05-03 | Prairie | 2025-08-14 | 13 | Unknown | Transformer fuse | Forced | None
OE-25-003508 | 18910 | 122 | 155 | BY-S25-02 | Bayou | 2025-08-14 | 16 | Animal | Lateral fuse | Forced | None
OE-25-003509 | 34143 | 599 | 57 | HB-S15-02 | Harbor | 2025-08-14 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003510 | 394 | 2 | 197 | PR-S06-01 | Prairie | 2025-08-14 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003511 | 902 | 11 | 82 | PR-S06-01 | Prairie | 2025-08-14 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003512 | 544 | 4 | 136 | PR-S04-01 | Prairie | 2025-08-14 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003513 | 795 | 5 | 159 | PR-S13-01 | Prairie | 2025-08-15 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003514 | 440186 | 2269 | 194 | BY-S29-01 | Bayou | 2025-08-15 | 5 | Weather - lightning | Feeder recloser | Forced | None
OE-25-003515 | 594 | 6 | 99 | CR-S21-02 | Crossroads | 2025-08-15 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003516 | 891 | 9 | 99 | CR-S26-04 | Crossroads | 2025-08-15 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003517 | 6262 | 62 | 101 | CR-S04-05 | Crossroads | 2025-08-15 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003518 | 2460 | 12 | 205 | CR-S27-04 | Crossroads | 2025-08-15 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003519 | 20520 | 342 | 60 | PR-S13-03 | Prairie | 2025-08-15 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-003520 | 33567 | 201 | 167 | BY-S11-03 | Bayou | 2025-08-15 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003521 | 3630 | 10 | 363 | BY-S24-03 | Bayou | 2025-08-15 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-003522 | 24208 | 356 | 68 | CR-S04-05 | Crossroads | 2025-08-15 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003523 | 1070 | 10 | 107 | BY-S05-02 | Bayou | 2025-08-15 | 18 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003524 | 3484 | 67 | 52 | BY-S07-04 | Bayou | 2025-08-15 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003525 | 114725 | 1765 | 65 | PR-S08-02 | Prairie | 2025-08-15 | 18 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-003526 | 1113 | 7 | 159 | CR-S20-04 | Crossroads | 2025-08-15 | 20 | Animal | Transformer fuse | Forced | None
OE-25-003527 | 28672 | 256 | 112 | PR-S20-03 | Prairie | 2025-08-15 | 20 | Vegetation | Feeder recloser | Forced | None
OE-25-003528 | 43710 | 310 | 141 | CR-S02-03 | Crossroads | 2025-08-15 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-003529 | 102120 | 1380 | 74 | BY-S23-03 | Bayou | 2025-08-16 | 3 | Vegetation | Feeder recloser | Forced | None
OE-25-003530 | 6417 | 31 | 207 | CR-S16-05 | Crossroads | 2025-08-16 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003531 | 1326 | 13 | 102 | BY-S18-02 | Bayou | 2025-08-16 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003532 | 544 | 8 | 68 | HB-S12-01 | Harbor | 2025-08-16 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003533 | 27690 | 130 | 213 | HB-S10-02 | Harbor | 2025-08-16 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003534 | 1755 | 27 | 65 | HB-S19-04 | Harbor | 2025-08-16 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003535 | 1197 | 7 | 171 | PR-S13-05 | Prairie | 2025-08-16 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003536 | 950 | 10 | 95 | HB-S10-03 | Harbor | 2025-08-16 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003537 | 103 | 1 | 103 | PR-S01-04 | Prairie | 2025-08-16 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003538 | 28350 | 675 | 42 | CR-S20-03 | Crossroads | 2025-08-16 | 17 | Weather - wind | Feeder recloser | Forced | None
OE-25-003539 | 11562 | 82 | 141 | CR-S23-04 | Crossroads | 2025-08-16 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003540 | 1134 | 6 | 189 | HB-S10-02 | Harbor | 2025-08-16 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003541 | 4401 | 163 | 27 | PR-S18-01 | Prairie | 2025-08-16 | 19 | Weather - lightning | Feeder recloser | Forced | None
OE-25-003542 | 944 | 8 | 118 | BY-S11-02 | Bayou | 2025-08-16 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-003543 | 7192 | 62 | 116 | CR-S19-03 | Crossroads | 2025-08-16 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003544 | 7750 | 62 | 125 | CR-S20-02 | Crossroads | 2025-08-17 | 4 | Weather - wind | Lateral fuse | Forced | None
OE-25-003545 | 107984 | 1588 | 68 | CR-S23-05 | Crossroads | 2025-08-17 | 8 | Weather - lightning | Substation breaker | Forced | None
OE-25-003546 | 3332 | 49 | 68 | BY-S21-03 | Bayou | 2025-08-17 | 9 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003547 | 2055 | 5 | 411 | BY-S14-03 | Bayou | 2025-08-17 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003548 | 1881 | 9 | 209 | HB-S14-02 | Harbor | 2025-08-17 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003549 | 1413 | 9 | 157 | PR-S16-03 | Prairie | 2025-08-17 | 13 | Animal | Transformer fuse | Forced | None
OE-25-003550 | 840 | 8 | 105 | BY-S20-02 | Bayou | 2025-08-17 | 14 | Animal | Transformer fuse | Forced | None
OE-25-003551 | 11880 | 216 | 55 | CR-S06-01 | Crossroads | 2025-08-17 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003552 | 8532 | 54 | 158 | CR-S30-07 | Crossroads | 2025-08-17 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003553 | 12480 | 48 | 260 | BY-S29-04 | Bayou | 2025-08-17 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003554 | 143298 | 1257 | 114 | CR-S16-03 | Crossroads | 2025-08-17 | 16 | Vegetation | Substation breaker | Forced | None
OE-25-003555 | 235 | 1 | 235 | PR-S07-01 | Prairie | 2025-08-17 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003556 | 972 | 12 | 81 | PR-S16-02 | Prairie | 2025-08-17 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003557 | 2044 | 14 | 146 | HB-S12-02 | Harbor | 2025-08-17 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003558 | 9660 | 84 | 115 | HB-S15-01 | Harbor | 2025-08-17 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003559 | 29700 | 270 | 110 | HB-S14-04 | Harbor | 2025-08-18 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003560 | 2926 | 14 | 209 | PR-S03-02 | Prairie | 2025-08-18 | 6 | Animal | Transformer fuse | Forced | None
OE-25-003561 | 32190 | 145 | 222 | PR-S01-02 | Prairie | 2025-08-18 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003562 | 1825 | 25 | 73 | BY-S15-03 | Bayou | 2025-08-18 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003563 | 2123 | 11 | 193 | CR-S07-06 | Crossroads | 2025-08-18 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-25-003564 | 526 | 2 | 263 | PR-S05-03 | Prairie | 2025-08-18 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003565 | 83842 | 2266 | 37 | CR-S17-01 | Crossroads | 2025-08-18 | 11 | Weather - wind | Feeder recloser | Forced | None
OE-25-003566 | 1593 | 27 | 59 | HB-S08-01 | Harbor | 2025-08-18 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-003567 | 6669 | 39 | 171 | PR-S12-02 | Prairie | 2025-08-18 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003568 | 14280 | 595 | 24 | PR-S15-06 | Prairie | 2025-08-18 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003569 | 3570 | 30 | 119 | CR-S26-02 | Crossroads | 2025-08-18 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003570 | 1870 | 11 | 170 | CR-S10-01 | Crossroads | 2025-08-18 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003571 | 220 | 2 | 110 | CR-S27-01 | Crossroads | 2025-08-18 | 15 | Animal | Transformer fuse | Forced | None
OE-25-003572 | 34472 | 62 | 556 | PR-S03-06 | Prairie | 2025-08-18 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003573 | 1782 | 18 | 99 | CR-S08-06 | Crossroads | 2025-08-18 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003574 | 1332 | 6 | 222 | PR-S09-04 | Prairie | 2025-08-19 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003575 | 5208 | 12 | 434 | PR-S10-03 | Prairie | 2025-08-19 | 8 | Animal | Transformer fuse | Forced | None
OE-25-003576 | 2100 | 14 | 150 | BY-S06-01 | Bayou | 2025-08-19 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003577 | 4375 | 35 | 125 | CR-S13-01 | Crossroads | 2025-08-19 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003578 | 5076 | 47 | 108 | HB-S15-02 | Harbor | 2025-08-19 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-003579 | 119424 | 2488 | 48 | BY-S17-02 | Bayou | 2025-08-19 | 11 | Unknown | Substation breaker | Outside cause | None
OE-25-003580 | 8925 | 119 | 75 | BY-S13-05 | Bayou | 2025-08-19 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003581 | 62976 | 492 | 128 | BY-S30-03 | Bayou | 2025-08-19 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-003582 | 4929 | 53 | 93 | CR-S16-04 | Crossroads | 2025-08-19 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003583 | 3930 | 30 | 131 | HB-S09-04 | Harbor | 2025-08-19 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003584 | 5655 | 39 | 145 | CR-S11-01 | Crossroads | 2025-08-19 | 14 | Animal | Lateral fuse | Forced | None
OE-25-003585 | 81627 | 507 | 161 | HB-S09-03 | Harbor | 2025-08-19 | 18 | Weather - wind | IGSD-isolated section | Forced | None
OE-25-003586 | 2160 | 20 | 108 | PR-S18-01 | Prairie | 2025-08-19 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-003587 | 20043 | 131 | 153 | PR-S09-04 | Prairie | 2025-08-19 | 20 | Animal | Lateral fuse | Forced | None
OE-25-003588 | 1270 | 10 | 127 | HB-S18-02 | Harbor | 2025-08-19 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-003589 | 2232 | 12 | 186 | PR-S07-06 | Prairie | 2025-08-20 | 1 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003590 | 23896 | 206 | 116 | HB-S19-03 | Harbor | 2025-08-20 | 4 | Unknown | Feeder recloser | Forced | None
OE-25-003591 | 34500 | 750 | 46 | HB-S08-03 | Harbor | 2025-08-20 | 7 | Weather - wind | Substation breaker | Forced | None
OE-25-003592 | 21000 | 200 | 105 | BY-S03-03 | Bayou | 2025-08-20 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003593 | 12150 | 81 | 150 | BY-S15-06 | Bayou | 2025-08-20 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-003594 | 8370 | 93 | 90 | CR-S07-05 | Crossroads | 2025-08-20 | 9 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003595 | 2412 | 36 | 67 | BY-S26-01 | Bayou | 2025-08-20 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003596 | 29161 | 241 | 121 | BY-S08-02 | Bayou | 2025-08-20 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003597 | 128698 | 562 | 229 | BY-S26-03 | Bayou | 2025-08-20 | 13 | Vegetation | Feeder recloser | Forced | None
OE-25-003598 | 21432 | 141 | 152 | HB-S20-01 | Harbor | 2025-08-20 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003599 | 15392 | 104 | 148 | HB-S20-05 | Harbor | 2025-08-20 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-003600 | 936 | 6 | 156 | CR-S09-01 | Crossroads | 2025-08-20 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003601 | 1160 | 8 | 145 | HB-S07-04 | Harbor | 2025-08-20 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-003602 | 3538 | 61 | 58 | CR-S22-03 | Crossroads | 2025-08-20 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003603 | 50864 | 578 | 88 | CR-S18-05 | Crossroads | 2025-08-20 | 19 | Unknown | Feeder recloser | Forced | None
OE-25-003604 | 966 | 14 | 69 | BY-S04-03 | Bayou | 2025-08-20 | 20 | Unknown | Transformer fuse | Forced | None
OE-25-003605 | 4094 | 46 | 89 | PR-S14-03 | Prairie | 2025-08-20 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003606 | 29733 | 159 | 187 | BY-S15-04 | Bayou | 2025-08-20 | 23 | Weather - wind | Lateral fuse | Forced | None
OE-25-003607 | 1395 | 31 | 45 | BY-S23-03 | Bayou | 2025-08-21 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-003608 | 1300 | 13 | 100 | CR-S05-05 | Crossroads | 2025-08-21 | 2 | Weather - wind | Transformer fuse | Forced | None
OE-25-003609 | 11374 | 94 | 121 | CR-S23-03 | Crossroads | 2025-08-21 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003610 | 1212 | 6 | 202 | BY-S20-03 | Bayou | 2025-08-21 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003611 | 14355 | 45 | 319 | BY-S27-03 | Bayou | 2025-08-21 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003612 | 6798 | 66 | 103 | CR-S04-01 | Crossroads | 2025-08-21 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003613 | 28028 | 77 | 364 | BY-S18-01 | Bayou | 2025-08-21 | 11 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003614 | 445 | 5 | 89 | BY-S22-03 | Bayou | 2025-08-21 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003615 | 3311 | 77 | 43 | HB-S06-04 | Harbor | 2025-08-21 | 11 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003616 | 3990 | 14 | 285 | HB-S15-02 | Harbor | 2025-08-21 | 11 | Animal | Transformer fuse | Forced | None
OE-25-003617 | 9150 | 50 | 183 | BY-S08-03 | Bayou | 2025-08-21 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003618 | 2898 | 14 | 207 | HB-S17-01 | Harbor | 2025-08-21 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-003619 | 51156 | 882 | 58 | CR-S22-01 | Crossroads | 2025-08-21 | 14 | Vehicle or public | Feeder recloser | Forced | None
OE-25-003620 | 22016 | 172 | 128 | HB-S02-01 | Harbor | 2025-08-21 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003621 | 63630 | 1515 | 42 | CR-S07-03 | Crossroads | 2025-08-21 | 16 | Vegetation | Feeder recloser | Forced | None
OE-25-003622 | 804 | 4 | 201 | HB-S11-01 | Harbor | 2025-08-21 | 16 | Animal | Transformer fuse | Forced | None
OE-25-003623 | 28832 | 212 | 136 | PR-S16-05 | Prairie | 2025-08-21 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003624 | 6270 | 66 | 95 | BY-S06-02 | Bayou | 2025-08-21 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003625 | 6860 | 98 | 70 | CR-S10-02 | Crossroads | 2025-08-21 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003626 | 13702 | 62 | 221 | HB-S19-02 | Harbor | 2025-08-21 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003627 | 7638 | 57 | 134 | BY-S15-01 | Bayou | 2025-08-22 | 0 | Animal | Lateral fuse | Forced | None
OE-25-003628 | 1820 | 7 | 260 | PR-S09-04 | Prairie | 2025-08-22 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003629 | 10912 | 62 | 176 | BY-S16-03 | Bayou | 2025-08-22 | 7 | Animal | Lateral fuse | Forced | None
OE-25-003630 | 6106 | 43 | 142 | BY-S23-04 | Bayou | 2025-08-22 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003631 | 188 | 2 | 94 | PR-S10-02 | Prairie | 2025-08-22 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-003632 | 417 | 3 | 139 | BY-S13-05 | Bayou | 2025-08-22 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-003633 | 5661 | 111 | 51 | BY-S28-01 | Bayou | 2025-08-22 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003634 | 20592 | 468 | 44 | HB-S09-03 | Harbor | 2025-08-22 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-003635 | 77 | 1 | 77 | HB-S14-01 | Harbor | 2025-08-22 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003636 | 936 | 8 | 117 | CR-S19-02 | Crossroads | 2025-08-22 | 14 | Animal | Transformer fuse | Forced | None
OE-25-003637 | 4255 | 23 | 185 | PR-S13-02 | Prairie | 2025-08-22 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003638 | 1416 | 12 | 118 | PR-S01-02 | Prairie | 2025-08-22 | 16 | Animal | Transformer fuse | Forced | None
OE-25-003639 | 1404 | 12 | 117 | PR-S13-01 | Prairie | 2025-08-22 | 16 | Animal | Transformer fuse | Forced | None
OE-25-003640 | 1330 | 19 | 70 | PR-S15-05 | Prairie | 2025-08-22 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003641 | 5880 | 105 | 56 | HB-S07-03 | Harbor | 2025-08-22 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003642 | 11907 | 189 | 63 | PR-S11-01 | Prairie | 2025-08-22 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003643 | 4095 | 39 | 105 | BY-S24-03 | Bayou | 2025-08-22 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-003644 | 711 | 9 | 79 | BY-S19-04 | Bayou | 2025-08-22 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003645 | 5510 | 38 | 145 | CR-S09-04 | Crossroads | 2025-08-22 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-003646 | 10736 | 88 | 122 | CR-S25-02 | Crossroads | 2025-08-22 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003647 | 27072 | 752 | 36 | HB-S07-02 | Harbor | 2025-08-23 | 0 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003648 | 6402 | 66 | 97 | HB-S04-01 | Harbor | 2025-08-23 | 4 | Vegetation | Lateral fuse | Forced | None
OE-25-003649 | 310 | 2 | 155 | BY-S21-04 | Bayou | 2025-08-23 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003650 | 2268 | 108 | 21 | BY-S18-07 | Bayou | 2025-08-23 | 13 | Animal | Lateral fuse | Forced | None
OE-25-003651 | 348 | 4 | 87 | HB-S09-05 | Harbor | 2025-08-23 | 13 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003652 | 2002 | 14 | 143 | PR-S08-01 | Prairie | 2025-08-23 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-003653 | 324 | 4 | 81 | BY-S25-04 | Bayou | 2025-08-23 | 14 | Animal | Transformer fuse | Forced | None
OE-25-003654 | 840 | 14 | 60 | CR-S09-05 | Crossroads | 2025-08-23 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003655 | 1953 | 9 | 217 | PR-S08-03 | Prairie | 2025-08-23 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003656 | 17640 | 882 | 20 | CR-S18-02 | Crossroads | 2025-08-23 | 15 | Equipment - overhead | Substation breaker | Forced | None
OE-25-003657 | 2030 | 14 | 145 | CR-S20-02 | Crossroads | 2025-08-23 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-003658 | 103 | 1 | 103 | HB-S11-01 | Harbor | 2025-08-23 | 20 | Animal | Transformer fuse | Forced | None
OE-25-003659 | 23940 | 342 | 70 | CR-S17-02 | Crossroads | 2025-08-23 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003660 | 31898 | 389 | 82 | CR-S18-04 | Crossroads | 2025-08-23 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003661 | 304 | 2 | 152 | HB-S11-01 | Harbor | 2025-08-24 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-003662 | 36936 | 1368 | 27 | HB-S01-05 | Harbor | 2025-08-24 | 4 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003663 | 462 | 7 | 66 | HB-S20-02 | Harbor | 2025-08-24 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003664 | 22015 | 85 | 259 | HB-S05-03 | Harbor | 2025-08-24 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003665 | 67485 | 1227 | 55 | HB-S17-02 | Harbor | 2025-08-24 | 9 | Vegetation | Feeder recloser | Forced | None
OE-25-003666 | 3458 | 14 | 247 | CR-S04-01 | Crossroads | 2025-08-24 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003667 | 999 | 3 | 333 | PR-S17-01 | Prairie | 2025-08-24 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003668 | 565 | 5 | 113 | HB-S10-03 | Harbor | 2025-08-24 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003669 | 927 | 9 | 103 | PR-S09-02 | Prairie | 2025-08-24 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003670 | 3235 | 5 | 647 | HB-S17-02 | Harbor | 2025-08-24 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003671 | 2136 | 12 | 178 | PR-S05-03 | Prairie | 2025-08-24 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003672 | 608 | 8 | 76 | CR-S03-02 | Crossroads | 2025-08-24 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-003673 | 2140 | 10 | 214 | HB-S17-02 | Harbor | 2025-08-24 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003674 | 32319 | 189 | 171 | BY-S18-07 | Bayou | 2025-08-24 | 20 | Animal | Lateral fuse | Forced | None
OE-25-003675 | 438 | 3 | 146 | BY-S26-06 | Bayou | 2025-08-24 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003676 | 1135 | 5 | 227 | HB-S17-03 | Harbor | 2025-08-24 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-003677 | 1836 | 12 | 153 | HB-S18-01 | Harbor | 2025-08-24 | 20 | Animal | Transformer fuse | Forced | None
OE-25-003678 | 115920 | 920 | 126 | PR-S18-02 | Prairie | 2025-08-24 | 23 | Weather - lightning | Substation breaker | Forced | None
OE-25-003679 | 1729 | 13 | 133 | PR-S04-02 | Prairie | 2025-08-25 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003680 | 4620 | 35 | 132 | PR-S16-01 | Prairie | 2025-08-25 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003681 | 1944 | 9 | 216 | CR-S09-05 | Crossroads | 2025-08-25 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003682 | 12330 | 137 | 90 | BY-S03-02 | Bayou | 2025-08-25 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003683 | 10656 | 144 | 74 | CR-S13-01 | Crossroads | 2025-08-25 | 11 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-003684 | 1323 | 7 | 189 | CR-S28-01 | Crossroads | 2025-08-25 | 12 | Animal | Transformer fuse | Forced | None
OE-25-003685 | 2375 | 19 | 125 | HB-S17-03 | Harbor | 2025-08-25 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003686 | 9246 | 67 | 138 | HB-S07-02 | Harbor | 2025-08-25 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-25-003687 | 440 | 4 | 110 | HB-S12-01 | Harbor | 2025-08-25 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-25-003688 | 3650 | 25 | 146 | PR-S02-03 | Prairie | 2025-08-25 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-003689 | 14000 | 500 | 28 | CR-S28-02 | Crossroads | 2025-08-25 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-003690 | 2366 | 13 | 182 | HB-S19-04 | Harbor | 2025-08-25 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-003691 | 2420 | 55 | 44 | BY-S13-05 | Bayou | 2025-08-25 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-003692 | 12408 | 188 | 66 | HB-S11-01 | Harbor | 2025-08-25 | 17 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-003693 | 792 | 3 | 264 | BY-S07-01 | Bayou | 2025-08-25 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003694 | 716 | 4 | 179 | BY-S23-05 | Bayou | 2025-08-25 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-003695 | 6360 | 12 | 530 | CR-S20-03 | Crossroads | 2025-08-26 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003696 | 5084 | 62 | 82 | CR-S03-01 | Crossroads | 2025-08-26 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-003697 | 3808 | 28 | 136 | HB-S10-01 | Harbor | 2025-08-26 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003698 | 121095 | 1053 | 115 | BY-S17-04 | Bayou | 2025-08-26 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-003699 | 2712 | 12 | 226 | BY-S21-01 | Bayou | 2025-08-26 | 12 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003700 | 1464 | 8 | 183 | HB-S05-04 | Harbor | 2025-08-26 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-003701 | 402 | 2 | 201 | BY-S06-01 | Bayou | 2025-08-26 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-003702 | 504 | 7 | 72 | HB-S04-01 | Harbor | 2025-08-26 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003703 | 2904 | 33 | 88 | BY-S23-01 | Bayou | 2025-08-26 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003704 | 88150 | 430 | 205 | PR-S01-03 | Prairie | 2025-08-26 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-003705 | 2856 | 12 | 238 | PR-S18-03 | Prairie | 2025-08-26 | 15 | Animal | Transformer fuse | Forced | None
OE-25-003706 | 7742 | 49 | 158 | BY-S06-02 | Bayou | 2025-08-26 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-003707 | 52332 | 623 | 84 | HB-S13-02 | Harbor | 2025-08-26 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-003708 | 15857 | 157 | 101 | CR-S04-01 | Crossroads | 2025-08-26 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-003709 | 6319 | 89 | 71 | PR-S13-06 | Prairie | 2025-08-26 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003710 | 1179 | 9 | 131 | PR-S09-04 | Prairie | 2025-08-26 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-003711 | 53125 | 425 | 125 | CR-S10-02 | Crossroads | 2025-08-26 | 22 | Unknown | IGSD-isolated section | Forced | None
OE-25-003712 | 65850 | 1317 | 50 | HB-S08-01 | Harbor | 2025-08-26 | 22 | Equipment - underground | Substation breaker | Forced | None
OE-25-003713 | 77371 | 1579 | 49 | PR-S14-04 | Prairie | 2025-08-27 | 1 | Vegetation | Feeder recloser | Forced | None
OE-25-003714 | 7100 | 100 | 71 | BY-S29-05 | Bayou | 2025-08-27 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-25-003715 | 25536 | 168 | 152 | CR-S20-03 | Crossroads | 2025-08-27 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003716 | 532 | 14 | 38 | HB-S20-05 | Harbor | 2025-08-27 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-003717 | 219 | 3 | 73 | HB-S05-06 | Harbor | 2025-08-27 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003718 | 33744 | 1406 | 24 | HB-S07-02 | Harbor | 2025-08-27 | 8 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003719 | 1128 | 8 | 141 | PR-S04-01 | Prairie | 2025-08-27 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003720 | 81716 | 659 | 124 | CR-S17-01 | Crossroads | 2025-08-27 | 9 | Animal | IGSD-isolated section | Forced | None
OE-25-003721 | 5282 | 38 | 139 | PR-S02-01 | Prairie | 2025-08-27 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003722 | 145 | 1 | 145 | HB-S05-02 | Harbor | 2025-08-27 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003723 | 5031 | 39 | 129 | BY-S07-04 | Bayou | 2025-08-27 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003724 | 15744 | 128 | 123 | BY-S09-04 | Bayou | 2025-08-27 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003725 | 4301 | 23 | 187 | BY-S23-02 | Bayou | 2025-08-27 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003726 | 13020 | 124 | 105 | BY-S29-01 | Bayou | 2025-08-27 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003727 | 2740 | 20 | 137 | HB-S01-03 | Harbor | 2025-08-27 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003728 | 43112 | 317 | 136 | PR-S16-03 | Prairie | 2025-08-27 | 12 | Weather - wind | Feeder recloser | Forced | None
OE-25-003729 | 1128 | 8 | 141 | CR-S12-02 | Crossroads | 2025-08-27 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003730 | 462 | 6 | 77 | CR-S17-01 | Crossroads | 2025-08-27 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-003731 | 240 | 1 | 240 | PR-S16-04 | Prairie | 2025-08-27 | 14 | Animal | Transformer fuse | Forced | None
OE-25-003732 | 1380 | 12 | 115 | CR-S26-03 | Crossroads | 2025-08-27 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003733 | 60756 | 996 | 61 | BY-S16-01 | Bayou | 2025-08-27 | 18 | Vehicle or public | IGSD-isolated section | Forced | None
OE-25-003734 | 71592 | 942 | 76 | HB-S16-03 | Harbor | 2025-08-27 | 23 | Unknown | Substation breaker | Outside cause | None
OE-25-003735 | 1428 | 12 | 119 | CR-S02-03 | Crossroads | 2025-08-28 | 1 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003736 | 13815 | 45 | 307 | HB-S09-02 | Harbor | 2025-08-28 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003737 | 1339 | 13 | 103 | BY-S29-01 | Bayou | 2025-08-28 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-003738 | 35987 | 371 | 97 | CR-S22-04 | Crossroads | 2025-08-28 | 8 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-003739 | 956 | 4 | 239 | PR-S17-01 | Prairie | 2025-08-28 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-003740 | 40338 | 1494 | 27 | BY-S18-05 | Bayou | 2025-08-28 | 13 | Vehicle or public | Substation breaker | Forced | None
OE-25-003741 | 412 | 4 | 103 | CR-S23-03 | Crossroads | 2025-08-28 | 13 | Animal | Transformer fuse | Forced | None
OE-25-003742 | 19557 | 123 | 159 | HB-S04-01 | Harbor | 2025-08-28 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003743 | 35148 | 303 | 116 | PR-S16-02 | Prairie | 2025-08-28 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-25-003744 | 140 | 1 | 140 | CR-S14-04 | Crossroads | 2025-08-28 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003745 | 4200 | 10 | 420 | HB-S12-01 | Harbor | 2025-08-28 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003746 | 36498 | 553 | 66 | BY-S07-01 | Bayou | 2025-08-28 | 15 | Animal | Feeder recloser | Forced | None
OE-25-003747 | 9711 | 83 | 117 | BY-S23-02 | Bayou | 2025-08-28 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-003748 | 49775 | 905 | 55 | CR-S23-05 | Crossroads | 2025-08-28 | 18 | Weather - wind | Feeder recloser | Forced | None
OE-25-003749 | 7774 | 46 | 169 | BY-S26-03 | Bayou | 2025-08-28 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003750 | 3051 | 27 | 113 | PR-S15-02 | Prairie | 2025-08-28 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-003751 | 15840 | 165 | 96 | PR-S07-02 | Prairie | 2025-08-28 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003752 | 7252 | 98 | 74 | PR-S18-06 | Prairie | 2025-08-29 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003753 | 267 | 3 | 89 | BY-S07-01 | Bayou | 2025-08-29 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003754 | 4730 | 55 | 86 | BY-S24-02 | Bayou | 2025-08-29 | 7 | Unknown | Lateral fuse | Forced | None
OE-25-003755 | 1251 | 9 | 139 | CR-S24-01 | Crossroads | 2025-08-29 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003756 | 891 | 11 | 81 | BY-S07-02 | Bayou | 2025-08-29 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003757 | 20930 | 230 | 91 | CR-S17-02 | Crossroads | 2025-08-29 | 9 | Weather - lightning | Feeder recloser | Forced | None
OE-25-003758 | 3114 | 9 | 346 | CR-S20-02 | Crossroads | 2025-08-29 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003759 | 9180 | 85 | 108 | BY-S15-05 | Bayou | 2025-08-29 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003760 | 5780 | 68 | 85 | CR-S15-01 | Crossroads | 2025-08-29 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003761 | 1926 | 9 | 214 | PR-S05-01 | Prairie | 2025-08-29 | 12 | Animal | Transformer fuse | Forced | None
OE-25-003762 | 5472 | 36 | 152 | BY-S18-03 | Bayou | 2025-08-29 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003763 | 8478 | 54 | 157 | CR-S06-02 | Crossroads | 2025-08-29 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003764 | 1360 | 10 | 136 | CR-S27-03 | Crossroads | 2025-08-29 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003765 | 5772 | 37 | 156 | PR-S08-03 | Prairie | 2025-08-29 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003766 | 749 | 7 | 107 | BY-S08-02 | Bayou | 2025-08-29 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003767 | 968 | 11 | 88 | BY-S13-05 | Bayou | 2025-08-29 | 17 | Animal | Transformer fuse | Forced | None
OE-25-003768 | 2310 | 77 | 30 | CR-S07-05 | Crossroads | 2025-08-29 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003769 | 12740 | 49 | 260 | PR-S20-02 | Prairie | 2025-08-29 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003770 | 2948 | 11 | 268 | BY-S08-02 | Bayou | 2025-08-30 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003771 | 1105 | 13 | 85 | CR-S06-03 | Crossroads | 2025-08-30 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003772 | 6786 | 78 | 87 | BY-S25-04 | Bayou | 2025-08-30 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003773 | 1763 | 41 | 43 | HB-S16-01 | Harbor | 2025-08-30 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-25-003774 | 7626 | 41 | 186 | PR-S07-05 | Prairie | 2025-08-30 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003775 | 2079 | 33 | 63 | HB-S05-03 | Harbor | 2025-08-30 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003776 | 10773 | 171 | 63 | HB-S14-02 | Harbor | 2025-08-30 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-003777 | 6048 | 56 | 108 | PR-S03-02 | Prairie | 2025-08-30 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003778 | 1742 | 13 | 134 | HB-S20-03 | Harbor | 2025-08-30 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003779 | 1250 | 10 | 125 | BY-S19-04 | Bayou | 2025-08-30 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-003780 | 10108 | 266 | 38 | PR-S15-01 | Prairie | 2025-08-30 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-003781 | 23826 | 418 | 57 | BY-S07-01 | Bayou | 2025-08-30 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003782 | 20424 | 222 | 92 | BY-S10-04 | Bayou | 2025-08-30 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003783 | 22975 | 919 | 25 | CR-S18-04 | Crossroads | 2025-08-30 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-003784 | 8658 | 37 | 234 | PR-S08-01 | Prairie | 2025-08-30 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003785 | 19981 | 377 | 53 | CR-S09-04 | Crossroads | 2025-08-31 | 0 | Animal | Feeder recloser | Forced | None
OE-25-003786 | 10797 | 59 | 183 | BY-S25-02 | Bayou | 2025-08-31 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003787 | 1115 | 5 | 223 | PR-S10-02 | Prairie | 2025-08-31 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003788 | 91 | 1 | 91 | BY-S19-02 | Bayou | 2025-08-31 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003789 | 72362 | 746 | 97 | BY-S15-06 | Bayou | 2025-08-31 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-25-003790 | 30396 | 447 | 68 | BY-S23-05 | Bayou | 2025-08-31 | 16 | Unknown | Feeder recloser | Forced | None
OE-25-003791 | 215 | 1 | 215 | CR-S21-03 | Crossroads | 2025-08-31 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003792 | 3481 | 59 | 59 | HB-S20-02 | Harbor | 2025-08-31 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003793 | 128 | 1 | 128 | PR-S05-02 | Prairie | 2025-08-31 | 19 | Animal | Transformer fuse | Forced | None
OE-25-003794 | 18205 | 55 | 331 | PR-S18-03 | Prairie | 2025-08-31 | 19 | Animal | Lateral fuse | Forced | None
OE-25-003795 | 15589 | 131 | 119 | BY-S01-02 | Bayou | 2025-08-31 | 21 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-003796 | 147477 | 1353 | 109 | HB-S07-02 | Harbor | 2025-09-01 | 3 | Weather - wind | Feeder recloser | Forced | None
OE-25-003797 | 2616 | 24 | 109 | HB-S02-03 | Harbor | 2025-09-01 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003798 | 8320 | 64 | 130 | PR-S09-01 | Prairie | 2025-09-01 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-25-003799 | 80538 | 433 | 186 | PR-S13-04 | Prairie | 2025-09-01 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003800 | 1746 | 9 | 194 | HB-S13-02 | Harbor | 2025-09-01 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-003801 | 2420 | 10 | 242 | BY-S19-02 | Bayou | 2025-09-01 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-003802 | 7380 | 30 | 246 | BY-S28-02 | Bayou | 2025-09-01 | 9 | Animal | Lateral fuse | Forced | None
OE-25-003803 | 30213 | 373 | 81 | CR-S03-02 | Crossroads | 2025-09-01 | 9 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003804 | 546 | 3 | 182 | PR-S15-05 | Prairie | 2025-09-01 | 9 | Animal | Transformer fuse | Forced | None
OE-25-003805 | 300 | 2 | 150 | HB-S15-03 | Harbor | 2025-09-01 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003806 | 30745 | 143 | 215 | CR-S25-03 | Crossroads | 2025-09-01 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-003807 | 672 | 7 | 96 | PR-S10-01 | Prairie | 2025-09-01 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-003808 | 3996 | 27 | 148 | BY-S09-05 | Bayou | 2025-09-01 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003809 | 14196 | 507 | 28 | PR-S01-06 | Prairie | 2025-09-01 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-25-003810 | 17365 | 115 | 151 | PR-S07-04 | Prairie | 2025-09-01 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-25-003811 | 663 | 3 | 221 | BY-S25-05 | Bayou | 2025-09-01 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-003812 | 2772 | 12 | 231 | BY-S18-06 | Bayou | 2025-09-01 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-003813 | 420 | 2 | 210 | CR-S13-06 | Crossroads | 2025-09-01 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003814 | 4284 | 34 | 126 | PR-S01-03 | Prairie | 2025-09-01 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003815 | 7228 | 139 | 52 | BY-S19-02 | Bayou | 2025-09-01 | 23 | Vegetation | Lateral fuse | Forced | None
OE-25-003816 | 477 | 3 | 159 | CR-S21-01 | Crossroads | 2025-09-02 | 3 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003817 | 193830 | 1846 | 105 | CR-S28-03 | Crossroads | 2025-09-02 | 5 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003818 | 3009 | 51 | 59 | BY-S19-04 | Bayou | 2025-09-02 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003819 | 4472 | 26 | 172 | CR-S01-03 | Crossroads | 2025-09-02 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003820 | 90552 | 924 | 98 | HB-S07-05 | Harbor | 2025-09-02 | 8 | Weather - wind | Substation breaker | Forced | None
OE-25-003821 | 2086 | 7 | 298 | PR-S09-03 | Prairie | 2025-09-02 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-003822 | 1640 | 8 | 205 | PR-S13-01 | Prairie | 2025-09-02 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003823 | 1944 | 27 | 72 | BY-S30-01 | Bayou | 2025-09-02 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003824 | 2070 | 30 | 69 | CR-S17-03 | Crossroads | 2025-09-02 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003825 | 7119 | 63 | 113 | CR-S28-03 | Crossroads | 2025-09-02 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003826 | 91948 | 508 | 181 | BY-S11-01 | Bayou | 2025-09-02 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003827 | 6567 | 33 | 199 | BY-S21-04 | Bayou | 2025-09-02 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003828 | 59584 | 532 | 112 | CR-S19-01 | Crossroads | 2025-09-02 | 16 | Animal | Feeder recloser | Forced | None
OE-25-003829 | 7524 | 99 | 76 | BY-S02-02 | Bayou | 2025-09-02 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-003830 | 298 | 2 | 149 | BY-S27-04 | Bayou | 2025-09-02 | 23 | Animal | Transformer fuse | Forced | None
OE-25-003831 | 10336 | 32 | 323 | CR-S16-06 | Crossroads | 2025-09-03 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003832 | 255 | 3 | 85 | CR-S04-01 | Crossroads | 2025-09-03 | 10 | Animal | Transformer fuse | Forced | None
OE-25-003833 | 550 | 5 | 110 | BY-S21-03 | Bayou | 2025-09-03 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-003834 | 32065 | 605 | 53 | CR-S04-02 | Crossroads | 2025-09-03 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003835 | 805 | 5 | 161 | CR-S24-04 | Crossroads | 2025-09-03 | 11 | Animal | Transformer fuse | Forced | None
OE-25-003836 | 5112 | 24 | 213 | BY-S06-02 | Bayou | 2025-09-03 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003837 | 9207 | 33 | 279 | CR-S29-02 | Crossroads | 2025-09-03 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003838 | 19838 | 109 | 182 | HB-S06-05 | Harbor | 2025-09-03 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003839 | 11835 | 45 | 263 | PR-S17-01 | Prairie | 2025-09-03 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003840 | 7035 | 67 | 105 | BY-S19-03 | Bayou | 2025-09-03 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-003841 | 3164 | 14 | 226 | BY-S15-02 | Bayou | 2025-09-03 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003842 | 2520 | 12 | 210 | HB-S08-02 | Harbor | 2025-09-03 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003843 | 3000 | 30 | 100 | BY-S02-02 | Bayou | 2025-09-03 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003844 | 14560 | 80 | 182 | CR-S04-06 | Crossroads | 2025-09-03 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-003845 | 1656 | 12 | 138 | CR-S26-01 | Crossroads | 2025-09-03 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003846 | 1364 | 31 | 44 | HB-S14-04 | Harbor | 2025-09-03 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003847 | 73332 | 1746 | 42 | BY-S07-02 | Bayou | 2025-09-03 | 17 | Equipment - underground | Substation breaker | Forced | None
OE-25-003848 | 1832 | 8 | 229 | BY-S16-06 | Bayou | 2025-09-03 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003849 | 31842 | 261 | 122 | BY-S03-01 | Bayou | 2025-09-03 | 20 | Vegetation | IGSD-isolated section | Forced | None
OE-25-003850 | 2002 | 26 | 77 | HB-S19-04 | Harbor | 2025-09-03 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003851 | 2761 | 11 | 251 | HB-S20-03 | Harbor | 2025-09-04 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003852 | 15436 | 68 | 227 | CR-S24-02 | Crossroads | 2025-09-04 | 9 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003853 | 67821 | 1833 | 37 | PR-S10-03 | Prairie | 2025-09-04 | 9 | Vegetation | Substation breaker | Forced | None
OE-25-003854 | 2670 | 6 | 445 | CR-S16-05 | Crossroads | 2025-09-04 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003855 | 4144 | 112 | 37 | CR-S02-04 | Crossroads | 2025-09-04 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003856 | 2596 | 44 | 59 | BY-S15-06 | Bayou | 2025-09-04 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003857 | 33120 | 230 | 144 | BY-S25-02 | Bayou | 2025-09-04 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003858 | 1592 | 8 | 199 | CR-S13-03 | Crossroads | 2025-09-04 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-003859 | 105672 | 1258 | 84 | CR-S28-03 | Crossroads | 2025-09-04 | 17 | Animal | Feeder recloser | Forced | None
OE-25-003860 | 7750 | 50 | 155 | BY-S17-04 | Bayou | 2025-09-04 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003861 | 1480 | 5 | 296 | PR-S16-03 | Prairie | 2025-09-05 | 3 | Vehicle or public | Transformer fuse | Forced | None
OE-25-003862 | 1128 | 8 | 141 | HB-S12-03 | Harbor | 2025-09-05 | 5 | Unknown | Transformer fuse | Forced | None
OE-25-003863 | 2412 | 9 | 268 | HB-S12-02 | Harbor | 2025-09-05 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003864 | 2431 | 17 | 143 | CR-S25-05 | Crossroads | 2025-09-05 | 8 | Unknown | Lateral fuse | Forced | None
OE-25-003865 | 5775 | 35 | 165 | HB-S01-02 | Harbor | 2025-09-05 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003866 | 1243 | 11 | 113 | PR-S20-03 | Prairie | 2025-09-05 | 9 | Animal | Transformer fuse | Forced | None
OE-25-003867 | 48060 | 890 | 54 | BY-S26-02 | Bayou | 2025-09-05 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003868 | 2200 | 25 | 88 | PR-S06-02 | Prairie | 2025-09-05 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-003869 | 52110 | 1158 | 45 | PR-S08-01 | Prairie | 2025-09-05 | 13 | Vegetation | Feeder recloser | Forced | None
OE-25-003870 | 18834 | 146 | 129 | HB-S18-01 | Harbor | 2025-09-05 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003871 | 186494 | 2422 | 77 | HB-S09-02 | Harbor | 2025-09-05 | 17 | Equipment - underground | Feeder recloser | Forced | None
OE-25-003872 | 3978 | 13 | 306 | BY-S06-02 | Bayou | 2025-09-05 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003873 | 1416 | 6 | 236 | HB-S12-02 | Harbor | 2025-09-06 | 3 | Vegetation | Transformer fuse | Forced | None
OE-25-003874 | 404 | 4 | 101 | CR-S26-04 | Crossroads | 2025-09-06 | 6 | Weather - wind | Transformer fuse | Forced | None
OE-25-003875 | 4921 | 37 | 133 | BY-S22-01 | Bayou | 2025-09-06 | 9 | Animal | Lateral fuse | Forced | None
OE-25-003876 | 2140 | 20 | 107 | CR-S18-06 | Crossroads | 2025-09-06 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003877 | 150 | 1 | 150 | PR-S14-04 | Prairie | 2025-09-06 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003878 | 216 | 2 | 108 | PR-S01-05 | Prairie | 2025-09-06 | 13 | Animal | Transformer fuse | Forced | None
OE-25-003879 | 708 | 2 | 354 | BY-S25-04 | Bayou | 2025-09-06 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-003880 | 10703 | 139 | 77 | BY-S27-05 | Bayou | 2025-09-06 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003881 | 85728 | 564 | 152 | BY-S14-03 | Bayou | 2025-09-06 | 16 | Vegetation | Feeder recloser | Forced | None
OE-25-003882 | 9064 | 88 | 103 | PR-S07-03 | Prairie | 2025-09-06 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-003883 | 925 | 25 | 37 | CR-S27-03 | Crossroads | 2025-09-06 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-003884 | 7920 | 72 | 110 | BY-S20-03 | Bayou | 2025-09-06 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-25-003885 | 1969 | 11 | 179 | CR-S22-04 | Crossroads | 2025-09-06 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003886 | 3196 | 68 | 47 | CR-S23-04 | Crossroads | 2025-09-06 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-003887 | 14946 | 106 | 141 | CR-S13-05 | Crossroads | 2025-09-06 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003888 | 20010 | 115 | 174 | BY-S06-01 | Bayou | 2025-09-06 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-003889 | 25432 | 136 | 187 | BY-S12-03 | Bayou | 2025-09-06 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-003890 | 2316 | 12 | 193 | HB-S09-04 | Harbor | 2025-09-06 | 22 | Animal | Transformer fuse | Forced | None
OE-25-003891 | 3182 | 43 | 74 | PR-S03-01 | Prairie | 2025-09-06 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003892 | 7215 | 65 | 111 | BY-S07-05 | Bayou | 2025-09-07 | 3 | Vegetation | Lateral fuse | Forced | None
OE-25-003893 | 3248 | 28 | 116 | BY-S20-03 | Bayou | 2025-09-07 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003894 | 1392 | 8 | 174 | PR-S15-01 | Prairie | 2025-09-07 | 4 | Animal | Transformer fuse | Forced | None
OE-25-003895 | 57986 | 158 | 367 | HB-S15-02 | Harbor | 2025-09-07 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-003896 | 137000 | 548 | 250 | CR-S30-02 | Crossroads | 2025-09-07 | 6 | Weather - wind | Feeder recloser | Forced | None
OE-25-003897 | 752 | 4 | 188 | PR-S20-04 | Prairie | 2025-09-07 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-003898 | 580 | 5 | 116 | CR-S27-04 | Crossroads | 2025-09-07 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003899 | 1680 | 12 | 140 | CR-S04-06 | Crossroads | 2025-09-07 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003900 | 219 | 3 | 73 | BY-S18-04 | Bayou | 2025-09-07 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003901 | 2292 | 12 | 191 | BY-S25-04 | Bayou | 2025-09-07 | 15 | Animal | Transformer fuse | Forced | None
OE-25-003902 | 3268 | 19 | 172 | PR-S15-03 | Prairie | 2025-09-07 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003903 | 910 | 14 | 65 | HB-S01-05 | Harbor | 2025-09-07 | 17 | Animal | Transformer fuse | Forced | None
OE-25-003904 | 29600 | 200 | 148 | BY-S26-03 | Bayou | 2025-09-07 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003905 | 8700 | 87 | 100 | HB-S15-03 | Harbor | 2025-09-07 | 19 | Unknown | Lateral fuse | Forced | None
OE-25-003906 | 6400 | 64 | 100 | CR-S14-01 | Crossroads | 2025-09-07 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003907 | 63 | 1 | 63 | BY-S25-04 | Bayou | 2025-09-07 | 22 | Animal | Transformer fuse | Forced | None
OE-25-003908 | 860 | 10 | 86 | PR-S06-01 | Prairie | 2025-09-08 | 0 | Unknown | Transformer fuse | Forced | None
OE-25-003909 | 2072 | 14 | 148 | CR-S07-01 | Crossroads | 2025-09-08 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-003910 | 11808 | 123 | 96 | CR-S16-02 | Crossroads | 2025-09-08 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003911 | 435 | 3 | 145 | CR-S22-04 | Crossroads | 2025-09-08 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003912 | 138 | 1 | 138 | HB-S15-03 | Harbor | 2025-09-08 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-003913 | 7950 | 75 | 106 | BY-S15-04 | Bayou | 2025-09-08 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-003914 | 94116 | 759 | 124 | BY-S28-03 | Bayou | 2025-09-08 | 10 | Weather - wind | Feeder recloser | Forced | None
OE-25-003915 | 7272 | 36 | 202 | CR-S28-03 | Crossroads | 2025-09-08 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003916 | 1092 | 7 | 156 | HB-S01-03 | Harbor | 2025-09-08 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-003917 | 12036 | 354 | 34 | BY-S25-02 | Bayou | 2025-09-08 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003918 | 16402 | 278 | 59 | PR-S02-01 | Prairie | 2025-09-08 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003919 | 1296 | 8 | 162 | BY-S10-01 | Bayou | 2025-09-08 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003920 | 18780 | 626 | 30 | BY-S12-03 | Bayou | 2025-09-08 | 16 | Vegetation | Feeder recloser | Forced | None
OE-25-003921 | 32200 | 115 | 280 | BY-S15-02 | Bayou | 2025-09-08 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003922 | 1304 | 8 | 163 | BY-S07-05 | Bayou | 2025-09-08 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-003923 | 68943 | 469 | 147 | BY-S27-03 | Bayou | 2025-09-08 | 18 | Weather - lightning | Feeder recloser | Forced | None
OE-25-003924 | 4085 | 43 | 95 | BY-S10-04 | Bayou | 2025-09-09 | 3 | Vegetation | Lateral fuse | Forced | None
OE-25-003925 | 1434 | 6 | 239 | CR-S10-02 | Crossroads | 2025-09-09 | 5 | Animal | Transformer fuse | Forced | None
OE-25-003926 | 1144 | 11 | 104 | CR-S07-03 | Crossroads | 2025-09-09 | 7 | Animal | Transformer fuse | Forced | None
OE-25-003927 | 2772 | 9 | 308 | PR-S01-03 | Prairie | 2025-09-09 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-003928 | 29488 | 152 | 194 | HB-S03-03 | Harbor | 2025-09-09 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-003929 | 4572 | 12 | 381 | PR-S01-03 | Prairie | 2025-09-09 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-003930 | 9870 | 105 | 94 | BY-S25-01 | Bayou | 2025-09-09 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-003931 | 10452 | 78 | 134 | CR-S01-02 | Crossroads | 2025-09-09 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003932 | 2130 | 10 | 213 | BY-S20-01 | Bayou | 2025-09-09 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003933 | 24941 | 509 | 49 | HB-S11-01 | Harbor | 2025-09-09 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003934 | 928 | 4 | 232 | PR-S15-06 | Prairie | 2025-09-09 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003935 | 252 | 4 | 63 | CR-S18-04 | Crossroads | 2025-09-09 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003936 | 731 | 17 | 43 | PR-S18-06 | Prairie | 2025-09-09 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-003937 | 3840 | 24 | 160 | BY-S24-02 | Bayou | 2025-09-09 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003938 | 23661 | 239 | 99 | HB-S06-01 | Harbor | 2025-09-09 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003939 | 517 | 11 | 47 | CR-S18-04 | Crossroads | 2025-09-09 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-003940 | 1414 | 14 | 101 | CR-S26-03 | Crossroads | 2025-09-09 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-003941 | 2086 | 7 | 298 | BY-S27-01 | Bayou | 2025-09-09 | 22 | Unknown | Transformer fuse | Forced | None
OE-25-003942 | 216300 | 700 | 309 | HB-S18-03 | Harbor | 2025-09-10 | 0 | Vegetation | Feeder recloser | Forced | None
OE-25-003943 | 24900 | 75 | 332 | BY-S18-01 | Bayou | 2025-09-10 | 1 | Vegetation | Lateral fuse | Forced | None
OE-25-003944 | 65408 | 224 | 292 | BY-S14-02 | Bayou | 2025-09-10 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003945 | 532 | 4 | 133 | BY-S26-05 | Bayou | 2025-09-10 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003946 | 2700 | 30 | 90 | CR-S29-01 | Crossroads | 2025-09-10 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-003947 | 42976 | 316 | 136 | CR-S14-02 | Crossroads | 2025-09-10 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003948 | 416 | 8 | 52 | BY-S15-05 | Bayou | 2025-09-10 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003949 | 58953 | 1371 | 43 | CR-S23-02 | Crossroads | 2025-09-10 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-003950 | 48910 | 146 | 335 | BY-S15-02 | Bayou | 2025-09-10 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-003951 | 20296 | 472 | 43 | CR-S09-05 | Crossroads | 2025-09-10 | 20 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003952 | 17220 | 84 | 205 | BY-S19-02 | Bayou | 2025-09-11 | 1 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003953 | 1026 | 6 | 171 | CR-S22-03 | Crossroads | 2025-09-11 | 1 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003954 | 1890 | 7 | 270 | BY-S12-03 | Bayou | 2025-09-11 | 5 | Animal | Transformer fuse | Forced | None
OE-25-003955 | 31680 | 144 | 220 | CR-S31-03 | Crossroads | 2025-09-11 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003956 | 940 | 5 | 188 | PR-S16-05 | Prairie | 2025-09-11 | 8 | Unknown | Transformer fuse | Forced | None
OE-25-003957 | 1134 | 9 | 126 | PR-S20-01 | Prairie | 2025-09-11 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003958 | 972 | 12 | 81 | PR-S17-01 | Prairie | 2025-09-11 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003959 | 950 | 5 | 190 | PR-S19-01 | Prairie | 2025-09-11 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003960 | 16954 | 173 | 98 | HB-S17-01 | Harbor | 2025-09-11 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-003961 | 4350 | 30 | 145 | BY-S18-04 | Bayou | 2025-09-11 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-003962 | 1608 | 12 | 134 | PR-S03-02 | Prairie | 2025-09-11 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-003963 | 11628 | 68 | 171 | PR-S18-04 | Prairie | 2025-09-11 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003964 | 267 | 1 | 267 | CR-S02-05 | Crossroads | 2025-09-11 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003965 | 1772 | 4 | 443 | CR-S12-03 | Crossroads | 2025-09-11 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003966 | 1070 | 5 | 214 | BY-S01-01 | Bayou | 2025-09-11 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003967 | 6003 | 29 | 207 | BY-S07-01 | Bayou | 2025-09-11 | 22 | Animal | Lateral fuse | Forced | None
OE-25-003968 | 36838 | 226 | 163 | HB-S13-02 | Harbor | 2025-09-11 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003969 | 109330 | 841 | 130 | PR-S19-01 | Prairie | 2025-09-11 | 22 | Animal | Substation breaker | Forced | None
OE-25-003970 | 40880 | 292 | 140 | BY-S17-03 | Bayou | 2025-09-12 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003971 | 12160 | 80 | 152 | CR-S17-01 | Crossroads | 2025-09-12 | 9 | Vehicle or public | Lateral fuse | Forced | None
OE-25-003972 | 2072 | 14 | 148 | CR-S14-05 | Crossroads | 2025-09-12 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003973 | 3596 | 29 | 124 | HB-S08-02 | Harbor | 2025-09-12 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003974 | 39556 | 116 | 341 | PR-S16-05 | Prairie | 2025-09-12 | 10 | Animal | Lateral fuse | Forced | None
OE-25-003975 | 1595 | 5 | 319 | BY-S22-01 | Bayou | 2025-09-12 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-003976 | 3510 | 13 | 270 | HB-S17-03 | Harbor | 2025-09-12 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003977 | 8850 | 50 | 177 | PR-S04-01 | Prairie | 2025-09-12 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003978 | 1653 | 19 | 87 | CR-S21-02 | Crossroads | 2025-09-12 | 12 | Animal | Lateral fuse | Forced | None
OE-25-003979 | 268 | 4 | 67 | CR-S32-04 | Crossroads | 2025-09-12 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-003980 | 3240 | 27 | 120 | HB-S15-02 | Harbor | 2025-09-12 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-003981 | 11368 | 56 | 203 | PR-S06-03 | Prairie | 2025-09-12 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-003982 | 1368 | 12 | 114 | PR-S14-04 | Prairie | 2025-09-12 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003983 | 4346 | 53 | 82 | BY-S15-05 | Bayou | 2025-09-12 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003984 | 42880 | 640 | 67 | PR-S18-04 | Prairie | 2025-09-12 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-003985 | 430 | 2 | 215 | BY-S30-03 | Bayou | 2025-09-12 | 20 | Animal | Transformer fuse | Forced | None
OE-25-003986 | 13065 | 67 | 195 | BY-S05-01 | Bayou | 2025-09-12 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003987 | 720 | 16 | 45 | BY-S10-04 | Bayou | 2025-09-13 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-003988 | 980 | 10 | 98 | CR-S30-04 | Crossroads | 2025-09-13 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-003989 | 910 | 5 | 182 | PR-S15-01 | Prairie | 2025-09-13 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-003990 | 133518 | 1309 | 102 | CR-S22-01 | Crossroads | 2025-09-13 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-003991 | 24525 | 545 | 45 | HB-S15-03 | Harbor | 2025-09-13 | 11 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-003992 | 8772 | 51 | 172 | CR-S03-03 | Crossroads | 2025-09-13 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-003993 | 2970 | 11 | 270 | HB-S13-01 | Harbor | 2025-09-13 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-003994 | 93720 | 781 | 120 | CR-S02-01 | Crossroads | 2025-09-13 | 15 | Weather - lightning | Feeder recloser | Forced | None
OE-25-003995 | 550 | 10 | 55 | CR-S04-01 | Crossroads | 2025-09-13 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-003996 | 594 | 6 | 99 | CR-S06-03 | Crossroads | 2025-09-13 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-003997 | 546 | 7 | 78 | CR-S25-05 | Crossroads | 2025-09-13 | 19 | Animal | Transformer fuse | Forced | None
OE-25-003998 | 34894 | 146 | 239 | PR-S13-03 | Prairie | 2025-09-13 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-003999 | 1890 | 10 | 189 | BY-S18-05 | Bayou | 2025-09-14 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-004000 | 316 | 4 | 79 | CR-S27-02 | Crossroads | 2025-09-14 | 7 | Animal | Transformer fuse | Forced | None
OE-25-004001 | 420 | 6 | 70 | BY-S18-04 | Bayou | 2025-09-14 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-004002 | 14696 | 167 | 88 | PR-S02-01 | Prairie | 2025-09-14 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-25-004003 | 51072 | 608 | 84 | PR-S18-02 | Prairie | 2025-09-14 | 9 | Animal | Feeder recloser | Forced | None
OE-25-004004 | 7533 | 31 | 243 | BY-S26-02 | Bayou | 2025-09-14 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-004005 | 5412 | 33 | 164 | BY-S15-04 | Bayou | 2025-09-14 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-004006 | 13350 | 150 | 89 | PR-S07-06 | Prairie | 2025-09-14 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004007 | 714 | 14 | 51 | HB-S07-01 | Harbor | 2025-09-14 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-004008 | 14746 | 73 | 202 | BY-S14-03 | Bayou | 2025-09-14 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004009 | 816 | 8 | 102 | CR-S22-01 | Crossroads | 2025-09-14 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004010 | 7047 | 81 | 87 | BY-S25-04 | Bayou | 2025-09-14 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-004011 | 83296 | 1096 | 76 | CR-S32-03 | Crossroads | 2025-09-14 | 20 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004012 | 103725 | 1383 | 75 | HB-S05-06 | Harbor | 2025-09-14 | 20 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004013 | 39160 | 220 | 178 | HB-S04-01 | Harbor | 2025-09-15 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004014 | 475 | 5 | 95 | BY-S13-06 | Bayou | 2025-09-15 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004015 | 3752 | 14 | 268 | CR-S30-06 | Crossroads | 2025-09-15 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-004016 | 2398 | 11 | 218 | BY-S19-01 | Bayou | 2025-09-15 | 10 | Animal | Transformer fuse | Forced | None
OE-25-004017 | 9870 | 329 | 30 | CR-S23-03 | Crossroads | 2025-09-15 | 10 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004018 | 280 | 2 | 140 | HB-S14-03 | Harbor | 2025-09-15 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004019 | 144124 | 526 | 274 | PR-S03-04 | Prairie | 2025-09-15 | 11 | Unknown | Substation breaker | Forced | None
OE-25-004020 | 20496 | 183 | 112 | PR-S19-01 | Prairie | 2025-09-15 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004021 | 10082 | 71 | 142 | BY-S02-01 | Bayou | 2025-09-15 | 13 | Unknown | Lateral fuse | Forced | None
OE-25-004022 | 688 | 16 | 43 | CR-S26-02 | Crossroads | 2025-09-15 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004023 | 32490 | 722 | 45 | BY-S15-01 | Bayou | 2025-09-15 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004024 | 7137 | 39 | 183 | BY-S22-04 | Bayou | 2025-09-15 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004025 | 17172 | 159 | 108 | BY-S26-06 | Bayou | 2025-09-15 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-004026 | 831 | 3 | 277 | BY-S23-01 | Bayou | 2025-09-15 | 19 | Weather - wind | Transformer fuse | Forced | None
OE-25-004027 | 45024 | 201 | 224 | PR-S02-01 | Prairie | 2025-09-15 | 19 | Animal | Lateral fuse | Forced | None
OE-25-004028 | 1170 | 10 | 117 | BY-S03-01 | Bayou | 2025-09-15 | 21 | Animal | Lateral fuse | Forced | None
OE-25-004029 | 882 | 9 | 98 | HB-S17-02 | Harbor | 2025-09-16 | 0 | Animal | Transformer fuse | Forced | None
OE-25-004030 | 832 | 8 | 104 | BY-S21-02 | Bayou | 2025-09-16 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004031 | 1560 | 13 | 120 | PR-S13-05 | Prairie | 2025-09-16 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004032 | 1417 | 13 | 109 | BY-S30-02 | Bayou | 2025-09-16 | 8 | Animal | Transformer fuse | Forced | None
OE-25-004033 | 4788 | 28 | 171 | PR-S03-05 | Prairie | 2025-09-16 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004034 | 18228 | 196 | 93 | BY-S11-03 | Bayou | 2025-09-16 | 9 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-004035 | 10360 | 70 | 148 | PR-S17-01 | Prairie | 2025-09-16 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004036 | 960 | 10 | 96 | BY-S04-03 | Bayou | 2025-09-16 | 10 | Animal | Transformer fuse | Forced | None
OE-25-004037 | 3650 | 50 | 73 | CR-S19-02 | Crossroads | 2025-09-16 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004038 | 1183 | 13 | 91 | BY-S27-02 | Bayou | 2025-09-16 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-004039 | 3752 | 56 | 67 | PR-S15-03 | Prairie | 2025-09-16 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004040 | 2140 | 10 | 214 | BY-S07-01 | Bayou | 2025-09-16 | 15 | Unknown | Transformer fuse | Forced | None
OE-25-004041 | 450 | 3 | 150 | BY-S30-03 | Bayou | 2025-09-16 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004042 | 2160 | 12 | 180 | HB-S04-02 | Harbor | 2025-09-16 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-004043 | 9301 | 131 | 71 | PR-S03-04 | Prairie | 2025-09-16 | 15 | Animal | Lateral fuse | Forced | None
OE-25-004044 | 24817 | 299 | 83 | CR-S02-01 | Crossroads | 2025-09-16 | 17 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-004045 | 872 | 8 | 109 | CR-S32-02 | Crossroads | 2025-09-16 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004046 | 20790 | 270 | 77 | PR-S06-02 | Prairie | 2025-09-16 | 21 | Vegetation | Feeder recloser | Forced | None
OE-25-004047 | 1820 | 14 | 130 | PR-S12-01 | Prairie | 2025-09-16 | 23 | Weather - wind | Transformer fuse | Forced | None
OE-25-004048 | 43316 | 476 | 91 | BY-S01-02 | Bayou | 2025-09-17 | 1 | Unknown | Feeder recloser | Forced | None
OE-25-004049 | 60723 | 519 | 117 | BY-S07-06 | Bayou | 2025-09-17 | 2 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004050 | 8800 | 32 | 275 | PR-S01-02 | Prairie | 2025-09-17 | 6 | Weather - wind | Lateral fuse | Forced | None
OE-25-004051 | 688 | 4 | 172 | PR-S03-03 | Prairie | 2025-09-17 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004052 | 984 | 6 | 164 | CR-S14-02 | Crossroads | 2025-09-17 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004053 | 6026 | 23 | 262 | BY-S25-04 | Bayou | 2025-09-17 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004054 | 4592 | 41 | 112 | CR-S09-03 | Crossroads | 2025-09-17 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004055 | 1708 | 4 | 427 | PR-S05-03 | Prairie | 2025-09-17 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-004056 | 1008 | 8 | 126 | BY-S12-02 | Bayou | 2025-09-17 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004057 | 648 | 9 | 72 | CR-S24-04 | Crossroads | 2025-09-17 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004058 | 5400 | 120 | 45 | BY-S17-02 | Bayou | 2025-09-17 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004059 | 3652 | 11 | 332 | PR-S16-05 | Prairie | 2025-09-18 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-004060 | 1700 | 10 | 170 | HB-S02-02 | Harbor | 2025-09-18 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004061 | 39732 | 903 | 44 | CR-S11-01 | Crossroads | 2025-09-18 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004062 | 1080 | 15 | 72 | BY-S29-03 | Bayou | 2025-09-18 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-004063 | 53361 | 847 | 63 | CR-S03-03 | Crossroads | 2025-09-18 | 15 | Vegetation | Substation breaker | Forced | None
OE-25-004064 | 7875 | 105 | 75 | PR-S13-02 | Prairie | 2025-09-18 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004065 | 7175 | 35 | 205 | CR-S14-02 | Crossroads | 2025-09-18 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004066 | 10212 | 74 | 138 | PR-S18-06 | Prairie | 2025-09-18 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004067 | 2765 | 79 | 35 | BY-S26-01 | Bayou | 2025-09-18 | 17 | Animal | Lateral fuse | Forced | None
OE-25-004068 | 27376 | 236 | 116 | CR-S04-05 | Crossroads | 2025-09-18 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004069 | 840 | 8 | 105 | BY-S25-05 | Bayou | 2025-09-18 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004070 | 5600 | 40 | 140 | HB-S07-02 | Harbor | 2025-09-18 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004071 | 43344 | 504 | 86 | PR-S02-02 | Prairie | 2025-09-18 | 19 | Weather - wind | Feeder recloser | Forced | None
OE-25-004072 | 1353 | 11 | 123 | BY-S29-02 | Bayou | 2025-09-18 | 21 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004073 | 480 | 6 | 80 | BY-S18-01 | Bayou | 2025-09-19 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004074 | 3266 | 46 | 71 | BY-S13-06 | Bayou | 2025-09-19 | 9 | Animal | Lateral fuse | Forced | None
OE-25-004075 | 1728 | 12 | 144 | PR-S14-03 | Prairie | 2025-09-19 | 9 | Unknown | Transformer fuse | Forced | None
OE-25-004076 | 900 | 12 | 75 | BY-S21-04 | Bayou | 2025-09-19 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004077 | 4422 | 67 | 66 | CR-S21-03 | Crossroads | 2025-09-19 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004078 | 1860 | 31 | 60 | HB-S03-03 | Harbor | 2025-09-19 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004079 | 15174 | 281 | 54 | PR-S11-01 | Prairie | 2025-09-19 | 11 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004080 | 12685 | 59 | 215 | PR-S09-02 | Prairie | 2025-09-19 | 14 | Animal | Lateral fuse | Forced | None
OE-25-004081 | 10746 | 199 | 54 | CR-S17-01 | Crossroads | 2025-09-19 | 15 | Animal | Lateral fuse | Forced | None
OE-25-004082 | 21630 | 206 | 105 | HB-S06-02 | Harbor | 2025-09-19 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004083 | 312 | 2 | 156 | HB-S17-02 | Harbor | 2025-09-19 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-25-004084 | 561 | 3 | 187 | CR-S05-01 | Crossroads | 2025-09-19 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004085 | 756 | 9 | 84 | BY-S29-02 | Bayou | 2025-09-19 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-004086 | 3315 | 13 | 255 | PR-S03-05 | Prairie | 2025-09-19 | 20 | Animal | Transformer fuse | Forced | None
OE-25-004087 | 3087 | 9 | 343 | BY-S14-01 | Bayou | 2025-09-19 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-004088 | 3432 | 52 | 66 | CR-S04-04 | Crossroads | 2025-09-19 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004089 | 432 | 6 | 72 | BY-S29-05 | Bayou | 2025-09-20 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004090 | 462 | 14 | 33 | CR-S14-06 | Crossroads | 2025-09-20 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004091 | 78 | 1 | 78 | BY-S24-01 | Bayou | 2025-09-20 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004092 | 710 | 5 | 142 | CR-S16-01 | Crossroads | 2025-09-20 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-004093 | 2279 | 53 | 43 | HB-S18-02 | Harbor | 2025-09-20 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-004094 | 25298 | 182 | 139 | BY-S20-02 | Bayou | 2025-09-20 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-004095 | 266 | 2 | 133 | BY-S21-04 | Bayou | 2025-09-20 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-004096 | 416 | 4 | 104 | CR-S05-03 | Crossroads | 2025-09-20 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-004097 | 1120 | 14 | 80 | PR-S05-01 | Prairie | 2025-09-20 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004098 | 15540 | 105 | 148 | CR-S04-02 | Crossroads | 2025-09-20 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004099 | 1105 | 5 | 221 | CR-S12-03 | Crossroads | 2025-09-20 | 20 | Animal | Transformer fuse | Forced | None
OE-25-004100 | 73587 | 1291 | 57 | BY-S25-04 | Bayou | 2025-09-20 | 21 | Equipment - overhead | Substation breaker | Forced | None
OE-25-004101 | 830 | 10 | 83 | CR-S06-02 | Crossroads | 2025-09-21 | 3 | Animal | Transformer fuse | Forced | None
OE-25-004102 | 2418 | 13 | 186 | BY-S05-01 | Bayou | 2025-09-21 | 4 | Vegetation | Transformer fuse | Forced | None
OE-25-004103 | 1800 | 12 | 150 | PR-S15-06 | Prairie | 2025-09-21 | 5 | Weather - wind | Transformer fuse | Forced | None
OE-25-004104 | 1615 | 17 | 95 | CR-S19-03 | Crossroads | 2025-09-21 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004105 | 132 | 1 | 132 | CR-S26-04 | Crossroads | 2025-09-21 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004106 | 432 | 4 | 108 | PR-S13-03 | Prairie | 2025-09-21 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-004107 | 4089 | 47 | 87 | BY-S16-03 | Bayou | 2025-09-21 | 9 | Animal | Lateral fuse | Forced | None
OE-25-004108 | 616 | 11 | 56 | CR-S22-01 | Crossroads | 2025-09-21 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004109 | 1330 | 14 | 95 | HB-S20-03 | Harbor | 2025-09-21 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004110 | 2970 | 55 | 54 | BY-S30-03 | Bayou | 2025-09-21 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004111 | 1408 | 8 | 176 | CR-S26-03 | Crossroads | 2025-09-21 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004112 | 162 | 1 | 162 | BY-S08-03 | Bayou | 2025-09-21 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004113 | 291708 | 2701 | 108 | CR-S31-02 | Crossroads | 2025-09-21 | 15 | Equipment - overhead | Substation breaker | Forced | None
OE-25-004114 | 7998 | 93 | 86 | CR-S01-03 | Crossroads | 2025-09-21 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004115 | 76248 | 353 | 216 | HB-S05-04 | Harbor | 2025-09-21 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004116 | 1501 | 19 | 79 | CR-S13-05 | Crossroads | 2025-09-21 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-004117 | 609 | 7 | 87 | BY-S27-01 | Bayou | 2025-09-21 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-004118 | 6794 | 86 | 79 | BY-S01-01 | Bayou | 2025-09-22 | 4 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004119 | 11776 | 46 | 256 | PR-S11-01 | Prairie | 2025-09-22 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-004120 | 5187 | 13 | 399 | CR-S16-04 | Crossroads | 2025-09-22 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004121 | 210 | 3 | 70 | HB-S15-02 | Harbor | 2025-09-22 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004122 | 15840 | 66 | 240 | PR-S13-02 | Prairie | 2025-09-22 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004123 | 901 | 17 | 53 | PR-S18-06 | Prairie | 2025-09-22 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-004124 | 1680 | 7 | 240 | CR-S26-02 | Crossroads | 2025-09-22 | 12 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004125 | 3752 | 28 | 134 | CR-S32-05 | Crossroads | 2025-09-22 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004126 | 992 | 8 | 124 | BY-S22-03 | Bayou | 2025-09-22 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004127 | 138 | 1 | 138 | CR-S21-02 | Crossroads | 2025-09-22 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004128 | 23010 | 295 | 78 | BY-S11-01 | Bayou | 2025-09-22 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004129 | 1903 | 11 | 173 | BY-S21-01 | Bayou | 2025-09-22 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004130 | 472 | 4 | 118 | CR-S07-05 | Crossroads | 2025-09-22 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004131 | 24827 | 671 | 37 | HB-S08-04 | Harbor | 2025-09-22 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004132 | 17760 | 74 | 240 | PR-S16-05 | Prairie | 2025-09-22 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004133 | 1925 | 35 | 55 | PR-S19-02 | Prairie | 2025-09-23 | 4 | Vegetation | Lateral fuse | Forced | None
OE-25-004134 | 43968 | 458 | 96 | BY-S02-01 | Bayou | 2025-09-23 | 7 | Animal | IGSD-isolated section | Forced | None
OE-25-004135 | 56644 | 833 | 68 | CR-S30-04 | Crossroads | 2025-09-23 | 7 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-004136 | 62730 | 615 | 102 | BY-S21-02 | Bayou | 2025-09-23 | 10 | Vegetation | Feeder recloser | Forced | None
OE-25-004137 | 10348 | 199 | 52 | BY-S02-02 | Bayou | 2025-09-23 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-004138 | 581 | 7 | 83 | HB-S05-03 | Harbor | 2025-09-23 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004139 | 1235 | 5 | 247 | BY-S29-04 | Bayou | 2025-09-23 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-004140 | 180 | 2 | 90 | CR-S26-04 | Crossroads | 2025-09-23 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004141 | 55100 | 380 | 145 | BY-S24-04 | Bayou | 2025-09-23 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004142 | 66584 | 1624 | 41 | CR-S24-01 | Crossroads | 2025-09-23 | 18 | Equipment - overhead | Substation breaker | Forced | None
OE-25-004143 | 22440 | 102 | 220 | BY-S17-03 | Bayou | 2025-09-23 | 22 | Weather - wind | Lateral fuse | Forced | None
OE-25-004144 | 11610 | 86 | 135 | PR-S06-02 | Prairie | 2025-09-23 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-004145 | 45758 | 334 | 137 | CR-S30-04 | Crossroads | 2025-09-23 | 23 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004146 | 4796 | 44 | 109 | HB-S17-03 | Harbor | 2025-09-24 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004147 | 40334 | 602 | 67 | BY-S13-01 | Bayou | 2025-09-24 | 4 | Vegetation | Feeder recloser | Forced | None
OE-25-004148 | 2457 | 27 | 91 | BY-S06-03 | Bayou | 2025-09-24 | 7 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004149 | 5888 | 46 | 128 | BY-S07-01 | Bayou | 2025-09-24 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004150 | 30504 | 93 | 328 | PR-S11-02 | Prairie | 2025-09-24 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004151 | 3256 | 11 | 296 | PR-S08-03 | Prairie | 2025-09-24 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-004152 | 428 | 4 | 107 | BY-S05-03 | Bayou | 2025-09-24 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-004153 | 102044 | 388 | 263 | BY-S12-04 | Bayou | 2025-09-24 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004154 | 45105 | 291 | 155 | CR-S27-03 | Crossroads | 2025-09-24 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004155 | 2805 | 11 | 255 | BY-S13-04 | Bayou | 2025-09-24 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004156 | 96015 | 519 | 185 | CR-S07-01 | Crossroads | 2025-09-24 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004157 | 3885 | 37 | 105 | BY-S23-03 | Bayou | 2025-09-24 | 17 | Unknown | Lateral fuse | Forced | None
OE-25-004158 | 1680 | 24 | 70 | CR-S25-03 | Crossroads | 2025-09-24 | 17 | Animal | Lateral fuse | Forced | None
OE-25-004159 | 332 | 2 | 166 | CR-S20-01 | Crossroads | 2025-09-24 | 20 | Animal | Transformer fuse | Forced | None
OE-25-004160 | 525 | 1 | 525 | BY-S15-02 | Bayou | 2025-09-24 | 23 | Vegetation | Transformer fuse | Forced | None
OE-25-004161 | 125290 | 1870 | 67 | HB-S09-02 | Harbor | 2025-09-25 | 1 | Vegetation | Feeder recloser | Forced | None
OE-25-004162 | 3220 | 28 | 115 | PR-S13-06 | Prairie | 2025-09-25 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004163 | 96 | 1 | 96 | BY-S03-03 | Bayou | 2025-09-25 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004164 | 8520 | 71 | 120 | PR-S13-01 | Prairie | 2025-09-25 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004165 | 3168 | 16 | 198 | HB-S05-02 | Harbor | 2025-09-25 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004166 | 7708 | 41 | 188 | HB-S19-04 | Harbor | 2025-09-25 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004167 | 1150 | 10 | 115 | CR-S26-04 | Crossroads | 2025-09-25 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004168 | 4551 | 111 | 41 | HB-S17-01 | Harbor | 2025-09-25 | 13 | Unknown | Lateral fuse | Forced | None
OE-25-004169 | 10692 | 108 | 99 | PR-S09-01 | Prairie | 2025-09-25 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004170 | 4498 | 13 | 346 | PR-S13-01 | Prairie | 2025-09-25 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004171 | 2002 | 22 | 91 | PR-S13-04 | Prairie | 2025-09-25 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-004172 | 5776 | 76 | 76 | HB-S15-03 | Harbor | 2025-09-25 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004173 | 3120 | 40 | 78 | BY-S26-01 | Bayou | 2025-09-25 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-004174 | 1700 | 10 | 170 | BY-S30-01 | Bayou | 2025-09-25 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-004175 | 69574 | 809 | 86 | CR-S29-03 | Crossroads | 2025-09-25 | 17 | Weather - wind | Feeder recloser | Forced | None
OE-25-004176 | 1248 | 8 | 156 | BY-S08-03 | Bayou | 2025-09-25 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-25-004177 | 114450 | 654 | 175 | BY-S30-01 | Bayou | 2025-09-25 | 21 | Weather - wind | Feeder recloser | Forced | None
OE-25-004178 | 1372 | 7 | 196 | CR-S07-06 | Crossroads | 2025-09-25 | 21 | Animal | Transformer fuse | Forced | None
OE-25-004179 | 8640 | 48 | 180 | PR-S20-02 | Prairie | 2025-09-26 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004180 | 1584 | 12 | 132 | BY-S04-01 | Bayou | 2025-09-26 | 9 | Unknown | Transformer fuse | Forced | None
OE-25-004181 | 800 | 5 | 160 | CR-S12-01 | Crossroads | 2025-09-26 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004182 | 96 | 1 | 96 | CR-S12-01 | Crossroads | 2025-09-26 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004183 | 1024 | 8 | 128 | CR-S07-03 | Crossroads | 2025-09-26 | 11 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004184 | 639 | 9 | 71 | HB-S05-05 | Harbor | 2025-09-26 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-004185 | 3456 | 48 | 72 | PR-S13-02 | Prairie | 2025-09-26 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004186 | 13932 | 86 | 162 | BY-S15-01 | Bayou | 2025-09-26 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004187 | 2840 | 10 | 284 | PR-S02-03 | Prairie | 2025-09-26 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-004188 | 8432 | 248 | 34 | CR-S27-01 | Crossroads | 2025-09-26 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-004189 | 54 | 1 | 54 | HB-S03-03 | Harbor | 2025-09-26 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004190 | 410 | 10 | 41 | HB-S08-04 | Harbor | 2025-09-27 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004191 | 42196 | 274 | 154 | PR-S01-03 | Prairie | 2025-09-27 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004192 | 21970 | 130 | 169 | PR-S05-03 | Prairie | 2025-09-27 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-004193 | 528 | 4 | 132 | BY-S13-06 | Bayou | 2025-09-27 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004194 | 2405 | 13 | 185 | BY-S07-03 | Bayou | 2025-09-27 | 11 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004195 | 7378 | 217 | 34 | BY-S16-03 | Bayou | 2025-09-27 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-004196 | 9735 | 165 | 59 | CR-S26-06 | Crossroads | 2025-09-27 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-004197 | 2698 | 19 | 142 | PR-S15-03 | Prairie | 2025-09-27 | 12 | Animal | Lateral fuse | Forced | None
OE-25-004198 | 488 | 2 | 244 | BY-S09-03 | Bayou | 2025-09-27 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-004199 | 612 | 2 | 306 | BY-S21-02 | Bayou | 2025-09-27 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004200 | 33003 | 57 | 579 | BY-S12-02 | Bayou | 2025-09-27 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-004201 | 1692 | 12 | 141 | BY-S18-04 | Bayou | 2025-09-27 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-004202 | 1404 | 12 | 117 | CR-S26-06 | Crossroads | 2025-09-27 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004203 | 4224 | 33 | 128 | PR-S18-06 | Prairie | 2025-09-27 | 14 | Unknown | Lateral fuse | Forced | None
OE-25-004204 | 9432 | 36 | 262 | PR-S01-03 | Prairie | 2025-09-27 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004205 | 6674 | 71 | 94 | PR-S08-01 | Prairie | 2025-09-27 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004206 | 26316 | 204 | 129 | BY-S13-06 | Bayou | 2025-09-27 | 20 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004207 | 5088 | 106 | 48 | CR-S18-04 | Crossroads | 2025-09-28 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-004208 | 170 | 5 | 34 | BY-S01-02 | Bayou | 2025-09-28 | 4 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004209 | 238380 | 1644 | 145 | BY-S02-01 | Bayou | 2025-09-28 | 6 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-004210 | 46800 | 780 | 60 | BY-S12-01 | Bayou | 2025-09-28 | 6 | Vegetation | Substation breaker | Forced | None
OE-25-004211 | 880 | 22 | 40 | BY-S23-01 | Bayou | 2025-09-28 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004212 | 365 | 5 | 73 | PR-S08-03 | Prairie | 2025-09-28 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004213 | 540 | 6 | 90 | CR-S27-02 | Crossroads | 2025-09-28 | 9 | Unknown | Transformer fuse | Forced | None
OE-25-004214 | 3456 | 54 | 64 | BY-S23-05 | Bayou | 2025-09-28 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-004215 | 1030 | 10 | 103 | HB-S15-02 | Harbor | 2025-09-28 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-004216 | 33480 | 1395 | 24 | CR-S05-03 | Crossroads | 2025-09-28 | 14 | Equipment - underground | Substation breaker | Forced | None
OE-25-004217 | 1442 | 14 | 103 | BY-S12-04 | Bayou | 2025-09-28 | 15 | Animal | Transformer fuse | Forced | None
OE-25-004218 | 23862 | 194 | 123 | CR-S22-01 | Crossroads | 2025-09-28 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004219 | 22842 | 162 | 141 | HB-S11-01 | Harbor | 2025-09-28 | 15 | Vegetation | IGSD-isolated section | Forced | None
OE-25-004220 | 47083 | 197 | 239 | HB-S03-03 | Harbor | 2025-09-28 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004221 | 10184 | 67 | 152 | PR-S03-03 | Prairie | 2025-09-28 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-004222 | 3640 | 56 | 65 | CR-S32-02 | Crossroads | 2025-09-28 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004223 | 70886 | 1058 | 67 | BY-S02-01 | Bayou | 2025-09-28 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004224 | 26112 | 384 | 68 | HB-S15-02 | Harbor | 2025-09-28 | 20 | Vegetation | Feeder recloser | Forced | None
OE-25-004225 | 23485 | 427 | 55 | BY-S18-02 | Bayou | 2025-09-28 | 21 | Vegetation | Feeder recloser | Forced | None
OE-25-004226 | 1968 | 48 | 41 | BY-S16-06 | Bayou | 2025-09-28 | 22 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004227 | 2613 | 13 | 201 | BY-S22-04 | Bayou | 2025-09-29 | 3 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004228 | 819 | 13 | 63 | PR-S01-05 | Prairie | 2025-09-29 | 4 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004229 | 9394 | 61 | 154 | CR-S09-01 | Crossroads | 2025-09-29 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-004230 | 101 | 1 | 101 | HB-S13-02 | Harbor | 2025-09-29 | 8 | Animal | Transformer fuse | Forced | None
OE-25-004231 | 3857 | 19 | 203 | PR-S06-03 | Prairie | 2025-09-29 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004232 | 5850 | 45 | 130 | HB-S11-03 | Harbor | 2025-09-29 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004233 | 1794 | 13 | 138 | CR-S14-04 | Crossroads | 2025-09-29 | 13 | Animal | Transformer fuse | Forced | None
OE-25-004234 | 5412 | 66 | 82 | BY-S19-02 | Bayou | 2025-09-29 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004235 | 1232 | 14 | 88 | HB-S03-02 | Harbor | 2025-09-29 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-004236 | 2977 | 13 | 229 | BY-S06-02 | Bayou | 2025-09-29 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004237 | 28861 | 133 | 217 | PR-S03-06 | Prairie | 2025-09-29 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-004238 | 2249 | 13 | 173 | CR-S04-03 | Crossroads | 2025-09-29 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004239 | 2590 | 37 | 70 | CR-S30-07 | Crossroads | 2025-09-29 | 18 | Animal | Lateral fuse | Forced | None
OE-25-004240 | 16492 | 124 | 133 | PR-S16-04 | Prairie | 2025-09-29 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-004241 | 13769 | 281 | 49 | PR-S06-03 | Prairie | 2025-09-29 | 20 | Vegetation | IGSD-isolated section | Forced | None
OE-25-004242 | 6776 | 121 | 56 | HB-S20-01 | Harbor | 2025-09-30 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004243 | 27456 | 832 | 33 | BY-S09-04 | Bayou | 2025-09-30 | 1 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004244 | 334 | 2 | 167 | PR-S01-05 | Prairie | 2025-09-30 | 1 | Vegetation | Transformer fuse | Forced | None
OE-25-004245 | 4189 | 59 | 71 | BY-S29-03 | Bayou | 2025-09-30 | 2 | Vegetation | Lateral fuse | Forced | None
OE-25-004246 | 464 | 4 | 116 | BY-S13-03 | Bayou | 2025-09-30 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004247 | 258 | 3 | 86 | PR-S20-03 | Prairie | 2025-09-30 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-25-004248 | 508 | 4 | 127 | PR-S07-05 | Prairie | 2025-09-30 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-004249 | 20079 | 97 | 207 | CR-S08-01 | Crossroads | 2025-09-30 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004250 | 125822 | 1187 | 106 | PR-S18-03 | Prairie | 2025-09-30 | 10 | Vegetation | Substation breaker | Forced | None
OE-25-004251 | 738 | 6 | 123 | HB-S12-03 | Harbor | 2025-09-30 | 13 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004252 | 4743 | 17 | 279 | PR-S19-01 | Prairie | 2025-09-30 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-004253 | 18262 | 397 | 46 | BY-S10-05 | Bayou | 2025-09-30 | 15 | Weather - wind | Feeder recloser | Forced | None
OE-25-004254 | 3014 | 11 | 274 | BY-S27-03 | Bayou | 2025-09-30 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-004255 | 1133 | 11 | 103 | CR-S25-02 | Crossroads | 2025-09-30 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004256 | 5950 | 85 | 70 | HB-S03-03 | Harbor | 2025-09-30 | 16 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004257 | 978 | 6 | 163 | BY-S11-02 | Bayou | 2025-09-30 | 17 | Animal | Transformer fuse | Forced | None
OE-25-004258 | 756 | 4 | 189 | BY-S02-01 | Bayou | 2025-09-30 | 18 | Animal | Transformer fuse | Forced | None
OE-25-004259 | 280 | 2 | 140 | CR-S04-02 | Crossroads | 2025-09-30 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004260 | 9312 | 97 | 96 | HB-S19-04 | Harbor | 2025-09-30 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004261 | 8442 | 63 | 134 | HB-S02-01 | Harbor | 2025-09-30 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004262 | 4308 | 6 | 718 | BY-S25-04 | Bayou | 2025-10-01 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004263 | 16660 | 85 | 196 | BY-S11-01 | Bayou | 2025-10-01 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004264 | 166 | 2 | 83 | CR-S26-02 | Crossroads | 2025-10-01 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004265 | 162 | 1 | 162 | BY-S07-01 | Bayou | 2025-10-01 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004266 | 19975 | 799 | 25 | HB-S18-01 | Harbor | 2025-10-01 | 9 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004267 | 1764 | 12 | 147 | PR-S07-04 | Prairie | 2025-10-01 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004268 | 14976 | 624 | 24 | CR-S11-02 | Crossroads | 2025-10-01 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004269 | 48709 | 727 | 67 | PR-S05-01 | Prairie | 2025-10-01 | 13 | Vegetation | Substation breaker | Forced | None
OE-25-004270 | 3520 | 64 | 55 | CR-S32-05 | Crossroads | 2025-10-01 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-004271 | 44560 | 557 | 80 | CR-S14-01 | Crossroads | 2025-10-01 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004272 | 3383 | 17 | 199 | BY-S24-04 | Bayou | 2025-10-01 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-004273 | 12948 | 83 | 156 | PR-S03-01 | Prairie | 2025-10-01 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004274 | 5254 | 37 | 142 | PR-S19-05 | Prairie | 2025-10-01 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-004275 | 6307 | 53 | 119 | BY-S03-01 | Bayou | 2025-10-01 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-004276 | 1040 | 8 | 130 | BY-S15-02 | Bayou | 2025-10-01 | 17 | Animal | Transformer fuse | Forced | None
OE-25-004277 | 21808 | 94 | 232 | BY-S28-03 | Bayou | 2025-10-01 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004278 | 7946 | 58 | 137 | HB-S01-01 | Harbor | 2025-10-01 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-004279 | 390 | 3 | 130 | CR-S30-05 | Crossroads | 2025-10-01 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004280 | 880 | 8 | 110 | BY-S29-05 | Bayou | 2025-10-02 | 6 | Weather - wind | Transformer fuse | Forced | None
OE-25-004281 | 5320 | 38 | 140 | HB-S18-03 | Harbor | 2025-10-02 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004282 | 790 | 10 | 79 | PR-S11-03 | Prairie | 2025-10-02 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-25-004283 | 736 | 4 | 184 | PR-S13-03 | Prairie | 2025-10-02 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-004284 | 20430 | 90 | 227 | PR-S15-04 | Prairie | 2025-10-02 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004285 | 162 | 1 | 162 | CR-S08-02 | Crossroads | 2025-10-02 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004286 | 4950 | 45 | 110 | BY-S28-01 | Bayou | 2025-10-02 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-004287 | 24274 | 229 | 106 | CR-S05-05 | Crossroads | 2025-10-02 | 23 | Animal | IGSD-isolated section | Forced | None
OE-25-004288 | 249600 | 1300 | 192 | CR-S07-07 | Crossroads | 2025-10-03 | 5 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004289 | 1210 | 10 | 121 | BY-S15-05 | Bayou | 2025-10-03 | 7 | Animal | Transformer fuse | Forced | None
OE-25-004290 | 852 | 6 | 142 | HB-S14-03 | Harbor | 2025-10-03 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004291 | 1596 | 14 | 114 | HB-S14-04 | Harbor | 2025-10-03 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004292 | 10944 | 144 | 76 | BY-S09-04 | Bayou | 2025-10-03 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004293 | 639 | 9 | 71 | CR-S23-03 | Crossroads | 2025-10-03 | 11 | Animal | Transformer fuse | Forced | None
OE-25-004294 | 5486 | 26 | 211 | HB-S17-01 | Harbor | 2025-10-03 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004295 | 20736 | 384 | 54 | PR-S13-06 | Prairie | 2025-10-03 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-004296 | 17967 | 339 | 53 | CR-S16-01 | Crossroads | 2025-10-03 | 12 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-004297 | 11070 | 82 | 135 | PR-S03-02 | Prairie | 2025-10-03 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004298 | 3610 | 10 | 361 | BY-S14-01 | Bayou | 2025-10-03 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004299 | 4433 | 11 | 403 | PR-S13-01 | Prairie | 2025-10-04 | 3 | Vegetation | Transformer fuse | Forced | None
OE-25-004300 | 38160 | 318 | 120 | CR-S07-04 | Crossroads | 2025-10-04 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004301 | 4790 | 10 | 479 | PR-S01-03 | Prairie | 2025-10-04 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004302 | 3300 | 44 | 75 | CR-S18-03 | Crossroads | 2025-10-04 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004303 | 261 | 3 | 87 | BY-S24-02 | Bayou | 2025-10-04 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-004304 | 4116 | 21 | 196 | CR-S12-03 | Crossroads | 2025-10-04 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-004305 | 161800 | 1618 | 100 | CR-S19-04 | Crossroads | 2025-10-04 | 20 | Vegetation | Feeder recloser | Forced | None
OE-25-004306 | 18507 | 199 | 93 | CR-S05-01 | Crossroads | 2025-10-04 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004307 | 37544 | 76 | 494 | PR-S07-06 | Prairie | 2025-10-05 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004308 | 73970 | 569 | 130 | BY-S21-04 | Bayou | 2025-10-05 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-004309 | 654 | 2 | 327 | PR-S10-02 | Prairie | 2025-10-05 | 9 | Animal | Transformer fuse | Forced | None
OE-25-004310 | 3192 | 38 | 84 | BY-S04-01 | Bayou | 2025-10-05 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004311 | 1764 | 9 | 196 | BY-S27-06 | Bayou | 2025-10-05 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-004312 | 2457 | 9 | 273 | BY-S10-05 | Bayou | 2025-10-05 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-004313 | 2115 | 9 | 235 | BY-S18-06 | Bayou | 2025-10-05 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-004314 | 2627 | 37 | 71 | BY-S10-04 | Bayou | 2025-10-05 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-004315 | 2574 | 26 | 99 | HB-S05-03 | Harbor | 2025-10-06 | 2 | Animal | Lateral fuse | Forced | None
OE-25-004316 | 1900 | 20 | 95 | BY-S06-02 | Bayou | 2025-10-06 | 5 | Animal | Lateral fuse | Forced | None
OE-25-004317 | 792 | 8 | 99 | CR-S14-03 | Crossroads | 2025-10-06 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004318 | 4445 | 35 | 127 | BY-S09-04 | Bayou | 2025-10-06 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004319 | 62702 | 214 | 293 | BY-S24-02 | Bayou | 2025-10-06 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004320 | 711 | 3 | 237 | CR-S24-03 | Crossroads | 2025-10-06 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004321 | 5157 | 27 | 191 | CR-S04-04 | Crossroads | 2025-10-06 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004322 | 1552 | 8 | 194 | CR-S09-02 | Crossroads | 2025-10-06 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004323 | 92 | 2 | 46 | HB-S06-04 | Harbor | 2025-10-06 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-25-004324 | 19153 | 107 | 179 | BY-S14-01 | Bayou | 2025-10-07 | 2 | Vegetation | Lateral fuse | Forced | None
OE-25-004325 | 1845 | 15 | 123 | PR-S10-01 | Prairie | 2025-10-07 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004326 | 104424 | 916 | 114 | PR-S06-01 | Prairie | 2025-10-07 | 11 | Animal | Feeder recloser | Forced | None
OE-25-004327 | 21988 | 478 | 46 | CR-S30-03 | Crossroads | 2025-10-07 | 12 | Animal | Feeder recloser | Forced | None
OE-25-004328 | 3616 | 113 | 32 | PR-S19-01 | Prairie | 2025-10-07 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004329 | 8028 | 36 | 223 | CR-S32-04 | Crossroads | 2025-10-07 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004330 | 986 | 29 | 34 | BY-S07-04 | Bayou | 2025-10-07 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004331 | 18290 | 118 | 155 | BY-S25-05 | Bayou | 2025-10-07 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-004332 | 102340 | 1204 | 85 | CR-S06-02 | Crossroads | 2025-10-07 | 15 | Vegetation | Feeder recloser | Forced | None
OE-25-004333 | 142704 | 1982 | 72 | CR-S14-02 | Crossroads | 2025-10-07 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004334 | 544 | 16 | 34 | PR-S04-02 | Prairie | 2025-10-07 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004335 | 2079 | 9 | 231 | PR-S20-01 | Prairie | 2025-10-07 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004336 | 5250 | 35 | 150 | BY-S10-03 | Bayou | 2025-10-07 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004337 | 660 | 12 | 55 | BY-S27-05 | Bayou | 2025-10-07 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-004338 | 3744 | 12 | 312 | PR-S12-02 | Prairie | 2025-10-07 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004339 | 7502 | 62 | 121 | HB-S06-01 | Harbor | 2025-10-08 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004340 | 4968 | 54 | 92 | BY-S11-02 | Bayou | 2025-10-08 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004341 | 801 | 9 | 89 | BY-S29-01 | Bayou | 2025-10-08 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004342 | 6468 | 77 | 84 | HB-S07-03 | Harbor | 2025-10-08 | 5 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004343 | 28305 | 333 | 85 | BY-S02-02 | Bayou | 2025-10-08 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-25-004344 | 34888 | 89 | 392 | BY-S15-02 | Bayou | 2025-10-08 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-004345 | 56090 | 355 | 158 | BY-S18-06 | Bayou | 2025-10-08 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-004346 | 2979 | 9 | 331 | CR-S25-02 | Crossroads | 2025-10-08 | 9 | Animal | Transformer fuse | Forced | None
OE-25-004347 | 13160 | 70 | 188 | BY-S15-01 | Bayou | 2025-10-08 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004348 | 2704 | 26 | 104 | PR-S12-03 | Prairie | 2025-10-08 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004349 | 21525 | 205 | 105 | CR-S32-03 | Crossroads | 2025-10-08 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004350 | 74655 | 553 | 135 | PR-S07-02 | Prairie | 2025-10-08 | 11 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004351 | 382 | 2 | 191 | PR-S12-01 | Prairie | 2025-10-08 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004352 | 805 | 7 | 115 | PR-S16-04 | Prairie | 2025-10-08 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-004353 | 18193 | 113 | 161 | BY-S29-03 | Bayou | 2025-10-08 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004354 | 1209 | 31 | 39 | BY-S07-01 | Bayou | 2025-10-08 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-25-004355 | 4472 | 86 | 52 | BY-S11-01 | Bayou | 2025-10-08 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004356 | 8096 | 88 | 92 | CR-S17-03 | Crossroads | 2025-10-08 | 15 | Animal | Lateral fuse | Forced | None
OE-25-004357 | 1420 | 10 | 142 | HB-S15-02 | Harbor | 2025-10-08 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004358 | 11883 | 51 | 233 | BY-S13-03 | Bayou | 2025-10-08 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004359 | 2079 | 11 | 189 | CR-S32-04 | Crossroads | 2025-10-08 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004360 | 17730 | 985 | 18 | HB-S06-05 | Harbor | 2025-10-09 | 6 | Weather - lightning | Substation breaker | Forced | None
OE-25-004361 | 2093 | 13 | 161 | CR-S10-02 | Crossroads | 2025-10-09 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004362 | 95288 | 554 | 172 | PR-S06-01 | Prairie | 2025-10-09 | 9 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004363 | 3780 | 36 | 105 | PR-S17-01 | Prairie | 2025-10-09 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004364 | 2442 | 22 | 111 | CR-S28-03 | Crossroads | 2025-10-09 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004365 | 952 | 8 | 119 | PR-S09-02 | Prairie | 2025-10-09 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004366 | 47528 | 914 | 52 | PR-S13-01 | Prairie | 2025-10-09 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-004367 | 11557 | 889 | 13 | CR-S26-03 | Crossroads | 2025-10-09 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004368 | 2508 | 33 | 76 | PR-S06-01 | Prairie | 2025-10-09 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004369 | 5180 | 14 | 370 | PR-S08-01 | Prairie | 2025-10-09 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-004370 | 1239 | 7 | 177 | PR-S16-05 | Prairie | 2025-10-09 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004371 | 35579 | 757 | 47 | BY-S09-03 | Bayou | 2025-10-09 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-004372 | 1036 | 4 | 259 | CR-S07-06 | Crossroads | 2025-10-09 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004373 | 3243 | 23 | 141 | PR-S10-01 | Prairie | 2025-10-09 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004374 | 2280 | 8 | 285 | PR-S14-03 | Prairie | 2025-10-10 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-004375 | 7620 | 30 | 254 | BY-S05-01 | Bayou | 2025-10-10 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004376 | 924 | 6 | 154 | BY-S27-06 | Bayou | 2025-10-10 | 8 | Unknown | Transformer fuse | Forced | None
OE-25-004377 | 959 | 7 | 137 | CR-S21-02 | Crossroads | 2025-10-10 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004378 | 2000 | 10 | 200 | BY-S15-01 | Bayou | 2025-10-10 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-004379 | 10807 | 101 | 107 | BY-S15-02 | Bayou | 2025-10-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004380 | 3552 | 24 | 148 | BY-S29-05 | Bayou | 2025-10-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004381 | 2530 | 22 | 115 | CR-S15-01 | Crossroads | 2025-10-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004382 | 17340 | 85 | 204 | CR-S09-04 | Crossroads | 2025-10-10 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004383 | 4459 | 13 | 343 | BY-S07-01 | Bayou | 2025-10-10 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-25-004384 | 2564 | 4 | 641 | PR-S20-02 | Prairie | 2025-10-10 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004385 | 4554 | 99 | 46 | BY-S09-04 | Bayou | 2025-10-10 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004386 | 7440 | 124 | 60 | BY-S26-04 | Bayou | 2025-10-10 | 22 | Unknown | Lateral fuse | Forced | None
OE-25-004387 | 2736 | 16 | 171 | BY-S07-01 | Bayou | 2025-10-11 | 0 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004388 | 67084 | 541 | 124 | BY-S02-02 | Bayou | 2025-10-11 | 1 | Weather - wind | Substation breaker | Forced | None
OE-25-004389 | 748 | 11 | 68 | BY-S01-01 | Bayou | 2025-10-11 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004390 | 1656 | 9 | 184 | BY-S09-01 | Bayou | 2025-10-11 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-004391 | 3078 | 38 | 81 | BY-S03-02 | Bayou | 2025-10-11 | 11 | Animal | Lateral fuse | Forced | None
OE-25-004392 | 846 | 9 | 94 | BY-S10-02 | Bayou | 2025-10-11 | 12 | Animal | Transformer fuse | Forced | None
OE-25-004393 | 2040 | 8 | 255 | HB-S14-01 | Harbor | 2025-10-11 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-004394 | 17100 | 76 | 225 | HB-S04-02 | Harbor | 2025-10-11 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-004395 | 572 | 11 | 52 | HB-S02-02 | Harbor | 2025-10-11 | 17 | Vegetation | Transformer fuse | Forced | None
OE-25-004396 | 212 | 2 | 106 | BY-S24-05 | Bayou | 2025-10-11 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004397 | 238569 | 849 | 281 | HB-S20-01 | Harbor | 2025-10-12 | 3 | Vegetation | Feeder recloser | Forced | None
OE-25-004398 | 5376 | 48 | 112 | BY-S09-02 | Bayou | 2025-10-12 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004399 | 2796 | 12 | 233 | PR-S16-05 | Prairie | 2025-10-12 | 8 | Vegetation | Transformer fuse | Forced | None
OE-25-004400 | 10234 | 86 | 119 | BY-S07-06 | Bayou | 2025-10-12 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-004401 | 1988 | 28 | 71 | PR-S20-04 | Prairie | 2025-10-12 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004402 | 5010 | 30 | 167 | PR-S01-03 | Prairie | 2025-10-12 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004403 | 1000 | 20 | 50 | HB-S06-02 | Harbor | 2025-10-12 | 12 | Animal | Lateral fuse | Forced | None
OE-25-004404 | 1236 | 4 | 309 | PR-S13-06 | Prairie | 2025-10-12 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004405 | 19896 | 829 | 24 | CR-S15-01 | Crossroads | 2025-10-12 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004406 | 380 | 2 | 190 | BY-S15-06 | Bayou | 2025-10-12 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004407 | 2244 | 12 | 187 | PR-S09-04 | Prairie | 2025-10-12 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004408 | 96 | 1 | 96 | BY-S13-01 | Bayou | 2025-10-12 | 22 | Animal | Transformer fuse | Forced | None
OE-25-004409 | 2951 | 13 | 227 | HB-S15-03 | Harbor | 2025-10-12 | 23 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004410 | 935 | 11 | 85 | PR-S13-02 | Prairie | 2025-10-13 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004411 | 1560 | 26 | 60 | BY-S09-03 | Bayou | 2025-10-13 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004412 | 1110 | 10 | 111 | BY-S15-04 | Bayou | 2025-10-13 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-004413 | 24080 | 86 | 280 | BY-S25-04 | Bayou | 2025-10-13 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-004414 | 332 | 2 | 166 | BY-S26-02 | Bayou | 2025-10-13 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004415 | 1140 | 15 | 76 | BY-S30-03 | Bayou | 2025-10-13 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004416 | 2625 | 15 | 175 | CR-S26-03 | Crossroads | 2025-10-13 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004417 | 72800 | 364 | 200 | PR-S01-03 | Prairie | 2025-10-13 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004418 | 4350 | 50 | 87 | CR-S16-03 | Crossroads | 2025-10-13 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-004419 | 200 | 1 | 200 | PR-S18-01 | Prairie | 2025-10-13 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004420 | 44600 | 1784 | 25 | CR-S04-01 | Crossroads | 2025-10-13 | 17 | Animal | Substation breaker | Forced | None
OE-25-004421 | 174 | 1 | 174 | BY-S15-02 | Bayou | 2025-10-13 | 18 | Unknown | Transformer fuse | Forced | None
OE-25-004422 | 93520 | 835 | 112 | BY-S17-03 | Bayou | 2025-10-13 | 22 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-004423 | 63720 | 1080 | 59 | BY-S15-02 | Bayou | 2025-10-14 | 2 | Vegetation | Feeder recloser | Forced | None
OE-25-004424 | 1976 | 13 | 152 | CR-S05-02 | Crossroads | 2025-10-14 | 3 | Vegetation | Transformer fuse | Forced | None
OE-25-004425 | 12936 | 154 | 84 | PR-S09-01 | Prairie | 2025-10-14 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004426 | 5681 | 23 | 247 | CR-S22-03 | Crossroads | 2025-10-14 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004427 | 6780 | 60 | 113 | PR-S08-02 | Prairie | 2025-10-14 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004428 | 1104 | 4 | 276 | PR-S11-03 | Prairie | 2025-10-14 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004429 | 2480 | 8 | 310 | BY-S09-04 | Bayou | 2025-10-14 | 11 | Animal | Transformer fuse | Forced | None
OE-25-004430 | 15540 | 105 | 148 | PR-S09-01 | Prairie | 2025-10-14 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004431 | 129375 | 575 | 225 | CR-S08-01 | Crossroads | 2025-10-14 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004432 | 480 | 5 | 96 | CR-S09-01 | Crossroads | 2025-10-14 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004433 | 324 | 2 | 162 | HB-S18-02 | Harbor | 2025-10-14 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004434 | 98256 | 712 | 138 | PR-S11-02 | Prairie | 2025-10-14 | 16 | Animal | Feeder recloser | Forced | None
OE-25-004435 | 2616 | 12 | 218 | PR-S18-02 | Prairie | 2025-10-14 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004436 | 1792 | 14 | 128 | CR-S20-05 | Crossroads | 2025-10-14 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-004437 | 1860 | 30 | 62 | CR-S06-02 | Crossroads | 2025-10-14 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004438 | 66550 | 275 | 242 | CR-S12-02 | Crossroads | 2025-10-14 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004439 | 22836 | 346 | 66 | BY-S28-03 | Bayou | 2025-10-14 | 23 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004440 | 648 | 9 | 72 | BY-S06-02 | Bayou | 2025-10-15 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004441 | 7575 | 75 | 101 | PR-S05-02 | Prairie | 2025-10-15 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004442 | 350 | 2 | 175 | BY-S08-01 | Bayou | 2025-10-15 | 11 | Animal | Transformer fuse | Forced | None
OE-25-004443 | 13439 | 151 | 89 | BY-S23-05 | Bayou | 2025-10-15 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-25-004444 | 8876 | 317 | 28 | PR-S14-02 | Prairie | 2025-10-15 | 15 | Animal | Feeder recloser | Forced | None
OE-25-004445 | 3000 | 25 | 120 | BY-S24-01 | Bayou | 2025-10-15 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-004446 | 14440 | 722 | 20 | PR-S18-04 | Prairie | 2025-10-15 | 21 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004447 | 1416 | 12 | 118 | BY-S02-01 | Bayou | 2025-10-15 | 23 | Animal | Transformer fuse | Forced | None
OE-25-004448 | 896 | 14 | 64 | CR-S16-06 | Crossroads | 2025-10-16 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004449 | 37788 | 201 | 188 | BY-S06-03 | Bayou | 2025-10-16 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-004450 | 2314 | 13 | 178 | BY-S14-01 | Bayou | 2025-10-16 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004451 | 1778 | 14 | 127 | CR-S01-03 | Crossroads | 2025-10-16 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004452 | 239355 | 985 | 243 | BY-S29-01 | Bayou | 2025-10-16 | 9 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-004453 | 6270 | 55 | 114 | CR-S29-03 | Crossroads | 2025-10-16 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004454 | 4061 | 31 | 131 | PR-S01-04 | Prairie | 2025-10-16 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004455 | 188246 | 3086 | 61 | BY-S15-02 | Bayou | 2025-10-16 | 12 | Equipment - overhead | Substation breaker | Forced | None
OE-25-004456 | 24570 | 234 | 105 | BY-S21-01 | Bayou | 2025-10-16 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004457 | 816 | 8 | 102 | BY-S16-05 | Bayou | 2025-10-16 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004458 | 80234 | 1042 | 77 | CR-S04-02 | Crossroads | 2025-10-16 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004459 | 900 | 9 | 100 | CR-S22-01 | Crossroads | 2025-10-16 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004460 | 4100 | 41 | 100 | HB-S05-05 | Harbor | 2025-10-16 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004461 | 24112 | 176 | 137 | PR-S19-02 | Prairie | 2025-10-16 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004462 | 3825 | 45 | 85 | BY-S24-01 | Bayou | 2025-10-16 | 18 | Unknown | Lateral fuse | Forced | None
OE-25-004463 | 11616 | 48 | 242 | PR-S19-05 | Prairie | 2025-10-16 | 18 | Animal | Lateral fuse | Forced | None
OE-25-004464 | 21423 | 111 | 193 | BY-S05-01 | Bayou | 2025-10-16 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004465 | 14877 | 87 | 171 | BY-S05-02 | Bayou | 2025-10-16 | 21 | Vegetation | Lateral fuse | Forced | None
OE-25-004466 | 3852 | 9 | 428 | PR-S17-01 | Prairie | 2025-10-16 | 21 | Unknown | Transformer fuse | Forced | None
OE-25-004467 | 14130 | 90 | 157 | HB-S11-03 | Harbor | 2025-10-17 | 5 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004468 | 58374 | 414 | 141 | BY-S15-02 | Bayou | 2025-10-17 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-25-004469 | 395 | 5 | 79 | CR-S01-01 | Crossroads | 2025-10-17 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004470 | 7693 | 157 | 49 | CR-S27-02 | Crossroads | 2025-10-17 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004471 | 2424 | 12 | 202 | CR-S10-03 | Crossroads | 2025-10-17 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004472 | 7360 | 80 | 92 | BY-S29-02 | Bayou | 2025-10-17 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004473 | 37195 | 173 | 215 | BY-S07-06 | Bayou | 2025-10-17 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004474 | 27448 | 146 | 188 | BY-S23-03 | Bayou | 2025-10-17 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004475 | 552 | 6 | 92 | HB-S11-01 | Harbor | 2025-10-17 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004476 | 7182 | 57 | 126 | BY-S22-02 | Bayou | 2025-10-17 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004477 | 25917 | 489 | 53 | PR-S19-01 | Prairie | 2025-10-17 | 18 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004478 | 14105 | 91 | 155 | PR-S13-05 | Prairie | 2025-10-17 | 19 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004479 | 592 | 4 | 148 | BY-S26-03 | Bayou | 2025-10-18 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004480 | 13604 | 179 | 76 | CR-S05-05 | Crossroads | 2025-10-18 | 11 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004481 | 3870 | 43 | 90 | CR-S10-03 | Crossroads | 2025-10-18 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-004482 | 2940 | 12 | 245 | CR-S17-03 | Crossroads | 2025-10-18 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004483 | 700 | 4 | 175 | CR-S27-02 | Crossroads | 2025-10-18 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004484 | 2422 | 14 | 173 | PR-S10-03 | Prairie | 2025-10-18 | 14 | Animal | Transformer fuse | Forced | None
OE-25-004485 | 5472 | 38 | 144 | BY-S21-05 | Bayou | 2025-10-18 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-004486 | 6215 | 55 | 113 | BY-S03-02 | Bayou | 2025-10-19 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-004487 | 14039 | 101 | 139 | PR-S11-03 | Prairie | 2025-10-19 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004488 | 824 | 8 | 103 | CR-S25-01 | Crossroads | 2025-10-19 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-004489 | 4590 | 45 | 102 | BY-S14-01 | Bayou | 2025-10-19 | 8 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004490 | 486 | 9 | 54 | BY-S09-05 | Bayou | 2025-10-19 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-25-004491 | 1065 | 15 | 71 | BY-S27-02 | Bayou | 2025-10-19 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004492 | 1639 | 11 | 149 | HB-S10-01 | Harbor | 2025-10-19 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004493 | 4888 | 47 | 104 | HB-S08-01 | Harbor | 2025-10-19 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004494 | 2366 | 13 | 182 | BY-S05-02 | Bayou | 2025-10-19 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004495 | 188490 | 1030 | 183 | BY-S05-01 | Bayou | 2025-10-20 | 5 | Vegetation | Substation breaker | Forced | None
OE-25-004496 | 4628 | 26 | 178 | PR-S18-03 | Prairie | 2025-10-20 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004497 | 4746 | 42 | 113 | HB-S15-01 | Harbor | 2025-10-20 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004498 | 33014 | 971 | 34 | BY-S02-01 | Bayou | 2025-10-20 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-004499 | 18618 | 107 | 174 | PR-S13-03 | Prairie | 2025-10-20 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-004500 | 22780 | 68 | 335 | BY-S05-01 | Bayou | 2025-10-20 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004501 | 3410 | 11 | 310 | CR-S18-05 | Crossroads | 2025-10-20 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004502 | 1391 | 13 | 107 | PR-S04-01 | Prairie | 2025-10-20 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-004503 | 2940 | 49 | 60 | HB-S04-01 | Harbor | 2025-10-20 | 18 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004504 | 6290 | 85 | 74 | BY-S18-03 | Bayou | 2025-10-20 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004505 | 11304 | 72 | 157 | PR-S07-01 | Prairie | 2025-10-21 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004506 | 20470 | 445 | 46 | HB-S11-01 | Harbor | 2025-10-21 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004507 | 5670 | 54 | 105 | PR-S03-02 | Prairie | 2025-10-21 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004508 | 11150 | 50 | 223 | CR-S20-01 | Crossroads | 2025-10-21 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004509 | 434 | 14 | 31 | PR-S15-03 | Prairie | 2025-10-21 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004510 | 26875 | 1075 | 25 | CR-S14-02 | Crossroads | 2025-10-21 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004511 | 64152 | 264 | 243 | BY-S01-02 | Bayou | 2025-10-21 | 16 | Vegetation | IGSD-isolated section | Forced | None
OE-25-004512 | 12180 | 87 | 140 | BY-S27-03 | Bayou | 2025-10-22 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-25-004513 | 1765 | 5 | 353 | PR-S03-05 | Prairie | 2025-10-22 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004514 | 128271 | 1859 | 69 | BY-S15-02 | Bayou | 2025-10-22 | 8 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004515 | 21357 | 339 | 63 | PR-S13-03 | Prairie | 2025-10-22 | 9 | Vegetation | Feeder recloser | Forced | None
OE-25-004516 | 1644 | 12 | 137 | HB-S08-05 | Harbor | 2025-10-22 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-004517 | 2786 | 14 | 199 | BY-S06-02 | Bayou | 2025-10-22 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004518 | 10106 | 62 | 163 | BY-S17-04 | Bayou | 2025-10-22 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004519 | 12804 | 97 | 132 | PR-S14-03 | Prairie | 2025-10-22 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004520 | 5304 | 39 | 136 | BY-S25-05 | Bayou | 2025-10-22 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004521 | 917 | 7 | 131 | HB-S15-02 | Harbor | 2025-10-22 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004522 | 12827 | 127 | 101 | CR-S19-01 | Crossroads | 2025-10-23 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004523 | 11730 | 170 | 69 | PR-S12-02 | Prairie | 2025-10-23 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004524 | 3100 | 20 | 155 | CR-S05-04 | Crossroads | 2025-10-23 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004525 | 848 | 16 | 53 | CR-S21-03 | Crossroads | 2025-10-23 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004526 | 24624 | 144 | 171 | BY-S24-01 | Bayou | 2025-10-23 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004527 | 48024 | 174 | 276 | PR-S13-03 | Prairie | 2025-10-23 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004528 | 585 | 13 | 45 | CR-S17-02 | Crossroads | 2025-10-23 | 23 | Weather - wind | Transformer fuse | Forced | None
OE-25-004529 | 29529 | 153 | 193 | BY-S29-03 | Bayou | 2025-10-24 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004530 | 1984 | 16 | 124 | BY-S21-02 | Bayou | 2025-10-24 | 8 | Animal | Lateral fuse | Forced | None
OE-25-004531 | 1815 | 11 | 165 | CR-S24-04 | Crossroads | 2025-10-24 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-25-004532 | 32400 | 450 | 72 | HB-S01-01 | Harbor | 2025-10-24 | 8 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-004533 | 2112 | 11 | 192 | CR-S32-05 | Crossroads | 2025-10-24 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004534 | 2550 | 10 | 255 | HB-S15-02 | Harbor | 2025-10-24 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-004535 | 695 | 5 | 139 | CR-S06-02 | Crossroads | 2025-10-24 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004536 | 23001 | 697 | 33 | PR-S16-05 | Prairie | 2025-10-24 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-004537 | 153720 | 3660 | 42 | CR-S21-03 | Crossroads | 2025-10-24 | 13 | Weather - wind | Substation breaker | Forced | None
OE-25-004538 | 54112 | 356 | 152 | BY-S03-01 | Bayou | 2025-10-24 | 14 | Animal | Lateral fuse | Forced | None
OE-25-004539 | 216 | 3 | 72 | CR-S15-03 | Crossroads | 2025-10-24 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004540 | 2652 | 39 | 68 | BY-S13-04 | Bayou | 2025-10-24 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-004541 | 28090 | 53 | 530 | PR-S02-03 | Prairie | 2025-10-24 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004542 | 1288 | 8 | 161 | BY-S25-04 | Bayou | 2025-10-24 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-004543 | 73920 | 1848 | 40 | HB-S17-03 | Harbor | 2025-10-24 | 22 | Animal | Substation breaker | Forced | None
OE-25-004544 | 102 | 1 | 102 | HB-S17-03 | Harbor | 2025-10-25 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004545 | 13483 | 97 | 139 | BY-S07-03 | Bayou | 2025-10-25 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004546 | 13625 | 545 | 25 | BY-S13-02 | Bayou | 2025-10-25 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-004547 | 381 | 3 | 127 | HB-S16-04 | Harbor | 2025-10-25 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004548 | 36735 | 395 | 93 | PR-S19-04 | Prairie | 2025-10-25 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-25-004549 | 240 | 4 | 60 | BY-S09-02 | Bayou | 2025-10-25 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-004550 | 14742 | 162 | 91 | HB-S16-04 | Harbor | 2025-10-25 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-004551 | 11918 | 101 | 118 | CR-S05-01 | Crossroads | 2025-10-25 | 22 | Animal | Lateral fuse | Forced | None
OE-25-004552 | 1764 | 14 | 126 | PR-S05-02 | Prairie | 2025-10-25 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004553 | 38718 | 162 | 239 | HB-S11-03 | Harbor | 2025-10-26 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004554 | 680 | 10 | 68 | CR-S08-06 | Crossroads | 2025-10-26 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004555 | 2808 | 13 | 216 | CR-S27-04 | Crossroads | 2025-10-26 | 10 | Animal | Transformer fuse | Forced | None
OE-25-004556 | 57081 | 359 | 159 | PR-S01-01 | Prairie | 2025-10-26 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004557 | 8184 | 93 | 88 | CR-S09-02 | Crossroads | 2025-10-26 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004558 | 264 | 3 | 88 | BY-S04-01 | Bayou | 2025-10-26 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004559 | 18542 | 254 | 73 | PR-S14-01 | Prairie | 2025-10-26 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-25-004560 | 453 | 3 | 151 | CR-S06-02 | Crossroads | 2025-10-26 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004561 | 1442 | 7 | 206 | BY-S17-01 | Bayou | 2025-10-26 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004562 | 1092 | 13 | 84 | HB-S06-01 | Harbor | 2025-10-26 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004563 | 26235 | 159 | 165 | BY-S13-03 | Bayou | 2025-10-26 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004564 | 804 | 12 | 67 | HB-S02-01 | Harbor | 2025-10-26 | 19 | Animal | Transformer fuse | Forced | None
OE-25-004565 | 3880 | 40 | 97 | PR-S10-01 | Prairie | 2025-10-26 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004566 | 1326 | 6 | 221 | PR-S18-02 | Prairie | 2025-10-27 | 0 | Animal | Transformer fuse | Forced | None
OE-25-004567 | 5760 | 384 | 15 | BY-S18-06 | Bayou | 2025-10-27 | 2 | Unknown | Feeder recloser | Forced | None
OE-25-004568 | 8576 | 67 | 128 | BY-S25-05 | Bayou | 2025-10-27 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-004569 | 1104 | 12 | 92 | HB-S17-01 | Harbor | 2025-10-27 | 13 | Animal | Transformer fuse | Forced | None
OE-25-004570 | 832 | 13 | 64 | CR-S32-01 | Crossroads | 2025-10-27 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-004571 | 412 | 4 | 103 | CR-S15-01 | Crossroads | 2025-10-27 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004572 | 9990 | 90 | 111 | HB-S10-02 | Harbor | 2025-10-27 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004573 | 351 | 3 | 117 | CR-S05-02 | Crossroads | 2025-10-28 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-004574 | 194 | 2 | 97 | BY-S17-01 | Bayou | 2025-10-28 | 6 | Unknown | Transformer fuse | Forced | None
OE-25-004575 | 1820 | 13 | 140 | BY-S30-01 | Bayou | 2025-10-28 | 8 | Animal | Transformer fuse | Forced | None
OE-25-004576 | 828 | 3 | 276 | CR-S19-03 | Crossroads | 2025-10-28 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-004577 | 1200 | 8 | 150 | CR-S21-01 | Crossroads | 2025-10-28 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-004578 | 9350 | 50 | 187 | PR-S20-04 | Prairie | 2025-10-28 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004579 | 9022 | 347 | 26 | CR-S11-02 | Crossroads | 2025-10-28 | 12 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004580 | 24375 | 325 | 75 | HB-S15-03 | Harbor | 2025-10-28 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-004581 | 6465 | 15 | 431 | PR-S16-04 | Prairie | 2025-10-28 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004582 | 23200 | 580 | 40 | PR-S06-01 | Prairie | 2025-10-28 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004583 | 395 | 5 | 79 | CR-S18-04 | Crossroads | 2025-10-29 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004584 | 22120 | 140 | 158 | CR-S21-03 | Crossroads | 2025-10-29 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004585 | 15696 | 144 | 109 | PR-S05-02 | Prairie | 2025-10-29 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004586 | 1120 | 8 | 140 | CR-S19-03 | Crossroads | 2025-10-29 | 11 | Unknown | Transformer fuse | Forced | None
OE-25-004587 | 26167 | 137 | 191 | CR-S05-01 | Crossroads | 2025-10-29 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004588 | 10032 | 228 | 44 | HB-S19-01 | Harbor | 2025-10-29 | 13 | Vegetation | IGSD-isolated section | Forced | None
OE-25-004589 | 278 | 2 | 139 | CR-S21-03 | Crossroads | 2025-10-29 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-004590 | 45936 | 1044 | 44 | CR-S22-02 | Crossroads | 2025-10-29 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004591 | 34440 | 246 | 140 | BY-S19-03 | Bayou | 2025-10-29 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004592 | 4416 | 64 | 69 | HB-S19-03 | Harbor | 2025-10-29 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004593 | 768 | 8 | 96 | HB-S17-01 | Harbor | 2025-10-29 | 17 | Animal | Transformer fuse | Forced | None
OE-25-004594 | 8096 | 46 | 176 | CR-S13-03 | Crossroads | 2025-10-29 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004595 | 16675 | 145 | 115 | BY-S16-04 | Bayou | 2025-10-29 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-004596 | 71 | 1 | 71 | CR-S11-01 | Crossroads | 2025-10-29 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004597 | 1518 | 11 | 138 | CR-S25-04 | Crossroads | 2025-10-29 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004598 | 1612 | 26 | 62 | BY-S02-02 | Bayou | 2025-10-30 | 5 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004599 | 30597 | 329 | 93 | PR-S20-03 | Prairie | 2025-10-30 | 5 | Weather - wind | Feeder recloser | Forced | None
OE-25-004600 | 1790 | 5 | 358 | CR-S25-01 | Crossroads | 2025-10-30 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004601 | 1210 | 10 | 121 | CR-S27-04 | Crossroads | 2025-10-30 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004602 | 1496 | 17 | 88 | BY-S10-01 | Bayou | 2025-10-30 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004603 | 864 | 9 | 96 | CR-S05-03 | Crossroads | 2025-10-30 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004604 | 1467 | 9 | 163 | PR-S13-05 | Prairie | 2025-10-30 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004605 | 63750 | 1250 | 51 | PR-S18-05 | Prairie | 2025-10-30 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004606 | 660 | 6 | 110 | BY-S16-05 | Bayou | 2025-10-30 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-004607 | 1085 | 5 | 217 | BY-S03-01 | Bayou | 2025-10-31 | 2 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004608 | 2496 | 13 | 192 | BY-S21-01 | Bayou | 2025-10-31 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004609 | 59109 | 969 | 61 | CR-S14-01 | Crossroads | 2025-10-31 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004610 | 77 | 1 | 77 | CR-S22-02 | Crossroads | 2025-10-31 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004611 | 17535 | 167 | 105 | PR-S17-02 | Prairie | 2025-10-31 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004612 | 128180 | 3770 | 34 | CR-S21-03 | Crossroads | 2025-10-31 | 14 | Equipment - underground | Substation breaker | Forced | None
OE-25-004613 | 1624 | 7 | 232 | PR-S10-03 | Prairie | 2025-10-31 | 17 | Animal | Transformer fuse | Forced | None
OE-25-004614 | 37098 | 458 | 81 | BY-S03-02 | Bayou | 2025-10-31 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004615 | 1140 | 10 | 114 | BY-S09-03 | Bayou | 2025-10-31 | 19 | Animal | Transformer fuse | Forced | None
OE-25-004616 | 198 | 1 | 198 | BY-S13-05 | Bayou | 2025-10-31 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004617 | 2960 | 40 | 74 | CR-S28-03 | Crossroads | 2025-10-31 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004618 | 12221 | 101 | 121 | HB-S14-03 | Harbor | 2025-10-31 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004619 | 3332 | 14 | 238 | HB-S20-05 | Harbor | 2025-10-31 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004620 | 62118 | 1479 | 42 | HB-S10-03 | Harbor | 2025-11-01 | 6 | Vegetation | IGSD-isolated section | Forced | None
OE-25-004621 | 19470 | 354 | 55 | BY-S10-05 | Bayou | 2025-11-01 | 8 | Vegetation | Feeder recloser | Forced | None
OE-25-004622 | 689 | 13 | 53 | BY-S29-03 | Bayou | 2025-11-01 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-004623 | 1518 | 11 | 138 | BY-S21-05 | Bayou | 2025-11-01 | 10 | Animal | Transformer fuse | Forced | None
OE-25-004624 | 1400 | 14 | 100 | PR-S20-04 | Prairie | 2025-11-01 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004625 | 174915 | 2535 | 69 | BY-S23-02 | Bayou | 2025-11-01 | 16 | Vegetation | Substation breaker | Forced | None
OE-25-004626 | 5632 | 44 | 128 | BY-S23-02 | Bayou | 2025-11-01 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-004627 | 31992 | 344 | 93 | PR-S01-06 | Prairie | 2025-11-01 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-004628 | 1196 | 4 | 299 | PR-S01-01 | Prairie | 2025-11-02 | 5 | Animal | Transformer fuse | Forced | None
OE-25-004629 | 34075 | 235 | 145 | PR-S13-03 | Prairie | 2025-11-02 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004630 | 1206 | 9 | 134 | CR-S30-03 | Crossroads | 2025-11-02 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-004631 | 8214 | 74 | 111 | HB-S01-02 | Harbor | 2025-11-02 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004632 | 4730 | 43 | 110 | HB-S03-01 | Harbor | 2025-11-02 | 11 | Animal | Lateral fuse | Forced | None
OE-25-004633 | 14137 | 67 | 211 | BY-S13-04 | Bayou | 2025-11-02 | 13 | Unknown | Lateral fuse | Forced | None
OE-25-004634 | 576 | 4 | 144 | HB-S15-03 | Harbor | 2025-11-02 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004635 | 1962 | 9 | 218 | CR-S06-03 | Crossroads | 2025-11-02 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004636 | 1771 | 11 | 161 | PR-S06-02 | Prairie | 2025-11-02 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-004637 | 1390 | 10 | 139 | HB-S16-03 | Harbor | 2025-11-02 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004638 | 832 | 13 | 64 | HB-S20-04 | Harbor | 2025-11-02 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-004639 | 7006 | 62 | 113 | CR-S23-02 | Crossroads | 2025-11-02 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004640 | 945 | 7 | 135 | CR-S13-06 | Crossroads | 2025-11-02 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004641 | 26568 | 492 | 54 | PR-S08-03 | Prairie | 2025-11-02 | 20 | Vegetation | Feeder recloser | Forced | None
OE-25-004642 | 2166 | 38 | 57 | BY-S18-06 | Bayou | 2025-11-03 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004643 | 5238 | 27 | 194 | CR-S32-03 | Crossroads | 2025-11-03 | 8 | Unknown | Lateral fuse | Forced | None
OE-25-004644 | 2862 | 54 | 53 | CR-S27-01 | Crossroads | 2025-11-03 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004645 | 25021 | 131 | 191 | BY-S10-03 | Bayou | 2025-11-03 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-004646 | 3220 | 14 | 230 | PR-S20-01 | Prairie | 2025-11-03 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004647 | 1920 | 10 | 192 | BY-S29-05 | Bayou | 2025-11-03 | 17 | Animal | Transformer fuse | Forced | None
OE-25-004648 | 66352 | 319 | 208 | BY-S09-03 | Bayou | 2025-11-04 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004649 | 32153 | 407 | 79 | CR-S04-06 | Crossroads | 2025-11-04 | 9 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-004650 | 19250 | 125 | 154 | BY-S28-03 | Bayou | 2025-11-04 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-004651 | 3510 | 39 | 90 | BY-S29-01 | Bayou | 2025-11-04 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-004652 | 744 | 8 | 93 | PR-S01-05 | Prairie | 2025-11-04 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004653 | 10956 | 132 | 83 | CR-S22-01 | Crossroads | 2025-11-04 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004654 | 1596 | 7 | 228 | HB-S16-04 | Harbor | 2025-11-04 | 15 | Animal | Transformer fuse | Forced | None
OE-25-004655 | 12864 | 201 | 64 | BY-S09-05 | Bayou | 2025-11-04 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-004656 | 3870 | 90 | 43 | BY-S03-02 | Bayou | 2025-11-04 | 18 | Unknown | Lateral fuse | Forced | None
OE-25-004657 | 485 | 5 | 97 | CR-S05-02 | Crossroads | 2025-11-04 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-25-004658 | 55322 | 199 | 278 | CR-S04-02 | Crossroads | 2025-11-04 | 23 | Vegetation | Lateral fuse | Forced | None
OE-25-004659 | 3139 | 43 | 73 | HB-S03-03 | Harbor | 2025-11-05 | 6 | Vegetation | Lateral fuse | Forced | None
OE-25-004660 | 13034 | 98 | 133 | PR-S05-02 | Prairie | 2025-11-05 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004661 | 432 | 4 | 108 | CR-S01-02 | Crossroads | 2025-11-05 | 9 | Animal | Transformer fuse | Forced | None
OE-25-004662 | 475 | 5 | 95 | HB-S09-03 | Harbor | 2025-11-05 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004663 | 53482 | 221 | 242 | HB-S02-03 | Harbor | 2025-11-05 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004664 | 7170 | 30 | 239 | BY-S13-04 | Bayou | 2025-11-05 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004665 | 1920 | 32 | 60 | BY-S23-03 | Bayou | 2025-11-05 | 12 | Animal | Lateral fuse | Forced | None
OE-25-004666 | 9856 | 64 | 154 | CR-S30-01 | Crossroads | 2025-11-05 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004667 | 52871 | 1079 | 49 | BY-S15-01 | Bayou | 2025-11-05 | 16 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004668 | 8888 | 88 | 101 | BY-S23-04 | Bayou | 2025-11-05 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004669 | 14196 | 84 | 169 | PR-S07-04 | Prairie | 2025-11-05 | 16 | Unknown | Lateral fuse | Forced | None
OE-25-004670 | 1507 | 11 | 137 | BY-S13-01 | Bayou | 2025-11-05 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004671 | 4800 | 75 | 64 | BY-S28-01 | Bayou | 2025-11-05 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004672 | 3900 | 13 | 300 | PR-S01-02 | Prairie | 2025-11-05 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-004673 | 31882 | 839 | 38 | HB-S05-01 | Harbor | 2025-11-05 | 18 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004674 | 26280 | 365 | 72 | BY-S26-01 | Bayou | 2025-11-05 | 19 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004675 | 4650 | 30 | 155 | CR-S29-02 | Crossroads | 2025-11-05 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004676 | 9456 | 48 | 197 | PR-S16-05 | Prairie | 2025-11-06 | 1 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004677 | 27072 | 288 | 94 | CR-S24-01 | Crossroads | 2025-11-06 | 3 | Weather - wind | IGSD-isolated section | Forced | None
OE-25-004678 | 1215 | 5 | 243 | BY-S13-01 | Bayou | 2025-11-06 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-004679 | 324 | 6 | 54 | BY-S18-03 | Bayou | 2025-11-06 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004680 | 105033 | 669 | 157 | PR-S16-05 | Prairie | 2025-11-06 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004681 | 10878 | 42 | 259 | BY-S18-02 | Bayou | 2025-11-06 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004682 | 6027 | 41 | 147 | HB-S09-04 | Harbor | 2025-11-06 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004683 | 1540 | 11 | 140 | CR-S12-01 | Crossroads | 2025-11-06 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004684 | 207558 | 1774 | 117 | BY-S15-06 | Bayou | 2025-11-06 | 15 | Vegetation | Substation breaker | Forced | None
OE-25-004685 | 3069 | 11 | 279 | BY-S29-04 | Bayou | 2025-11-06 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-004686 | 432 | 6 | 72 | HB-S09-02 | Harbor | 2025-11-06 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-004687 | 4992 | 39 | 128 | CR-S14-02 | Crossroads | 2025-11-06 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004688 | 1600 | 8 | 200 | PR-S13-01 | Prairie | 2025-11-06 | 21 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004689 | 183216 | 2082 | 88 | BY-S22-04 | Bayou | 2025-11-07 | 0 | Unknown | Substation breaker | Outside cause | None
OE-25-004690 | 4134 | 39 | 106 | BY-S11-03 | Bayou | 2025-11-07 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004691 | 1260 | 14 | 90 | CR-S19-04 | Crossroads | 2025-11-07 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004692 | 270 | 2 | 135 | PR-S16-01 | Prairie | 2025-11-07 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004693 | 11856 | 104 | 114 | HB-S17-03 | Harbor | 2025-11-07 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004694 | 14442 | 87 | 166 | BY-S12-03 | Bayou | 2025-11-07 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004695 | 492 | 4 | 123 | BY-S17-04 | Bayou | 2025-11-07 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004696 | 128115 | 585 | 219 | PR-S13-06 | Prairie | 2025-11-07 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004697 | 400 | 2 | 200 | PR-S18-03 | Prairie | 2025-11-07 | 14 | Animal | Transformer fuse | Forced | None
OE-25-004698 | 1305 | 9 | 145 | CR-S07-03 | Crossroads | 2025-11-07 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004699 | 1221 | 11 | 111 | HB-S01-02 | Harbor | 2025-11-07 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004700 | 63872 | 499 | 128 | BY-S29-05 | Bayou | 2025-11-07 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-004701 | 970 | 10 | 97 | BY-S13-01 | Bayou | 2025-11-07 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004702 | 165 | 1 | 165 | PR-S07-01 | Prairie | 2025-11-07 | 22 | Animal | Transformer fuse | Forced | None
OE-25-004703 | 890 | 10 | 89 | BY-S14-02 | Bayou | 2025-11-08 | 5 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004704 | 700 | 20 | 35 | BY-S15-02 | Bayou | 2025-11-08 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-004705 | 5868 | 18 | 326 | CR-S08-06 | Crossroads | 2025-11-08 | 8 | Animal | Lateral fuse | Forced | None
OE-25-004706 | 2497 | 11 | 227 | PR-S18-03 | Prairie | 2025-11-08 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004707 | 2322 | 27 | 86 | PR-S18-05 | Prairie | 2025-11-08 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-25-004708 | 5047 | 103 | 49 | CR-S04-02 | Crossroads | 2025-11-08 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004709 | 3100 | 31 | 100 | CR-S26-03 | Crossroads | 2025-11-08 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004710 | 488 | 2 | 244 | BY-S13-03 | Bayou | 2025-11-08 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-004711 | 2034 | 6 | 339 | BY-S05-02 | Bayou | 2025-11-08 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-004712 | 1410 | 30 | 47 | PR-S04-02 | Prairie | 2025-11-08 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004713 | 4704 | 32 | 147 | PR-S18-05 | Prairie | 2025-11-08 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-004714 | 630 | 7 | 90 | BY-S12-02 | Bayou | 2025-11-08 | 18 | Animal | Transformer fuse | Forced | None
OE-25-004715 | 2556 | 18 | 142 | CR-S04-01 | Crossroads | 2025-11-08 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004716 | 262 | 2 | 131 | HB-S03-03 | Harbor | 2025-11-08 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-004717 | 4440 | 8 | 555 | PR-S15-05 | Prairie | 2025-11-09 | 0 | Animal | Transformer fuse | Forced | None
OE-25-004718 | 124960 | 1136 | 110 | PR-S13-06 | Prairie | 2025-11-09 | 8 | Equipment - overhead | Substation breaker | Forced | None
OE-25-004719 | 3212 | 44 | 73 | PR-S08-01 | Prairie | 2025-11-09 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004720 | 265 | 5 | 53 | CR-S09-02 | Crossroads | 2025-11-09 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004721 | 125760 | 1310 | 96 | PR-S15-06 | Prairie | 2025-11-09 | 15 | Weather - lightning | Substation breaker | Forced | None
OE-25-004722 | 5251 | 59 | 89 | PR-S15-06 | Prairie | 2025-11-09 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-25-004723 | 62748 | 126 | 498 | BY-S07-05 | Bayou | 2025-11-09 | 22 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004724 | 27416 | 184 | 149 | PR-S18-06 | Prairie | 2025-11-10 | 6 | Vegetation | Lateral fuse | Forced | None
OE-25-004725 | 963 | 9 | 107 | BY-S05-01 | Bayou | 2025-11-10 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-004726 | 4048 | 44 | 92 | BY-S27-06 | Bayou | 2025-11-10 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-004727 | 1235 | 13 | 95 | CR-S10-01 | Crossroads | 2025-11-10 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004728 | 2690 | 10 | 269 | CR-S11-01 | Crossroads | 2025-11-10 | 14 | Animal | Transformer fuse | Forced | None
OE-25-004729 | 72360 | 1080 | 67 | CR-S30-02 | Crossroads | 2025-11-10 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004730 | 2366 | 26 | 91 | PR-S12-02 | Prairie | 2025-11-10 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004731 | 16566 | 753 | 22 | BY-S29-02 | Bayou | 2025-11-10 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-004732 | 3432 | 24 | 143 | CR-S02-03 | Crossroads | 2025-11-10 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-25-004733 | 257 | 1 | 257 | BY-S02-01 | Bayou | 2025-11-10 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004734 | 18360 | 120 | 153 | PR-S10-03 | Prairie | 2025-11-11 | 5 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004735 | 5773 | 23 | 251 | CR-S08-06 | Crossroads | 2025-11-11 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004736 | 7950 | 50 | 159 | HB-S10-03 | Harbor | 2025-11-11 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004737 | 920 | 10 | 92 | HB-S18-04 | Harbor | 2025-11-11 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004738 | 7821 | 99 | 79 | HB-S18-01 | Harbor | 2025-11-11 | 9 | Animal | Lateral fuse | Forced | None
OE-25-004739 | 21105 | 469 | 45 | HB-S03-03 | Harbor | 2025-11-11 | 14 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-004740 | 54520 | 232 | 235 | PR-S06-03 | Prairie | 2025-11-11 | 14 | Equipment - underground | IGSD-isolated section | Forced | None
OE-25-004741 | 1378 | 13 | 106 | HB-S16-01 | Harbor | 2025-11-11 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004742 | 240 | 3 | 80 | BY-S30-01 | Bayou | 2025-11-11 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-25-004743 | 981 | 9 | 109 | PR-S11-03 | Prairie | 2025-11-11 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-004744 | 520 | 4 | 130 | PR-S07-04 | Prairie | 2025-11-11 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004745 | 1888 | 8 | 236 | CR-S11-01 | Crossroads | 2025-11-11 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004746 | 312 | 2 | 156 | BY-S18-07 | Bayou | 2025-11-12 | 5 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004747 | 2016 | 9 | 224 | PR-S18-04 | Prairie | 2025-11-12 | 5 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004748 | 61040 | 545 | 112 | PR-S09-01 | Prairie | 2025-11-12 | 8 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004749 | 1560 | 10 | 156 | CR-S01-03 | Crossroads | 2025-11-12 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-25-004750 | 2849 | 11 | 259 | PR-S15-03 | Prairie | 2025-11-12 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004751 | 11760 | 80 | 147 | PR-S05-02 | Prairie | 2025-11-12 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004752 | 2635 | 17 | 155 | PR-S15-05 | Prairie | 2025-11-12 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004753 | 3094 | 13 | 238 | BY-S24-01 | Bayou | 2025-11-12 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004754 | 6336 | 32 | 198 | CR-S13-04 | Crossroads | 2025-11-12 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004755 | 286 | 2 | 143 | BY-S18-03 | Bayou | 2025-11-12 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004756 | 8970 | 65 | 138 | CR-S14-01 | Crossroads | 2025-11-12 | 18 | Animal | Lateral fuse | Forced | None
OE-25-004757 | 9234 | 54 | 171 | CR-S25-01 | Crossroads | 2025-11-12 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004758 | 31820 | 370 | 86 | PR-S13-02 | Prairie | 2025-11-12 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004759 | 47712 | 213 | 224 | BY-S22-03 | Bayou | 2025-11-13 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004760 | 25564 | 581 | 44 | CR-S25-06 | Crossroads | 2025-11-13 | 9 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004761 | 8137 | 79 | 103 | CR-S26-02 | Crossroads | 2025-11-13 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004762 | 1122 | 11 | 102 | CR-S25-03 | Crossroads | 2025-11-13 | 13 | Vegetation | Transformer fuse | Forced | None
OE-25-004763 | 2870 | 35 | 82 | PR-S12-03 | Prairie | 2025-11-13 | 13 | Animal | Lateral fuse | Forced | None
OE-25-004764 | 5694 | 73 | 78 | CR-S16-02 | Crossroads | 2025-11-13 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004765 | 76048 | 776 | 98 | HB-S05-03 | Harbor | 2025-11-13 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-004766 | 33139 | 1069 | 31 | BY-S13-05 | Bayou | 2025-11-13 | 16 | Vegetation | Feeder recloser | Forced | None
OE-25-004767 | 1285 | 5 | 257 | BY-S16-03 | Bayou | 2025-11-13 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004768 | 882 | 14 | 63 | BY-S02-01 | Bayou | 2025-11-13 | 19 | Animal | Transformer fuse | Forced | None
OE-25-004769 | 474 | 3 | 158 | BY-S15-04 | Bayou | 2025-11-13 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-004770 | 2958 | 29 | 102 | CR-S17-03 | Crossroads | 2025-11-14 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004771 | 2725 | 5 | 545 | BY-S20-01 | Bayou | 2025-11-14 | 2 | Weather - wind | Lateral fuse | Forced | None
OE-25-004772 | 940 | 10 | 94 | HB-S19-03 | Harbor | 2025-11-14 | 10 | Animal | Transformer fuse | Forced | None
OE-25-004773 | 16590 | 79 | 210 | HB-S03-03 | Harbor | 2025-11-14 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004774 | 9360 | 104 | 90 | CR-S09-02 | Crossroads | 2025-11-14 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004775 | 12382 | 82 | 151 | HB-S05-03 | Harbor | 2025-11-14 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004776 | 378 | 3 | 126 | PR-S12-01 | Prairie | 2025-11-14 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004777 | 1728 | 12 | 144 | BY-S07-03 | Bayou | 2025-11-14 | 23 | Animal | Transformer fuse | Forced | None
OE-25-004778 | 7236 | 67 | 108 | CR-S13-03 | Crossroads | 2025-11-15 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-004779 | 35112 | 114 | 308 | CR-S29-03 | Crossroads | 2025-11-15 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004780 | 20700 | 225 | 92 | HB-S06-04 | Harbor | 2025-11-15 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004781 | 8450 | 338 | 25 | HB-S07-05 | Harbor | 2025-11-15 | 21 | Unknown | Feeder recloser | Forced | None
OE-25-004782 | 861 | 7 | 123 | CR-S08-02 | Crossroads | 2025-11-16 | 0 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004783 | 85312 | 496 | 172 | CR-S30-02 | Crossroads | 2025-11-16 | 7 | Weather - wind | Feeder recloser | Forced | None
OE-25-004784 | 36480 | 640 | 57 | BY-S02-01 | Bayou | 2025-11-16 | 9 | Vegetation | Feeder recloser | Forced | None
OE-25-004785 | 1305 | 9 | 145 | BY-S25-04 | Bayou | 2025-11-16 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004786 | 121402 | 1202 | 101 | CR-S22-01 | Crossroads | 2025-11-16 | 9 | Vegetation | Feeder recloser | Forced | None
OE-25-004787 | 31155 | 155 | 201 | PR-S07-06 | Prairie | 2025-11-16 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-004788 | 104 | 1 | 104 | CR-S18-04 | Crossroads | 2025-11-16 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004789 | 55770 | 165 | 338 | PR-S20-04 | Prairie | 2025-11-16 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004790 | 520 | 5 | 104 | HB-S01-02 | Harbor | 2025-11-16 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-004791 | 75 | 1 | 75 | HB-S15-02 | Harbor | 2025-11-16 | 14 | Animal | Transformer fuse | Forced | None
OE-25-004792 | 3990 | 14 | 285 | HB-S17-03 | Harbor | 2025-11-16 | 15 | Animal | Transformer fuse | Forced | None
OE-25-004793 | 1683 | 11 | 153 | BY-S11-01 | Bayou | 2025-11-16 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-004794 | 420 | 3 | 140 | BY-S13-01 | Bayou | 2025-11-16 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004795 | 248 | 1 | 248 | HB-S06-05 | Harbor | 2025-11-16 | 20 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004796 | 2380 | 10 | 238 | PR-S01-03 | Prairie | 2025-11-16 | 23 | Vegetation | Transformer fuse | Forced | None
OE-25-004797 | 20330 | 95 | 214 | PR-S06-02 | Prairie | 2025-11-17 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-004798 | 13120 | 80 | 164 | BY-S11-02 | Bayou | 2025-11-17 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004799 | 318 | 6 | 53 | HB-S02-01 | Harbor | 2025-11-17 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004800 | 3840 | 48 | 80 | HB-S17-01 | Harbor | 2025-11-17 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004801 | 2448 | 17 | 144 | CR-S32-03 | Crossroads | 2025-11-17 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004802 | 5929 | 77 | 77 | BY-S03-03 | Bayou | 2025-11-17 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-004803 | 82512 | 1719 | 48 | BY-S16-02 | Bayou | 2025-11-17 | 18 | Vegetation | Substation breaker | Forced | None
OE-25-004804 | 1596 | 14 | 114 | BY-S16-06 | Bayou | 2025-11-17 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004805 | 803 | 11 | 73 | PR-S13-04 | Prairie | 2025-11-17 | 22 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004806 | 31140 | 180 | 173 | BY-S01-01 | Bayou | 2025-11-18 | 3 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004807 | 6800 | 34 | 200 | HB-S14-04 | Harbor | 2025-11-18 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004808 | 81312 | 1694 | 48 | CR-S22-03 | Crossroads | 2025-11-18 | 10 | Weather - wind | Feeder recloser | Forced | None
OE-25-004809 | 43632 | 1212 | 36 | CR-S31-01 | Crossroads | 2025-11-18 | 10 | Vegetation | Feeder recloser | Forced | None
OE-25-004810 | 31809 | 461 | 69 | HB-S15-01 | Harbor | 2025-11-18 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004811 | 9834 | 447 | 22 | HB-S18-03 | Harbor | 2025-11-18 | 17 | Unknown | IGSD-isolated section | Forced | None
OE-25-004812 | 1908 | 12 | 159 | PR-S09-02 | Prairie | 2025-11-18 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004813 | 2587 | 13 | 199 | PR-S18-04 | Prairie | 2025-11-18 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004814 | 1242 | 9 | 138 | HB-S15-02 | Harbor | 2025-11-19 | 2 | Unknown | Transformer fuse | Forced | None
OE-25-004815 | 2436 | 29 | 84 | BY-S17-04 | Bayou | 2025-11-19 | 4 | Vegetation | Lateral fuse | Forced | None
OE-25-004816 | 6369 | 33 | 193 | PR-S20-04 | Prairie | 2025-11-19 | 6 | Vegetation | Lateral fuse | Forced | None
OE-25-004817 | 13359 | 73 | 183 | HB-S11-01 | Harbor | 2025-11-19 | 12 | Animal | Lateral fuse | Forced | None
OE-25-004818 | 750 | 10 | 75 | PR-S18-03 | Prairie | 2025-11-19 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-25-004819 | 2198 | 14 | 157 | HB-S10-03 | Harbor | 2025-11-19 | 13 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004820 | 46956 | 258 | 182 | CR-S07-03 | Crossroads | 2025-11-19 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004821 | 2912 | 13 | 224 | HB-S06-04 | Harbor | 2025-11-19 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004822 | 3594 | 6 | 599 | BY-S03-02 | Bayou | 2025-11-19 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-004823 | 28013 | 257 | 109 | BY-S24-03 | Bayou | 2025-11-19 | 18 | Vegetation | Feeder recloser | Forced | None
OE-25-004824 | 544 | 8 | 68 | CR-S30-04 | Crossroads | 2025-11-20 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004825 | 1204 | 14 | 86 | BY-S11-01 | Bayou | 2025-11-20 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004826 | 85674 | 393 | 218 | CR-S06-02 | Crossroads | 2025-11-20 | 8 | Weather - lightning | IGSD-isolated section | Forced | None
OE-25-004827 | 4392 | 72 | 61 | HB-S05-01 | Harbor | 2025-11-20 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004828 | 1956 | 12 | 163 | HB-S14-02 | Harbor | 2025-11-20 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004829 | 11830 | 91 | 130 | CR-S19-01 | Crossroads | 2025-11-20 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004830 | 6909 | 49 | 141 | HB-S20-03 | Harbor | 2025-11-20 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004831 | 12432 | 111 | 112 | CR-S16-03 | Crossroads | 2025-11-20 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004832 | 1008 | 8 | 126 | HB-S07-03 | Harbor | 2025-11-20 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004833 | 5883 | 37 | 159 | HB-S11-01 | Harbor | 2025-11-20 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004834 | 540 | 6 | 90 | CR-S28-02 | Crossroads | 2025-11-20 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004835 | 2626 | 13 | 202 | HB-S12-03 | Harbor | 2025-11-20 | 17 | Unknown | Transformer fuse | Forced | None
OE-25-004836 | 1022 | 7 | 146 | CR-S16-04 | Crossroads | 2025-11-20 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-25-004837 | 585 | 5 | 117 | CR-S09-04 | Crossroads | 2025-11-21 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-25-004838 | 1116 | 3 | 372 | BY-S08-02 | Bayou | 2025-11-21 | 3 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004839 | 2839 | 17 | 167 | CR-S32-03 | Crossroads | 2025-11-21 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004840 | 5995 | 55 | 109 | BY-S17-01 | Bayou | 2025-11-21 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-004841 | 6201 | 53 | 117 | BY-S19-03 | Bayou | 2025-11-21 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004842 | 846 | 9 | 94 | PR-S15-01 | Prairie | 2025-11-21 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004843 | 4394 | 26 | 169 | BY-S25-03 | Bayou | 2025-11-21 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004844 | 3712 | 29 | 128 | BY-S07-02 | Bayou | 2025-11-21 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-004845 | 770 | 7 | 110 | HB-S10-01 | Harbor | 2025-11-21 | 15 | Animal | Transformer fuse | Forced | None
OE-25-004846 | 273 | 1 | 273 | HB-S11-01 | Harbor | 2025-11-21 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-25-004847 | 1428 | 12 | 119 | PR-S15-06 | Prairie | 2025-11-21 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004848 | 37100 | 700 | 53 | BY-S07-02 | Bayou | 2025-11-21 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-004849 | 19110 | 98 | 195 | CR-S24-02 | Crossroads | 2025-11-21 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004850 | 1200 | 10 | 120 | CR-S01-02 | Crossroads | 2025-11-21 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004851 | 472 | 4 | 118 | CR-S05-03 | Crossroads | 2025-11-21 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004852 | 870 | 10 | 87 | CR-S31-01 | Crossroads | 2025-11-22 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004853 | 8015 | 35 | 229 | BY-S27-01 | Bayou | 2025-11-22 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004854 | 3135 | 11 | 285 | PR-S19-02 | Prairie | 2025-11-22 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-004855 | 816 | 6 | 136 | CR-S32-04 | Crossroads | 2025-11-22 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004856 | 33375 | 125 | 267 | PR-S19-04 | Prairie | 2025-11-22 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004857 | 42607 | 137 | 311 | HB-S05-04 | Harbor | 2025-11-22 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004858 | 1830 | 10 | 183 | HB-S06-01 | Harbor | 2025-11-22 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004859 | 40299 | 399 | 101 | PR-S15-03 | Prairie | 2025-11-22 | 14 | Weather - lightning | Feeder recloser | Forced | None
OE-25-004860 | 7742 | 98 | 79 | PR-S17-01 | Prairie | 2025-11-22 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004861 | 13662 | 66 | 207 | PR-S09-02 | Prairie | 2025-11-23 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004862 | 1596 | 7 | 228 | HB-S08-04 | Harbor | 2025-11-23 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-004863 | 4559 | 47 | 97 | BY-S29-01 | Bayou | 2025-11-23 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004864 | 1375 | 11 | 125 | BY-S23-04 | Bayou | 2025-11-23 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-004865 | 19908 | 553 | 36 | CR-S26-03 | Crossroads | 2025-11-23 | 11 | Unknown | Feeder recloser | Forced | None
OE-25-004866 | 3825 | 51 | 75 | BY-S25-04 | Bayou | 2025-11-23 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004867 | 1680 | 42 | 40 | CR-S12-01 | Crossroads | 2025-11-23 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004868 | 6342 | 42 | 151 | PR-S07-05 | Prairie | 2025-11-23 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004869 | 1908 | 9 | 212 | PR-S19-03 | Prairie | 2025-11-23 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004870 | 1141 | 7 | 163 | PR-S01-01 | Prairie | 2025-11-24 | 2 | Vegetation | Transformer fuse | Forced | None
OE-25-004871 | 83475 | 525 | 159 | PR-S03-01 | Prairie | 2025-11-24 | 6 | Vegetation | Feeder recloser | Forced | None
OE-25-004872 | 1030 | 10 | 103 | CR-S30-06 | Crossroads | 2025-11-24 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004873 | 7314 | 46 | 159 | BY-S05-02 | Bayou | 2025-11-24 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004874 | 4104 | 36 | 114 | HB-S03-03 | Harbor | 2025-11-24 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004875 | 310 | 5 | 62 | CR-S26-03 | Crossroads | 2025-11-24 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004876 | 1496 | 8 | 187 | BY-S26-02 | Bayou | 2025-11-24 | 15 | Animal | Transformer fuse | Forced | None
OE-25-004877 | 2300 | 10 | 230 | CR-S19-02 | Crossroads | 2025-11-24 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-004878 | 57772 | 404 | 143 | PR-S11-03 | Prairie | 2025-11-24 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004879 | 790 | 5 | 158 | BY-S08-02 | Bayou | 2025-11-24 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004880 | 5920 | 185 | 32 | CR-S16-01 | Crossroads | 2025-11-24 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-004881 | 2849 | 37 | 77 | CR-S23-05 | Crossroads | 2025-11-24 | 17 | Animal | Lateral fuse | Forced | None
OE-25-004882 | 707 | 7 | 101 | PR-S07-05 | Prairie | 2025-11-24 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004883 | 3074 | 29 | 106 | CR-S03-01 | Crossroads | 2025-11-24 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004884 | 8614 | 118 | 73 | CR-S16-04 | Crossroads | 2025-11-24 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004885 | 6820 | 55 | 124 | CR-S17-02 | Crossroads | 2025-11-24 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004886 | 8023 | 71 | 113 | CR-S04-05 | Crossroads | 2025-11-25 | 2 | Vegetation | Lateral fuse | Forced | None
OE-25-004887 | 1826 | 11 | 166 | PR-S08-03 | Prairie | 2025-11-25 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004888 | 12880 | 184 | 70 | BY-S07-03 | Bayou | 2025-11-25 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-004889 | 12795 | 853 | 15 | CR-S23-01 | Crossroads | 2025-11-25 | 8 | Animal | Feeder recloser | Forced | None
OE-25-004890 | 2618 | 17 | 154 | CR-S26-03 | Crossroads | 2025-11-25 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004891 | 2030 | 14 | 145 | HB-S06-05 | Harbor | 2025-11-25 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004892 | 9821 | 61 | 161 | PR-S13-02 | Prairie | 2025-11-25 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004893 | 4898 | 62 | 79 | BY-S29-02 | Bayou | 2025-11-25 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-004894 | 5390 | 70 | 77 | HB-S15-01 | Harbor | 2025-11-25 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004895 | 3835 | 59 | 65 | PR-S14-04 | Prairie | 2025-11-25 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004896 | 10209 | 83 | 123 | HB-S18-03 | Harbor | 2025-11-25 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004897 | 2016 | 14 | 144 | BY-S15-01 | Bayou | 2025-11-25 | 19 | Vegetation | Transformer fuse | Forced | None
OE-25-004898 | 6968 | 67 | 104 | BY-S22-01 | Bayou | 2025-11-25 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-004899 | 38505 | 255 | 151 | PR-S06-03 | Prairie | 2025-11-25 | 20 | Vegetation | Lateral fuse | Forced | None
OE-25-004900 | 5481 | 21 | 261 | CR-S26-01 | Crossroads | 2025-11-26 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004901 | 46098 | 234 | 197 | BY-S02-02 | Bayou | 2025-11-26 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-25-004902 | 194776 | 1004 | 194 | CR-S16-04 | Crossroads | 2025-11-26 | 11 | Vegetation | Feeder recloser | Forced | None
OE-25-004903 | 33711 | 661 | 51 | BY-S21-01 | Bayou | 2025-11-26 | 12 | Vegetation | Feeder recloser | Forced | None
OE-25-004904 | 1030 | 10 | 103 | CR-S18-03 | Crossroads | 2025-11-26 | 12 | Animal | Transformer fuse | Forced | None
OE-25-004905 | 882 | 7 | 126 | BY-S06-03 | Bayou | 2025-11-26 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-25-004906 | 107700 | 1795 | 60 | BY-S22-04 | Bayou | 2025-11-26 | 13 | Animal | Substation breaker | Forced | None
OE-25-004907 | 3403 | 41 | 83 | HB-S02-01 | Harbor | 2025-11-26 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004908 | 1575 | 9 | 175 | PR-S07-06 | Prairie | 2025-11-26 | 14 | Animal | Transformer fuse | Forced | None
OE-25-004909 | 15912 | 72 | 221 | BY-S07-02 | Bayou | 2025-11-26 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004910 | 848 | 8 | 106 | HB-S08-02 | Harbor | 2025-11-26 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-25-004911 | 2912 | 91 | 32 | BY-S20-02 | Bayou | 2025-11-26 | 18 | Vegetation | Lateral fuse | Forced | None
OE-25-004912 | 1440 | 24 | 60 | HB-S08-05 | Harbor | 2025-11-26 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-004913 | 1518 | 11 | 138 | HB-S18-01 | Harbor | 2025-11-27 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004914 | 31603 | 187 | 169 | BY-S13-05 | Bayou | 2025-11-27 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-004915 | 5434 | 38 | 143 | BY-S19-01 | Bayou | 2025-11-27 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004916 | 10608 | 78 | 136 | CR-S04-06 | Crossroads | 2025-11-27 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004917 | 25000 | 125 | 200 | HB-S20-01 | Harbor | 2025-11-27 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004918 | 1815 | 11 | 165 | PR-S19-02 | Prairie | 2025-11-27 | 11 | Unknown | Lateral fuse | Forced | None
OE-25-004919 | 336 | 2 | 168 | CR-S15-01 | Crossroads | 2025-11-27 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004920 | 13359 | 73 | 183 | PR-S13-06 | Prairie | 2025-11-27 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004921 | 17850 | 105 | 170 | CR-S24-04 | Crossroads | 2025-11-27 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004922 | 264 | 2 | 132 | CR-S25-06 | Crossroads | 2025-11-27 | 17 | Animal | Transformer fuse | Forced | None
OE-25-004923 | 47800 | 100 | 478 | HB-S20-02 | Harbor | 2025-11-27 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-004924 | 3861 | 33 | 117 | HB-S02-03 | Harbor | 2025-11-27 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004925 | 9936 | 138 | 72 | BY-S07-06 | Bayou | 2025-11-28 | 4 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004926 | 1512 | 12 | 126 | CR-S23-03 | Crossroads | 2025-11-28 | 6 | Vegetation | Transformer fuse | Forced | None
OE-25-004927 | 6570 | 73 | 90 | BY-S15-06 | Bayou | 2025-11-28 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-004928 | 13167 | 77 | 171 | BY-S02-01 | Bayou | 2025-11-28 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-004929 | 1820 | 14 | 130 | BY-S25-04 | Bayou | 2025-11-28 | 10 | Animal | Transformer fuse | Forced | None
OE-25-004930 | 1353 | 11 | 123 | BY-S25-03 | Bayou | 2025-11-28 | 14 | Unknown | Transformer fuse | Forced | None
OE-25-004931 | 495 | 9 | 55 | HB-S18-03 | Harbor | 2025-11-28 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004932 | 39330 | 874 | 45 | CR-S16-04 | Crossroads | 2025-11-28 | 16 | Vegetation | Feeder recloser | Forced | None
OE-25-004933 | 1584 | 12 | 132 | CR-S07-02 | Crossroads | 2025-11-28 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004934 | 828 | 6 | 138 | CR-S20-01 | Crossroads | 2025-11-28 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004935 | 10744 | 79 | 136 | PR-S05-03 | Prairie | 2025-11-28 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004936 | 1710 | 9 | 190 | PR-S09-03 | Prairie | 2025-11-28 | 21 | Animal | Transformer fuse | Forced | None
OE-25-004937 | 77495 | 1409 | 55 | BY-S07-01 | Bayou | 2025-11-29 | 4 | Weather - lightning | Substation breaker | Outside cause | None
OE-25-004938 | 3982 | 11 | 362 | PR-S06-02 | Prairie | 2025-11-29 | 6 | Animal | Transformer fuse | Forced | None
OE-25-004939 | 2370 | 10 | 237 | PR-S20-01 | Prairie | 2025-11-29 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004940 | 962 | 13 | 74 | CR-S05-02 | Crossroads | 2025-11-29 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004941 | 2604 | 12 | 217 | CR-S26-03 | Crossroads | 2025-11-29 | 12 | Animal | Transformer fuse | Forced | None
OE-25-004942 | 2064 | 8 | 258 | HB-S15-03 | Harbor | 2025-11-29 | 12 | Animal | Transformer fuse | Forced | None
OE-25-004943 | 30589 | 169 | 181 | CR-S18-05 | Crossroads | 2025-11-29 | 15 | Unknown | Lateral fuse | Forced | None
OE-25-004944 | 5184 | 72 | 72 | PR-S13-04 | Prairie | 2025-11-29 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004945 | 35046 | 177 | 198 | BY-S14-03 | Bayou | 2025-11-29 | 22 | Vehicle or public | Lateral fuse | Forced | None
OE-25-004946 | 3978 | 39 | 102 | BY-S18-06 | Bayou | 2025-11-29 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004947 | 930 | 6 | 155 | HB-S15-03 | Harbor | 2025-11-30 | 6 | Unknown | Transformer fuse | Forced | None
OE-25-004948 | 198 | 1 | 198 | BY-S13-06 | Bayou | 2025-11-30 | 7 | Vegetation | Transformer fuse | Forced | None
OE-25-004949 | 8060 | 65 | 124 | PR-S08-02 | Prairie | 2025-11-30 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-25-004950 | 38313 | 297 | 129 | BY-S13-01 | Bayou | 2025-11-30 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004951 | 167 | 1 | 167 | HB-S05-06 | Harbor | 2025-11-30 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-004952 | 115 | 5 | 23 | CR-S07-06 | Crossroads | 2025-11-30 | 12 | Animal | Transformer fuse | Forced | None
OE-25-004953 | 1677 | 13 | 129 | BY-S12-02 | Bayou | 2025-11-30 | 16 | Animal | Transformer fuse | Forced | None
OE-25-004954 | 469 | 1 | 469 | PR-S18-06 | Prairie | 2025-11-30 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-25-004955 | 2178 | 11 | 198 | BY-S06-02 | Bayou | 2025-11-30 | 18 | Animal | Transformer fuse | Forced | None
OE-25-004956 | 4704 | 48 | 98 | PR-S16-05 | Prairie | 2025-11-30 | 21 | Unknown | Lateral fuse | Forced | None
OE-25-004957 | 4446 | 57 | 78 | HB-S15-03 | Harbor | 2025-12-01 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004958 | 4050 | 27 | 150 | HB-S09-03 | Harbor | 2025-12-01 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004959 | 9360 | 156 | 60 | PR-S19-03 | Prairie | 2025-12-01 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-004960 | 8601 | 61 | 141 | PR-S20-01 | Prairie | 2025-12-01 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004961 | 14381 | 73 | 197 | BY-S15-03 | Bayou | 2025-12-01 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004962 | 24102 | 206 | 117 | CR-S20-03 | Crossroads | 2025-12-01 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004963 | 8262 | 54 | 153 | PR-S13-04 | Prairie | 2025-12-01 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004964 | 870 | 5 | 174 | PR-S18-03 | Prairie | 2025-12-01 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004965 | 664 | 8 | 83 | BY-S24-05 | Bayou | 2025-12-01 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-004966 | 1939 | 7 | 277 | BY-S21-01 | Bayou | 2025-12-02 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-004967 | 3240 | 30 | 108 | HB-S05-01 | Harbor | 2025-12-02 | 5 | Vegetation | Lateral fuse | Forced | None
OE-25-004968 | 1140 | 5 | 228 | BY-S17-04 | Bayou | 2025-12-02 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004969 | 110 | 1 | 110 | BY-S10-04 | Bayou | 2025-12-02 | 10 | Animal | Transformer fuse | Forced | None
OE-25-004970 | 1204 | 28 | 43 | HB-S05-05 | Harbor | 2025-12-02 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004971 | 4278 | 31 | 138 | PR-S18-05 | Prairie | 2025-12-02 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004972 | 6464 | 101 | 64 | BY-S18-06 | Bayou | 2025-12-02 | 12 | Animal | Lateral fuse | Forced | None
OE-25-004973 | 30246 | 213 | 142 | CR-S13-02 | Crossroads | 2025-12-02 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-004974 | 96 | 1 | 96 | CR-S06-02 | Crossroads | 2025-12-02 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004975 | 480 | 6 | 80 | HB-S13-02 | Harbor | 2025-12-02 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004976 | 3444 | 42 | 82 | PR-S12-02 | Prairie | 2025-12-02 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004977 | 1708 | 7 | 244 | BY-S18-04 | Bayou | 2025-12-02 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004978 | 112995 | 1395 | 81 | PR-S07-03 | Prairie | 2025-12-03 | 4 | Equipment - overhead | Substation breaker | Forced | None
OE-25-004979 | 22407 | 231 | 97 | PR-S17-02 | Prairie | 2025-12-03 | 7 | Weather - wind | Feeder recloser | Forced | None
OE-25-004980 | 22950 | 459 | 50 | BY-S10-01 | Bayou | 2025-12-03 | 8 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-004981 | 1395 | 9 | 155 | BY-S23-02 | Bayou | 2025-12-03 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004982 | 24276 | 238 | 102 | BY-S26-05 | Bayou | 2025-12-03 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004983 | 2060 | 10 | 206 | PR-S11-02 | Prairie | 2025-12-03 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-004984 | 20952 | 216 | 97 | PR-S15-03 | Prairie | 2025-12-03 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-25-004985 | 2436 | 12 | 203 | BY-S19-02 | Bayou | 2025-12-03 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-25-004986 | 15246 | 66 | 231 | BY-S14-01 | Bayou | 2025-12-03 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-004987 | 12730 | 335 | 38 | BY-S16-02 | Bayou | 2025-12-03 | 14 | Vegetation | IGSD-isolated section | Forced | None
OE-25-004988 | 912 | 12 | 76 | HB-S07-03 | Harbor | 2025-12-03 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-004989 | 12189 | 51 | 239 | PR-S16-04 | Prairie | 2025-12-03 | 17 | Animal | Lateral fuse | Forced | None
OE-25-004990 | 8791 | 59 | 149 | BY-S12-01 | Bayou | 2025-12-03 | 20 | Animal | Lateral fuse | Forced | None
OE-25-004991 | 1092 | 6 | 182 | BY-S01-01 | Bayou | 2025-12-03 | 23 | Vegetation | Transformer fuse | Forced | None
OE-25-004992 | 768 | 2 | 384 | BY-S14-03 | Bayou | 2025-12-04 | 9 | Unknown | Transformer fuse | Forced | None
OE-25-004993 | 3150 | 25 | 126 | HB-S05-05 | Harbor | 2025-12-04 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004994 | 1632 | 16 | 102 | PR-S10-03 | Prairie | 2025-12-04 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-004995 | 15344 | 137 | 112 | CR-S28-03 | Crossroads | 2025-12-04 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-004996 | 3132 | 29 | 108 | PR-S12-01 | Prairie | 2025-12-04 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-004997 | 2860 | 11 | 260 | PR-S19-05 | Prairie | 2025-12-04 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004998 | 1936 | 8 | 242 | PR-S08-03 | Prairie | 2025-12-05 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-004999 | 280 | 2 | 140 | BY-S29-03 | Bayou | 2025-12-05 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-005000 | 2162 | 23 | 94 | CR-S14-03 | Crossroads | 2025-12-05 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005001 | 13916 | 196 | 71 | CR-S16-06 | Crossroads | 2025-12-05 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005002 | 1504 | 8 | 188 | BY-S27-06 | Bayou | 2025-12-05 | 11 | Animal | Transformer fuse | Forced | None
OE-25-005003 | 990 | 10 | 99 | HB-S15-02 | Harbor | 2025-12-05 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-25-005004 | 5180 | 74 | 70 | PR-S08-03 | Prairie | 2025-12-05 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-25-005005 | 26368 | 206 | 128 | CR-S02-03 | Crossroads | 2025-12-05 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-005006 | 20488 | 197 | 104 | HB-S12-03 | Harbor | 2025-12-05 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-005007 | 1161 | 9 | 129 | BY-S24-02 | Bayou | 2025-12-05 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-005008 | 100277 | 673 | 149 | BY-S29-05 | Bayou | 2025-12-06 | 7 | Vegetation | Feeder recloser | Forced | None
OE-25-005009 | 680 | 5 | 136 | HB-S02-02 | Harbor | 2025-12-06 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005010 | 3136 | 14 | 224 | PR-S16-01 | Prairie | 2025-12-06 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005011 | 128 | 2 | 64 | BY-S16-05 | Bayou | 2025-12-06 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-005012 | 54910 | 578 | 95 | CR-S19-01 | Crossroads | 2025-12-06 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005013 | 924 | 11 | 84 | BY-S13-04 | Bayou | 2025-12-06 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005014 | 13420 | 110 | 122 | PR-S16-04 | Prairie | 2025-12-06 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005015 | 1272 | 4 | 318 | CR-S25-05 | Crossroads | 2025-12-06 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005016 | 25620 | 610 | 42 | BY-S29-05 | Bayou | 2025-12-06 | 22 | Vegetation | Feeder recloser | Forced | None
OE-25-005017 | 330 | 6 | 55 | BY-S23-04 | Bayou | 2025-12-06 | 23 | Animal | Transformer fuse | Forced | None
OE-25-005018 | 7104 | 48 | 148 | CR-S05-06 | Crossroads | 2025-12-07 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-25-005019 | 25066 | 166 | 151 | CR-S14-05 | Crossroads | 2025-12-07 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005020 | 20824 | 548 | 38 | HB-S03-01 | Harbor | 2025-12-07 | 8 | Animal | Feeder recloser | Forced | None
OE-25-005021 | 7264 | 32 | 227 | CR-S25-01 | Crossroads | 2025-12-07 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-25-005022 | 4046 | 34 | 119 | HB-S18-03 | Harbor | 2025-12-07 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-005023 | 560 | 2 | 280 | BY-S08-03 | Bayou | 2025-12-07 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-005024 | 49010 | 377 | 130 | CR-S24-02 | Crossroads | 2025-12-07 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005025 | 6000 | 48 | 125 | CR-S12-01 | Crossroads | 2025-12-07 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005026 | 1386 | 6 | 231 | PR-S18-06 | Prairie | 2025-12-07 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005027 | 6612 | 58 | 114 | PR-S20-04 | Prairie | 2025-12-07 | 13 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-005028 | 1794 | 13 | 138 | PR-S07-05 | Prairie | 2025-12-07 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-005029 | 2387 | 11 | 217 | PR-S11-01 | Prairie | 2025-12-07 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-25-005030 | 316 | 2 | 158 | PR-S14-04 | Prairie | 2025-12-07 | 15 | Unknown | Transformer fuse | Forced | None
OE-25-005031 | 3024 | 72 | 42 | CR-S32-04 | Crossroads | 2025-12-07 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005032 | 28980 | 138 | 210 | PR-S14-04 | Prairie | 2025-12-07 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005033 | 6426 | 189 | 34 | CR-S07-06 | Crossroads | 2025-12-07 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005034 | 2556 | 12 | 213 | BY-S29-01 | Bayou | 2025-12-07 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-005035 | 2070 | 9 | 230 | PR-S01-05 | Prairie | 2025-12-08 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005036 | 180003 | 2069 | 87 | BY-S06-02 | Bayou | 2025-12-08 | 9 | Vegetation | Substation breaker | Forced | None
OE-25-005037 | 1760 | 20 | 88 | HB-S05-01 | Harbor | 2025-12-08 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-005038 | 23370 | 246 | 95 | BY-S04-01 | Bayou | 2025-12-08 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-25-005039 | 43365 | 295 | 147 | PR-S13-05 | Prairie | 2025-12-08 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-25-005040 | 153 | 1 | 153 | HB-S03-03 | Harbor | 2025-12-08 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005041 | 26000 | 250 | 104 | BY-S27-04 | Bayou | 2025-12-08 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005042 | 1300 | 10 | 130 | CR-S30-04 | Crossroads | 2025-12-09 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005043 | 588 | 12 | 49 | CR-S04-06 | Crossroads | 2025-12-09 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005044 | 5290 | 46 | 115 | CR-S24-01 | Crossroads | 2025-12-09 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005045 | 7205 | 55 | 131 | HB-S10-03 | Harbor | 2025-12-09 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-005046 | 1190 | 10 | 119 | BY-S27-05 | Bayou | 2025-12-09 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-005047 | 1974 | 14 | 141 | HB-S01-03 | Harbor | 2025-12-09 | 9 | Animal | Transformer fuse | Forced | None
OE-25-005048 | 2576 | 14 | 184 | CR-S02-03 | Crossroads | 2025-12-09 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005049 | 1414 | 14 | 101 | CR-S25-03 | Crossroads | 2025-12-09 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-25-005050 | 1300 | 10 | 130 | PR-S12-01 | Prairie | 2025-12-09 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005051 | 25920 | 576 | 45 | BY-S25-04 | Bayou | 2025-12-09 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005052 | 404 | 4 | 101 | CR-S28-02 | Crossroads | 2025-12-09 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005053 | 1350 | 9 | 150 | BY-S11-01 | Bayou | 2025-12-09 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005054 | 2086 | 14 | 149 | HB-S06-04 | Harbor | 2025-12-09 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-005055 | 912 | 3 | 304 | BY-S12-01 | Bayou | 2025-12-09 | 20 | Animal | Transformer fuse | Forced | None
OE-25-005056 | 62618 | 478 | 131 | BY-S29-05 | Bayou | 2025-12-09 | 20 | Vehicle or public | Feeder recloser | Forced | None
OE-25-005057 | 56628 | 234 | 242 | HB-S16-01 | Harbor | 2025-12-09 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005058 | 26676 | 702 | 38 | BY-S27-04 | Bayou | 2025-12-10 | 4 | Unknown | Substation breaker | Outside cause | None
OE-25-005059 | 42360 | 120 | 353 | PR-S17-02 | Prairie | 2025-12-10 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005060 | 8094 | 71 | 114 | CR-S09-05 | Crossroads | 2025-12-10 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005061 | 3060 | 30 | 102 | CR-S13-02 | Crossroads | 2025-12-10 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005062 | 920 | 5 | 184 | PR-S01-06 | Prairie | 2025-12-10 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-005063 | 1560 | 10 | 156 | BY-S29-05 | Bayou | 2025-12-10 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-005064 | 5539 | 29 | 191 | HB-S06-04 | Harbor | 2025-12-10 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005065 | 26970 | 174 | 155 | CR-S09-03 | Crossroads | 2025-12-10 | 13 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-25-005066 | 325 | 5 | 65 | HB-S15-03 | Harbor | 2025-12-10 | 14 | Animal | Transformer fuse | Forced | None
OE-25-005067 | 475 | 5 | 95 | CR-S31-01 | Crossroads | 2025-12-10 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005068 | 1044 | 12 | 87 | BY-S26-04 | Bayou | 2025-12-10 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005069 | 107555 | 2195 | 49 | CR-S16-02 | Crossroads | 2025-12-10 | 18 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005070 | 1090 | 10 | 109 | CR-S12-01 | Crossroads | 2025-12-10 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-25-005071 | 832 | 13 | 64 | BY-S26-03 | Bayou | 2025-12-10 | 23 | Animal | Transformer fuse | Forced | None
OE-25-005072 | 39432 | 212 | 186 | BY-S21-04 | Bayou | 2025-12-11 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005073 | 10432 | 326 | 32 | CR-S08-04 | Crossroads | 2025-12-11 | 11 | Weather - lightning | Feeder recloser | Forced | None
OE-25-005074 | 37720 | 410 | 92 | HB-S15-02 | Harbor | 2025-12-11 | 14 | Vegetation | Feeder recloser | Forced | None
OE-25-005075 | 23432 | 404 | 58 | PR-S01-03 | Prairie | 2025-12-11 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005076 | 2832 | 12 | 236 | BY-S27-04 | Bayou | 2025-12-11 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-25-005077 | 880 | 5 | 176 | CR-S01-04 | Crossroads | 2025-12-11 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005078 | 672 | 7 | 96 | HB-S18-02 | Harbor | 2025-12-11 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005079 | 18326 | 154 | 119 | PR-S20-01 | Prairie | 2025-12-11 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005080 | 4662 | 37 | 126 | PR-S20-01 | Prairie | 2025-12-11 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005081 | 624 | 12 | 52 | CR-S13-02 | Crossroads | 2025-12-11 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-25-005082 | 11264 | 88 | 128 | PR-S10-03 | Prairie | 2025-12-11 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005083 | 2668 | 46 | 58 | CR-S14-03 | Crossroads | 2025-12-11 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005084 | 3690 | 30 | 123 | HB-S19-01 | Harbor | 2025-12-11 | 23 | Vehicle or public | Lateral fuse | Forced | None
OE-25-005085 | 103332 | 654 | 158 | CR-S25-02 | Crossroads | 2025-12-12 | 6 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-005086 | 4655 | 95 | 49 | CR-S25-01 | Crossroads | 2025-12-12 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005087 | 7384 | 104 | 71 | HB-S02-02 | Harbor | 2025-12-12 | 11 | Weather - lightning | Lateral fuse | Forced | None
OE-25-005088 | 1320 | 22 | 60 | BY-S29-02 | Bayou | 2025-12-12 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005089 | 2394 | 9 | 266 | CR-S07-01 | Crossroads | 2025-12-12 | 12 | Vegetation | Transformer fuse | Forced | None
OE-25-005090 | 3978 | 39 | 102 | BY-S21-02 | Bayou | 2025-12-12 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005091 | 1072 | 8 | 134 | CR-S12-03 | Crossroads | 2025-12-12 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005092 | 195437 | 1793 | 109 | CR-S14-05 | Crossroads | 2025-12-12 | 15 | Weather - wind | Substation breaker | Forced | None
OE-25-005093 | 9030 | 105 | 86 | BY-S09-02 | Bayou | 2025-12-12 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005094 | 1885 | 13 | 145 | BY-S09-04 | Bayou | 2025-12-12 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-005095 | 923 | 13 | 71 | CR-S04-06 | Crossroads | 2025-12-12 | 22 | Vegetation | Transformer fuse | Forced | None
OE-25-005096 | 2016 | 16 | 126 | CR-S03-03 | Crossroads | 2025-12-13 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005097 | 1336 | 8 | 167 | PR-S09-03 | Prairie | 2025-12-13 | 12 | Unknown | Lateral fuse | Forced | None
OE-25-005098 | 3360 | 42 | 80 | PR-S13-02 | Prairie | 2025-12-13 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-005099 | 2160 | 16 | 135 | BY-S29-02 | Bayou | 2025-12-13 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-005100 | 4212 | 13 | 324 | CR-S31-03 | Crossroads | 2025-12-13 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-005101 | 5037 | 73 | 69 | BY-S21-04 | Bayou | 2025-12-13 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005102 | 8520 | 30 | 284 | BY-S09-02 | Bayou | 2025-12-13 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-25-005103 | 4032 | 48 | 84 | PR-S18-03 | Prairie | 2025-12-13 | 21 | Vehicle or public | Lateral fuse | Forced | None
OE-25-005104 | 14880 | 124 | 120 | HB-S12-02 | Harbor | 2025-12-13 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005105 | 151984 | 944 | 161 | BY-S23-04 | Bayou | 2025-12-14 | 5 | Vegetation | Feeder recloser | Forced | None
OE-25-005106 | 575 | 5 | 115 | BY-S30-01 | Bayou | 2025-12-14 | 10 | Vegetation | Transformer fuse | Forced | None
OE-25-005107 | 316480 | 1840 | 172 | CR-S31-01 | Crossroads | 2025-12-14 | 10 | Equipment - underground | Substation breaker | Forced | None
OE-25-005108 | 265923 | 3283 | 81 | CR-S14-02 | Crossroads | 2025-12-14 | 14 | Equipment - underground | Substation breaker | Forced | None
OE-25-005109 | 1280 | 8 | 160 | CR-S32-04 | Crossroads | 2025-12-14 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005110 | 588 | 3 | 196 | HB-S07-03 | Harbor | 2025-12-14 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005111 | 11270 | 49 | 230 | HB-S18-01 | Harbor | 2025-12-14 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005112 | 596721 | 1347 | 443 | PR-S14-04 | Prairie | 2025-12-14 | 17 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005113 | 1463 | 11 | 133 | CR-S08-03 | Crossroads | 2025-12-15 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-25-005114 | 5076 | 18 | 282 | BY-S16-04 | Bayou | 2025-12-15 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005115 | 35700 | 714 | 50 | CR-S08-02 | Crossroads | 2025-12-15 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005116 | 765 | 5 | 153 | PR-S12-01 | Prairie | 2025-12-15 | 19 | Animal | Transformer fuse | Forced | None
OE-25-005117 | 82777 | 1403 | 59 | HB-S04-01 | Harbor | 2025-12-15 | 20 | Unknown | Substation breaker | Outside cause | None
OE-25-005118 | 10296 | 132 | 78 | PR-S10-03 | Prairie | 2025-12-15 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005119 | 24360 | 116 | 210 | PR-S20-02 | Prairie | 2025-12-16 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-005120 | 602 | 14 | 43 | CR-S11-01 | Crossroads | 2025-12-16 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-005121 | 48720 | 870 | 56 | PR-S18-03 | Prairie | 2025-12-16 | 9 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005122 | 80 | 1 | 80 | HB-S11-03 | Harbor | 2025-12-16 | 11 | Vegetation | Transformer fuse | Forced | None
OE-25-005123 | 412 | 2 | 206 | HB-S16-04 | Harbor | 2025-12-16 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-25-005124 | 7888 | 136 | 58 | BY-S23-01 | Bayou | 2025-12-16 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-005125 | 84280 | 860 | 98 | CR-S26-02 | Crossroads | 2025-12-16 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-005126 | 6854 | 149 | 46 | HB-S16-01 | Harbor | 2025-12-16 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005127 | 2916 | 12 | 243 | BY-S29-05 | Bayou | 2025-12-16 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005128 | 1794 | 13 | 138 | HB-S17-02 | Harbor | 2025-12-16 | 23 | Vegetation | Transformer fuse | Forced | None
OE-25-005129 | 1384 | 8 | 173 | BY-S17-03 | Bayou | 2025-12-17 | 5 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005130 | 3280 | 41 | 80 | CR-S14-01 | Crossroads | 2025-12-17 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-25-005131 | 41685 | 1191 | 35 | HB-S02-02 | Harbor | 2025-12-17 | 8 | Animal | Substation breaker | Forced | None
OE-25-005132 | 5504 | 64 | 86 | BY-S18-06 | Bayou | 2025-12-17 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005133 | 76707 | 947 | 81 | PR-S11-01 | Prairie | 2025-12-17 | 16 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-005134 | 1232 | 14 | 88 | CR-S02-04 | Crossroads | 2025-12-17 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005135 | 15048 | 114 | 132 | PR-S18-05 | Prairie | 2025-12-18 | 2 | Vehicle or public | Lateral fuse | Forced | None
OE-25-005136 | 1776 | 12 | 148 | BY-S28-02 | Bayou | 2025-12-18 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005137 | 2847 | 39 | 73 | CR-S08-04 | Crossroads | 2025-12-18 | 8 | Animal | Lateral fuse | Forced | None
OE-25-005138 | 8118 | 82 | 99 | CR-S13-03 | Crossroads | 2025-12-18 | 10 | Animal | Lateral fuse | Forced | None
OE-25-005139 | 2744 | 56 | 49 | CR-S27-03 | Crossroads | 2025-12-18 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005140 | 16878 | 87 | 194 | BY-S30-01 | Bayou | 2025-12-18 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005141 | 2684 | 11 | 244 | BY-S29-01 | Bayou | 2025-12-18 | 13 | Animal | Transformer fuse | Forced | None
OE-25-005142 | 7056 | 84 | 84 | BY-S16-01 | Bayou | 2025-12-18 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-005143 | 31328 | 352 | 89 | PR-S01-05 | Prairie | 2025-12-18 | 15 | Weather - wind | Feeder recloser | Forced | None
OE-25-005144 | 992 | 4 | 248 | BY-S17-01 | Bayou | 2025-12-18 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-25-005145 | 20865 | 535 | 39 | HB-S03-02 | Harbor | 2025-12-18 | 17 | Weather - lightning | Feeder recloser | Forced | None
OE-25-005146 | 75764 | 806 | 94 | PR-S19-01 | Prairie | 2025-12-18 | 18 | Vegetation | Substation breaker | Forced | None
OE-25-005147 | 1488 | 12 | 124 | HB-S15-02 | Harbor | 2025-12-19 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005148 | 7560 | 56 | 135 | PR-S03-04 | Prairie | 2025-12-19 | 2 | Vehicle or public | Lateral fuse | Forced | None
OE-25-005149 | 83805 | 755 | 111 | CR-S04-03 | Crossroads | 2025-12-19 | 3 | Vegetation | Feeder recloser | Forced | None
OE-25-005150 | 154974 | 1123 | 138 | CR-S09-01 | Crossroads | 2025-12-19 | 3 | Vegetation | Feeder recloser | Forced | None
OE-25-005151 | 22770 | 138 | 165 | CR-S13-05 | Crossroads | 2025-12-19 | 4 | Unknown | Lateral fuse | Forced | None
OE-25-005152 | 37504 | 1172 | 32 | CR-S27-02 | Crossroads | 2025-12-19 | 7 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005153 | 2821 | 31 | 91 | BY-S12-03 | Bayou | 2025-12-19 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005154 | 11822 | 257 | 46 | BY-S16-03 | Bayou | 2025-12-19 | 12 | Animal | Lateral fuse | Forced | None
OE-25-005155 | 124 | 1 | 124 | BY-S30-03 | Bayou | 2025-12-19 | 13 | Unknown | Transformer fuse | Forced | None
OE-25-005156 | 19096 | 77 | 248 | CR-S16-02 | Crossroads | 2025-12-19 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005157 | 37914 | 534 | 71 | BY-S21-05 | Bayou | 2025-12-19 | 15 | Vehicle or public | Feeder recloser | Forced | None
OE-25-005158 | 4823 | 53 | 91 | CR-S10-01 | Crossroads | 2025-12-19 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005159 | 1810 | 10 | 181 | BY-S23-02 | Bayou | 2025-12-19 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-005160 | 57620 | 860 | 67 | HB-S15-02 | Harbor | 2025-12-19 | 16 | Equipment - overhead | Substation breaker | Forced | None
OE-25-005161 | 41202 | 981 | 42 | CR-S06-02 | Crossroads | 2025-12-19 | 18 | Weather - wind | Feeder recloser | Forced | None
OE-25-005162 | 39494 | 434 | 91 | BY-S23-03 | Bayou | 2025-12-20 | 0 | Weather - lightning | Lateral fuse | Forced | None
OE-25-005163 | 54418 | 161 | 338 | PR-S11-01 | Prairie | 2025-12-20 | 15 | Vegetation | Lateral fuse | Forced | None
OE-25-005164 | 9263 | 59 | 157 | PR-S13-06 | Prairie | 2025-12-20 | 16 | Vegetation | Lateral fuse | Forced | None
OE-25-005165 | 1740 | 12 | 145 | BY-S18-04 | Bayou | 2025-12-20 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-25-005166 | 620 | 4 | 155 | CR-S06-02 | Crossroads | 2025-12-20 | 18 | Animal | Transformer fuse | Forced | None
OE-25-005167 | 16848 | 117 | 144 | CR-S23-02 | Crossroads | 2025-12-21 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005168 | 16290 | 90 | 181 | PR-S13-01 | Prairie | 2025-12-21 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005169 | 2626 | 13 | 202 | PR-S13-06 | Prairie | 2025-12-21 | 13 | Animal | Transformer fuse | Forced | None
OE-25-005170 | 34980 | 159 | 220 | BY-S24-02 | Bayou | 2025-12-21 | 17 | Animal | Lateral fuse | Forced | None
OE-25-005171 | 1080 | 8 | 135 | CR-S27-02 | Crossroads | 2025-12-21 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005172 | 124497 | 1537 | 81 | PR-S09-03 | Prairie | 2025-12-21 | 22 | Equipment - overhead | Substation breaker | Outside cause | None
OE-25-005173 | 7986 | 66 | 121 | PR-S18-02 | Prairie | 2025-12-22 | 8 | Animal | Lateral fuse | Forced | None
OE-25-005174 | 4148 | 61 | 68 | CR-S09-02 | Crossroads | 2025-12-22 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005175 | 15040 | 94 | 160 | BY-S18-07 | Bayou | 2025-12-22 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005176 | 1560 | 12 | 130 | BY-S22-02 | Bayou | 2025-12-22 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005177 | 2002 | 14 | 143 | BY-S29-02 | Bayou | 2025-12-22 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-005178 | 630 | 3 | 210 | CR-S04-06 | Crossroads | 2025-12-22 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005179 | 60838 | 1601 | 38 | CR-S08-02 | Crossroads | 2025-12-22 | 14 | Weather - lightning | Substation breaker | Forced | None
OE-25-005180 | 876 | 12 | 73 | HB-S15-03 | Harbor | 2025-12-22 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005181 | 4891 | 73 | 67 | CR-S24-01 | Crossroads | 2025-12-22 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-25-005182 | 66795 | 305 | 219 | PR-S11-01 | Prairie | 2025-12-22 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-25-005183 | 80850 | 525 | 154 | CR-S15-03 | Crossroads | 2025-12-22 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-005184 | 711 | 9 | 79 | PR-S01-05 | Prairie | 2025-12-22 | 18 | Vegetation | Transformer fuse | Forced | None
OE-25-005185 | 816 | 12 | 68 | PR-S07-06 | Prairie | 2025-12-22 | 19 | Animal | Transformer fuse | Forced | None
OE-25-005186 | 1666 | 14 | 119 | BY-S03-01 | Bayou | 2025-12-22 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005187 | 918 | 9 | 102 | BY-S29-01 | Bayou | 2025-12-22 | 22 | Vehicle or public | Transformer fuse | Forced | None
OE-25-005188 | 1040 | 10 | 104 | BY-S27-03 | Bayou | 2025-12-23 | 9 | Vegetation | Transformer fuse | Forced | None
OE-25-005189 | 20349 | 133 | 153 | BY-S01-02 | Bayou | 2025-12-23 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005190 | 6240 | 65 | 96 | BY-S30-01 | Bayou | 2025-12-23 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-005191 | 266 | 2 | 133 | BY-S12-02 | Bayou | 2025-12-23 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005192 | 10519 | 67 | 157 | BY-S26-02 | Bayou | 2025-12-23 | 20 | Unknown | Lateral fuse | Forced | None
OE-25-005193 | 223 | 1 | 223 | CR-S02-02 | Crossroads | 2025-12-23 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-005194 | 3591 | 19 | 189 | BY-S19-02 | Bayou | 2025-12-23 | 22 | Vegetation | Lateral fuse | Forced | None
OE-25-005195 | 22560 | 235 | 96 | BY-S08-02 | Bayou | 2025-12-24 | 0 | Vegetation | Lateral fuse | Forced | None
OE-25-005196 | 1760 | 44 | 40 | PR-S12-03 | Prairie | 2025-12-24 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005197 | 3760 | 16 | 235 | HB-S06-01 | Harbor | 2025-12-24 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005198 | 12285 | 315 | 39 | HB-S15-01 | Harbor | 2025-12-24 | 10 | Vegetation | Lateral fuse | Forced | None
OE-25-005199 | 21630 | 618 | 35 | PR-S03-03 | Prairie | 2025-12-24 | 10 | Equipment - overhead | Substation breaker | Forced | None
OE-25-005200 | 3822 | 78 | 49 | BY-S01-02 | Bayou | 2025-12-24 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005201 | 6916 | 38 | 182 | BY-S19-02 | Bayou | 2025-12-24 | 13 | Unknown | Lateral fuse | Forced | None
OE-25-005202 | 2618 | 17 | 154 | CR-S22-03 | Crossroads | 2025-12-24 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005203 | 6555 | 69 | 95 | HB-S07-05 | Harbor | 2025-12-24 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005204 | 160 | 1 | 160 | PR-S20-03 | Prairie | 2025-12-24 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-25-005205 | 2310 | 14 | 165 | BY-S23-02 | Bayou | 2025-12-24 | 16 | Vegetation | Transformer fuse | Forced | None
OE-25-005206 | 6104 | 56 | 109 | PR-S07-06 | Prairie | 2025-12-24 | 17 | Vegetation | Lateral fuse | Forced | None
OE-25-005207 | 3016 | 13 | 232 | PR-S18-01 | Prairie | 2025-12-24 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005208 | 2093 | 13 | 161 | HB-S01-05 | Harbor | 2025-12-24 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005209 | 33366 | 166 | 201 | BY-S05-02 | Bayou | 2025-12-25 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-005210 | 20470 | 445 | 46 | BY-S27-04 | Bayou | 2025-12-25 | 8 | Animal | Feeder recloser | Forced | None
OE-25-005211 | 13320 | 40 | 333 | PR-S18-06 | Prairie | 2025-12-25 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005212 | 1111 | 11 | 101 | CR-S03-03 | Crossroads | 2025-12-25 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005213 | 1200 | 12 | 100 | PR-S07-06 | Prairie | 2025-12-25 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005214 | 2520 | 10 | 252 | CR-S30-05 | Crossroads | 2025-12-26 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005215 | 6732 | 33 | 204 | BY-S13-01 | Bayou | 2025-12-26 | 9 | Vegetation | Lateral fuse | Forced | None
OE-25-005216 | 4508 | 28 | 161 | BY-S06-03 | Bayou | 2025-12-26 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005217 | 9812 | 44 | 223 | HB-S08-04 | Harbor | 2025-12-26 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005218 | 91188 | 306 | 298 | BY-S04-01 | Bayou | 2025-12-26 | 12 | Vegetation | Lateral fuse | Forced | None
OE-25-005219 | 4209 | 23 | 183 | CR-S01-01 | Crossroads | 2025-12-26 | 14 | Vegetation | Lateral fuse | Forced | None
OE-25-005220 | 30888 | 572 | 54 | CR-S32-03 | Crossroads | 2025-12-26 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-005221 | 770 | 14 | 55 | CR-S12-01 | Crossroads | 2025-12-26 | 15 | Vegetation | Transformer fuse | Forced | None
OE-25-005222 | 6241 | 79 | 79 | PR-S18-03 | Prairie | 2025-12-26 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-25-005223 | 2184 | 13 | 168 | PR-S03-02 | Prairie | 2025-12-26 | 21 | Animal | Transformer fuse | Forced | None
OE-25-005224 | 1617 | 7 | 231 | PR-S08-01 | Prairie | 2025-12-27 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005225 | 29346 | 219 | 134 | BY-S24-04 | Bayou | 2025-12-27 | 7 | Vegetation | Lateral fuse | Forced | None
OE-25-005226 | 5616 | 78 | 72 | PR-S11-02 | Prairie | 2025-12-27 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005227 | 1140 | 4 | 285 | BY-S07-02 | Bayou | 2025-12-27 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005228 | 1358 | 7 | 194 | PR-S07-05 | Prairie | 2025-12-27 | 14 | Vegetation | Transformer fuse | Forced | None
OE-25-005229 | 1925 | 11 | 175 | BY-S10-02 | Bayou | 2025-12-27 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005230 | 6944 | 62 | 112 | PR-S09-01 | Prairie | 2025-12-27 | 19 | Vegetation | Lateral fuse | Forced | None
OE-25-005231 | 2002 | 11 | 182 | BY-S07-01 | Bayou | 2025-12-27 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005232 | 3912 | 12 | 326 | HB-S15-01 | Harbor | 2025-12-27 | 21 | Vegetation | Transformer fuse | Forced | None
OE-25-005233 | 14586 | 102 | 143 | HB-S19-02 | Harbor | 2025-12-28 | 10 | Animal | Lateral fuse | Forced | None
OE-25-005234 | 1716 | 11 | 156 | PR-S15-06 | Prairie | 2025-12-28 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005235 | 1775 | 5 | 355 | PR-S13-03 | Prairie | 2025-12-28 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005236 | 10397 | 281 | 37 | PR-S18-01 | Prairie | 2025-12-28 | 17 | Vegetation | Feeder recloser | Forced | None
OE-25-005237 | 855 | 9 | 95 | PR-S07-04 | Prairie | 2025-12-28 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-25-005238 | 159 | 1 | 159 | PR-S06-02 | Prairie | 2025-12-29 | 0 | Vegetation | Transformer fuse | Forced | None
OE-25-005239 | 188 | 1 | 188 | PR-S14-03 | Prairie | 2025-12-29 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005240 | 5656 | 56 | 101 | PR-S19-02 | Prairie | 2025-12-29 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005241 | 19950 | 475 | 42 | BY-S06-03 | Bayou | 2025-12-29 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-005242 | 28459 | 149 | 191 | BY-S15-06 | Bayou | 2025-12-29 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005243 | 52152 | 1272 | 41 | CR-S19-04 | Crossroads | 2025-12-29 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-25-005244 | 2640 | 33 | 80 | PR-S02-01 | Prairie | 2025-12-29 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-25-005245 | 1210 | 11 | 110 | BY-S02-01 | Bayou | 2025-12-29 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-25-005246 | 16120 | 124 | 130 | HB-S17-03 | Harbor | 2025-12-29 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-25-005247 | 39720 | 662 | 60 | CR-S32-03 | Crossroads | 2025-12-29 | 19 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-005248 | 18772 | 52 | 361 | PR-S20-02 | Prairie | 2025-12-29 | 21 | Vehicle or public | Lateral fuse | Forced | None
OE-25-005249 | 1368 | 6 | 228 | CR-S01-02 | Crossroads | 2025-12-29 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005250 | 3078 | 18 | 171 | PR-S07-06 | Prairie | 2025-12-29 | 23 | Weather - wind | Lateral fuse | Forced | None
OE-25-005251 | 206654 | 1018 | 203 | HB-S17-03 | Harbor | 2025-12-30 | 0 | Vegetation | Feeder recloser | Forced | None
OE-25-005252 | 1125 | 9 | 125 | BY-S06-02 | Bayou | 2025-12-30 | 2 | Vehicle or public | Transformer fuse | Forced | None
OE-25-005253 | 3840 | 24 | 160 | CR-S10-03 | Crossroads | 2025-12-30 | 4 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005254 | 6264 | 116 | 54 | BY-S29-02 | Bayou | 2025-12-30 | 11 | Vegetation | Lateral fuse | Forced | None
OE-25-005255 | 18352 | 62 | 296 | PR-S14-04 | Prairie | 2025-12-30 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005256 | 143925 | 1425 | 101 | PR-S13-01 | Prairie | 2025-12-30 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-25-005257 | 13888 | 62 | 224 | PR-S17-01 | Prairie | 2025-12-30 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-25-005258 | 12816 | 89 | 144 | BY-S13-06 | Bayou | 2025-12-30 | 16 | Animal | Lateral fuse | Forced | None
OE-25-005259 | 520 | 10 | 52 | CR-S06-01 | Crossroads | 2025-12-30 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-25-005260 | 129 | 3 | 43 | HB-S05-06 | Harbor | 2025-12-30 | 20 | Vegetation | Transformer fuse | Forced | None
OE-25-005261 | 4648 | 56 | 83 | BY-S03-03 | Bayou | 2025-12-31 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-25-005262 | 24382 | 73 | 334 | BY-S12-04 | Bayou | 2025-12-31 | 8 | Vegetation | Lateral fuse | Forced | None
OE-25-005263 | 12200 | 305 | 40 | BY-S10-01 | Bayou | 2025-12-31 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-25-005264 | 22137 | 157 | 141 | BY-S29-01 | Bayou | 2025-12-31 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-25-005265 | 13104 | 117 | 112 | HB-S16-05 | Harbor | 2025-12-31 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-25-005266 | 2697 | 29 | 93 | PR-S05-03 | Prairie | 2025-12-31 | 13 | Vegetation | Lateral fuse | Forced | None
OE-25-005267 | 21462 | 219 | 98 | BY-S15-05 | Bayou | 2025-12-31 | 14 | Animal | Lateral fuse | Forced | None
OE-25-005268 | 2225 | 25 | 89 | PR-S03-04 | Prairie | 2025-12-31 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-25-005269 | 1235 | 5 | 247 | BY-S16-01 | Bayou | 2025-12-31 | 22 | Vegetation | Transformer fuse | Forced | None

## Data 2
event_id | customer_minutes | customers_interrupted | duration_minutes | feeder_code | district | start_date | start_hour | cause | device | classification | major_event
OE-26-000001 | 66334 | 1951 | 34 | BY-S16-01 | Bayou | 2026-01-01 | 1 | Vegetation | Feeder recloser | Forced | None
OE-26-000002 | 10500 | 125 | 84 | CR-S04-03 | Crossroads | 2026-01-01 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000003 | 5775 | 11 | 525 | PR-S20-03 | Prairie | 2026-01-01 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000004 | 25300 | 100 | 253 | CR-S12-02 | Crossroads | 2026-01-01 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000005 | 5472 | 36 | 152 | BY-S16-05 | Bayou | 2026-01-01 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000006 | 15694 | 118 | 133 | CR-S29-03 | Crossroads | 2026-01-01 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000007 | 158523 | 997 | 159 | PR-S17-01 | Prairie | 2026-01-01 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-000008 | 26600 | 475 | 56 | CR-S29-01 | Crossroads | 2026-01-01 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000009 | 6960 | 40 | 174 | PR-S10-03 | Prairie | 2026-01-01 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000010 | 4169 | 11 | 379 | CR-S06-01 | Crossroads | 2026-01-01 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000011 | 1845 | 9 | 205 | BY-S18-04 | Bayou | 2026-01-01 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-000012 | 1057 | 7 | 151 | CR-S10-02 | Crossroads | 2026-01-01 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-000013 | 3600 | 12 | 300 | HB-S18-02 | Harbor | 2026-01-02 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000014 | 16910 | 178 | 95 | CR-S19-03 | Crossroads | 2026-01-02 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000015 | 89586 | 1422 | 63 | HB-S09-03 | Harbor | 2026-01-02 | 9 | Weather - wind | Substation breaker | Forced | None
OE-26-000016 | 4296 | 24 | 179 | BY-S15-03 | Bayou | 2026-01-02 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000017 | 15582 | 106 | 147 | BY-S10-03 | Bayou | 2026-01-02 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000018 | 876 | 4 | 219 | BY-S25-05 | Bayou | 2026-01-02 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-000019 | 15051 | 87 | 173 | PR-S12-02 | Prairie | 2026-01-02 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-000020 | 21120 | 88 | 240 | CR-S06-02 | Crossroads | 2026-01-02 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-26-000021 | 4379 | 29 | 151 | CR-S24-01 | Crossroads | 2026-01-02 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000022 | 7497 | 63 | 119 | CR-S26-05 | Crossroads | 2026-01-03 | 11 | Animal | Lateral fuse | Forced | None
OE-26-000023 | 2940 | 28 | 105 | CR-S07-01 | Crossroads | 2026-01-03 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000024 | 25047 | 363 | 69 | CR-S16-05 | Crossroads | 2026-01-03 | 14 | Vegetation | Feeder recloser | Forced | None
OE-26-000025 | 127872 | 432 | 296 | HB-S12-03 | Harbor | 2026-01-03 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000026 | 95358 | 1382 | 69 | BY-S20-02 | Bayou | 2026-01-03 | 17 | Vegetation | Substation breaker | Forced | None
OE-26-000027 | 5500 | 11 | 500 | PR-S02-02 | Prairie | 2026-01-03 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000028 | 2940 | 70 | 42 | CR-S03-02 | Crossroads | 2026-01-03 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-000029 | 139794 | 3039 | 46 | CR-S19-03 | Crossroads | 2026-01-03 | 18 | Equipment - underground | Substation breaker | Forced | None
OE-26-000030 | 9180 | 102 | 90 | HB-S17-03 | Harbor | 2026-01-03 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000031 | 784 | 8 | 98 | PR-S20-03 | Prairie | 2026-01-03 | 23 | Weather - wind | Transformer fuse | Forced | None
OE-26-000032 | 4136 | 22 | 188 | BY-S27-05 | Bayou | 2026-01-04 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000033 | 2684 | 44 | 61 | CR-S22-03 | Crossroads | 2026-01-04 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000034 | 610 | 5 | 122 | BY-S18-06 | Bayou | 2026-01-04 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000035 | 6664 | 136 | 49 | BY-S30-02 | Bayou | 2026-01-04 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-26-000036 | 156 | 1 | 156 | BY-S19-02 | Bayou | 2026-01-04 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-000037 | 7347 | 79 | 93 | BY-S11-02 | Bayou | 2026-01-04 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000038 | 2360 | 40 | 59 | HB-S20-04 | Harbor | 2026-01-04 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000039 | 1001 | 7 | 143 | HB-S14-01 | Harbor | 2026-01-04 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000040 | 384 | 2 | 192 | CR-S13-06 | Crossroads | 2026-01-04 | 21 | Animal | Transformer fuse | Forced | None
OE-26-000041 | 432 | 4 | 108 | HB-S08-04 | Harbor | 2026-01-05 | 5 | Unknown | Transformer fuse | Forced | None
OE-26-000042 | 63750 | 625 | 102 | BY-S03-01 | Bayou | 2026-01-05 | 10 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000043 | 27776 | 112 | 248 | BY-S29-03 | Bayou | 2026-01-05 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-26-000044 | 1992 | 8 | 249 | BY-S06-02 | Bayou | 2026-01-05 | 12 | Animal | Transformer fuse | Forced | None
OE-26-000045 | 2090 | 10 | 209 | CR-S30-02 | Crossroads | 2026-01-05 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000046 | 15525 | 75 | 207 | PR-S15-06 | Prairie | 2026-01-05 | 19 | Animal | Lateral fuse | Forced | None
OE-26-000047 | 5166 | 63 | 82 | CR-S22-02 | Crossroads | 2026-01-06 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000048 | 19788 | 582 | 34 | HB-S04-01 | Harbor | 2026-01-06 | 8 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000049 | 688 | 4 | 172 | BY-S14-02 | Bayou | 2026-01-06 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000050 | 900 | 6 | 150 | CR-S02-03 | Crossroads | 2026-01-06 | 9 | Animal | Transformer fuse | Forced | None
OE-26-000051 | 2860 | 13 | 220 | CR-S13-03 | Crossroads | 2026-01-06 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000052 | 6500 | 52 | 125 | BY-S27-02 | Bayou | 2026-01-06 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000053 | 8684 | 52 | 167 | PR-S16-04 | Prairie | 2026-01-06 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000054 | 913 | 11 | 83 | BY-S27-04 | Bayou | 2026-01-06 | 14 | Unknown | Transformer fuse | Forced | None
OE-26-000055 | 250480 | 1010 | 248 | PR-S02-02 | Prairie | 2026-01-06 | 15 | Vegetation | Feeder recloser | Forced | None
OE-26-000056 | 44160 | 920 | 48 | CR-S15-01 | Crossroads | 2026-01-06 | 18 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000057 | 1400 | 5 | 280 | CR-S16-04 | Crossroads | 2026-01-06 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000058 | 4884 | 66 | 74 | CR-S12-03 | Crossroads | 2026-01-06 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000059 | 3420 | 38 | 90 | BY-S06-01 | Bayou | 2026-01-07 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-26-000060 | 7990 | 47 | 170 | BY-S15-03 | Bayou | 2026-01-07 | 5 | Vegetation | Lateral fuse | Forced | None
OE-26-000061 | 18156 | 178 | 102 | BY-S27-02 | Bayou | 2026-01-07 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000062 | 846 | 9 | 94 | BY-S18-05 | Bayou | 2026-01-07 | 7 | Animal | Transformer fuse | Forced | None
OE-26-000063 | 35949 | 69 | 521 | CR-S26-06 | Crossroads | 2026-01-07 | 9 | Vehicle or public | Lateral fuse | Forced | None
OE-26-000064 | 11250 | 75 | 150 | CR-S18-04 | Crossroads | 2026-01-07 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000065 | 3315 | 13 | 255 | CR-S20-03 | Crossroads | 2026-01-07 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000066 | 468 | 3 | 156 | CR-S15-01 | Crossroads | 2026-01-07 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000067 | 3132 | 9 | 348 | BY-S26-06 | Bayou | 2026-01-07 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000068 | 17100 | 171 | 100 | CR-S07-01 | Crossroads | 2026-01-08 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000069 | 11319 | 33 | 343 | BY-S25-02 | Bayou | 2026-01-08 | 16 | Animal | Lateral fuse | Forced | None
OE-26-000070 | 23856 | 852 | 28 | CR-S26-01 | Crossroads | 2026-01-08 | 16 | Unknown | Substation breaker | Outside cause | None
OE-26-000071 | 420 | 3 | 140 | PR-S13-01 | Prairie | 2026-01-08 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000072 | 7406 | 46 | 161 | PR-S16-02 | Prairie | 2026-01-08 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000073 | 804 | 6 | 134 | BY-S13-03 | Bayou | 2026-01-08 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000074 | 93366 | 741 | 126 | CR-S04-05 | Crossroads | 2026-01-08 | 20 | Vehicle or public | Feeder recloser | Forced | None
OE-26-000075 | 18354 | 69 | 266 | CR-S03-03 | Crossroads | 2026-01-09 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000076 | 2626 | 13 | 202 | PR-S19-03 | Prairie | 2026-01-09 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000077 | 1133 | 11 | 103 | CR-S14-04 | Crossroads | 2026-01-09 | 7 | Animal | Transformer fuse | Forced | None
OE-26-000078 | 880 | 55 | 16 | BY-S09-05 | Bayou | 2026-01-09 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-000079 | 1060 | 5 | 212 | PR-S01-05 | Prairie | 2026-01-09 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-000080 | 7986 | 66 | 121 | BY-S13-03 | Bayou | 2026-01-09 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000081 | 7380 | 45 | 164 | PR-S03-02 | Prairie | 2026-01-09 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000082 | 1440 | 9 | 160 | BY-S01-01 | Bayou | 2026-01-09 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000083 | 1359 | 9 | 151 | BY-S20-01 | Bayou | 2026-01-09 | 16 | Unknown | Transformer fuse | Forced | None
OE-26-000084 | 536 | 8 | 67 | BY-S11-01 | Bayou | 2026-01-09 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000085 | 927 | 9 | 103 | PR-S07-04 | Prairie | 2026-01-09 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-000086 | 1520 | 8 | 190 | BY-S10-02 | Bayou | 2026-01-09 | 20 | Animal | Transformer fuse | Forced | None
OE-26-000087 | 1708 | 7 | 244 | CR-S14-05 | Crossroads | 2026-01-10 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000088 | 924 | 11 | 84 | HB-S09-04 | Harbor | 2026-01-10 | 10 | Animal | Transformer fuse | Forced | None
OE-26-000089 | 17700 | 354 | 50 | CR-S10-02 | Crossroads | 2026-01-10 | 11 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-000090 | 1350 | 10 | 135 | PR-S18-04 | Prairie | 2026-01-10 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000091 | 1098 | 6 | 183 | CR-S22-04 | Crossroads | 2026-01-10 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000092 | 19758 | 89 | 222 | PR-S19-02 | Prairie | 2026-01-10 | 17 | Animal | Lateral fuse | Forced | None
OE-26-000093 | 1536 | 8 | 192 | PR-S04-01 | Prairie | 2026-01-10 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000094 | 51090 | 390 | 131 | PR-S07-04 | Prairie | 2026-01-10 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000095 | 67440 | 1405 | 48 | CR-S05-01 | Crossroads | 2026-01-11 | 6 | Equipment - underground | Substation breaker | Forced | None
OE-26-000096 | 267 | 3 | 89 | HB-S04-02 | Harbor | 2026-01-11 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-000097 | 575 | 5 | 115 | HB-S11-01 | Harbor | 2026-01-11 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-000098 | 163 | 1 | 163 | BY-S15-02 | Bayou | 2026-01-11 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-000099 | 2912 | 13 | 224 | BY-S24-02 | Bayou | 2026-01-11 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-000100 | 668 | 4 | 167 | BY-S11-03 | Bayou | 2026-01-11 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000101 | 20700 | 150 | 138 | CR-S02-02 | Crossroads | 2026-01-11 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000102 | 1970 | 10 | 197 | CR-S26-02 | Crossroads | 2026-01-11 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000103 | 3080 | 70 | 44 | PR-S07-05 | Prairie | 2026-01-11 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000104 | 660 | 5 | 132 | PR-S07-06 | Prairie | 2026-01-11 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000105 | 20488 | 394 | 52 | PR-S16-04 | Prairie | 2026-01-11 | 17 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000106 | 1452 | 11 | 132 | BY-S23-03 | Bayou | 2026-01-11 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-000107 | 11070 | 90 | 123 | BY-S09-05 | Bayou | 2026-01-11 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000108 | 3587 | 17 | 211 | BY-S09-01 | Bayou | 2026-01-11 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-000109 | 27648 | 144 | 192 | CR-S07-05 | Crossroads | 2026-01-11 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000110 | 270 | 3 | 90 | CR-S20-05 | Crossroads | 2026-01-11 | 23 | Animal | Transformer fuse | Forced | None
OE-26-000111 | 795 | 5 | 159 | BY-S18-03 | Bayou | 2026-01-12 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000112 | 11388 | 73 | 156 | BY-S24-03 | Bayou | 2026-01-12 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000113 | 6519 | 53 | 123 | BY-S13-01 | Bayou | 2026-01-12 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000114 | 2259 | 9 | 251 | PR-S07-06 | Prairie | 2026-01-12 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-000115 | 8624 | 44 | 196 | PR-S01-06 | Prairie | 2026-01-12 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-26-000116 | 2256 | 12 | 188 | BY-S02-02 | Bayou | 2026-01-13 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000117 | 32900 | 658 | 50 | BY-S07-03 | Bayou | 2026-01-13 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000118 | 1890 | 27 | 70 | CR-S04-01 | Crossroads | 2026-01-13 | 10 | Animal | Lateral fuse | Forced | None
OE-26-000119 | 1122 | 11 | 102 | BY-S16-02 | Bayou | 2026-01-13 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000120 | 1632 | 12 | 136 | BY-S27-02 | Bayou | 2026-01-13 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000121 | 260448 | 2713 | 96 | BY-S13-06 | Bayou | 2026-01-13 | 18 | Vegetation | Substation breaker | Forced | None
OE-26-000122 | 19028 | 134 | 142 | CR-S18-04 | Crossroads | 2026-01-13 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-000123 | 304 | 4 | 76 | BY-S28-03 | Bayou | 2026-01-13 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-000124 | 1659 | 21 | 79 | BY-S08-02 | Bayou | 2026-01-13 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000125 | 55 | 1 | 55 | BY-S26-06 | Bayou | 2026-01-14 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000126 | 11640 | 60 | 194 | CR-S15-03 | Crossroads | 2026-01-14 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000127 | 2048 | 32 | 64 | HB-S11-02 | Harbor | 2026-01-14 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000128 | 565 | 5 | 113 | BY-S16-06 | Bayou | 2026-01-14 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000129 | 860 | 4 | 215 | CR-S26-01 | Crossroads | 2026-01-14 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000130 | 17496 | 729 | 24 | CR-S09-01 | Crossroads | 2026-01-14 | 11 | Vegetation | IGSD-isolated section | Forced | None
OE-26-000131 | 1764 | 12 | 147 | CR-S23-04 | Crossroads | 2026-01-14 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000132 | 9310 | 70 | 133 | PR-S09-04 | Prairie | 2026-01-14 | 15 | Animal | Lateral fuse | Forced | None
OE-26-000133 | 1242 | 6 | 207 | BY-S30-03 | Bayou | 2026-01-14 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000134 | 564 | 6 | 94 | HB-S03-02 | Harbor | 2026-01-14 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-000135 | 1276 | 11 | 116 | CR-S15-02 | Crossroads | 2026-01-14 | 22 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000136 | 1892 | 11 | 172 | CR-S19-01 | Crossroads | 2026-01-14 | 22 | Unknown | Transformer fuse | Forced | None
OE-26-000137 | 24272 | 164 | 148 | CR-S31-03 | Crossroads | 2026-01-15 | 4 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000138 | 60750 | 810 | 75 | PR-S05-03 | Prairie | 2026-01-15 | 6 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000139 | 710 | 10 | 71 | CR-S15-03 | Crossroads | 2026-01-15 | 7 | Animal | Transformer fuse | Forced | None
OE-26-000140 | 26386 | 167 | 158 | CR-S06-03 | Crossroads | 2026-01-15 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000141 | 49306 | 554 | 89 | BY-S03-01 | Bayou | 2026-01-15 | 9 | Animal | Feeder recloser | Forced | None
OE-26-000142 | 10944 | 96 | 114 | HB-S09-02 | Harbor | 2026-01-15 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000143 | 98700 | 700 | 141 | HB-S04-01 | Harbor | 2026-01-15 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-000144 | 3796 | 13 | 292 | CR-S06-01 | Crossroads | 2026-01-15 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-000145 | 37520 | 560 | 67 | PR-S13-03 | Prairie | 2026-01-15 | 14 | Weather - lightning | Substation breaker | Forced | None
OE-26-000146 | 560 | 7 | 80 | BY-S29-05 | Bayou | 2026-01-15 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000147 | 7520 | 94 | 80 | CR-S07-07 | Crossroads | 2026-01-15 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000148 | 1428 | 7 | 204 | HB-S03-02 | Harbor | 2026-01-15 | 16 | Animal | Transformer fuse | Forced | None
OE-26-000149 | 18090 | 335 | 54 | BY-S18-05 | Bayou | 2026-01-15 | 18 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-000150 | 151364 | 958 | 158 | CR-S01-03 | Crossroads | 2026-01-15 | 20 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000151 | 5754 | 42 | 137 | PR-S06-01 | Prairie | 2026-01-15 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-000152 | 3976 | 56 | 71 | BY-S29-01 | Bayou | 2026-01-16 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-000153 | 836 | 11 | 76 | BY-S05-02 | Bayou | 2026-01-16 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000154 | 4048 | 23 | 176 | PR-S18-04 | Prairie | 2026-01-16 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000155 | 8932 | 116 | 77 | BY-S09-02 | Bayou | 2026-01-16 | 12 | Unknown | Lateral fuse | Forced | None
OE-26-000156 | 3504 | 73 | 48 | CR-S12-03 | Crossroads | 2026-01-16 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000157 | 294125 | 1625 | 181 | PR-S14-04 | Prairie | 2026-01-16 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000158 | 314 | 2 | 157 | BY-S24-01 | Bayou | 2026-01-16 | 15 | Animal | Transformer fuse | Forced | None
OE-26-000159 | 71373 | 1929 | 37 | HB-S19-04 | Harbor | 2026-01-17 | 1 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-000160 | 2700 | 27 | 100 | PR-S09-01 | Prairie | 2026-01-17 | 5 | Animal | Lateral fuse | Forced | None
OE-26-000161 | 109155 | 1915 | 57 | CR-S24-03 | Crossroads | 2026-01-17 | 12 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000162 | 2464 | 32 | 77 | CR-S22-01 | Crossroads | 2026-01-17 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000163 | 3367 | 13 | 259 | PR-S02-02 | Prairie | 2026-01-17 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000164 | 84666 | 618 | 137 | PR-S14-02 | Prairie | 2026-01-17 | 22 | Weather - lightning | Substation breaker | Forced | None
OE-26-000165 | 4740 | 6 | 790 | BY-S19-02 | Bayou | 2026-01-18 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-000166 | 1463 | 11 | 133 | PR-S11-02 | Prairie | 2026-01-18 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-26-000167 | 2210 | 13 | 170 | CR-S32-01 | Crossroads | 2026-01-18 | 12 | Animal | Transformer fuse | Forced | None
OE-26-000168 | 440 | 2 | 220 | PR-S13-05 | Prairie | 2026-01-18 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000169 | 798 | 7 | 114 | PR-S06-03 | Prairie | 2026-01-18 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000170 | 2380 | 17 | 140 | HB-S07-02 | Harbor | 2026-01-18 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000171 | 12070 | 85 | 142 | HB-S18-01 | Harbor | 2026-01-18 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-000172 | 1960 | 10 | 196 | CR-S26-04 | Crossroads | 2026-01-18 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000173 | 2604 | 14 | 186 | CR-S30-06 | Crossroads | 2026-01-19 | 7 | Weather - wind | Transformer fuse | Forced | None
OE-26-000174 | 805 | 5 | 161 | HB-S16-04 | Harbor | 2026-01-19 | 8 | Animal | Transformer fuse | Forced | None
OE-26-000175 | 138 | 1 | 138 | BY-S26-02 | Bayou | 2026-01-19 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000176 | 8946 | 71 | 126 | CR-S15-02 | Crossroads | 2026-01-19 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000177 | 29120 | 320 | 91 | BY-S18-05 | Bayou | 2026-01-19 | 12 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-000178 | 395 | 5 | 79 | PR-S07-05 | Prairie | 2026-01-19 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000179 | 904 | 8 | 113 | PR-S12-02 | Prairie | 2026-01-19 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000180 | 2838 | 11 | 258 | BY-S18-04 | Bayou | 2026-01-19 | 16 | Animal | Transformer fuse | Forced | None
OE-26-000181 | 1128 | 4 | 282 | PR-S18-01 | Prairie | 2026-01-19 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000182 | 1000 | 8 | 125 | CR-S23-05 | Crossroads | 2026-01-19 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-000183 | 126 | 2 | 63 | BY-S13-06 | Bayou | 2026-01-19 | 18 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000184 | 525600 | 1752 | 300 | PR-S03-05 | Prairie | 2026-01-19 | 23 | Vegetation | Substation breaker | Forced | None
OE-26-000185 | 3087 | 21 | 147 | BY-S27-03 | Bayou | 2026-01-20 | 4 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000186 | 112894 | 2402 | 47 | HB-S18-01 | Harbor | 2026-01-20 | 6 | Unknown | Substation breaker | Outside cause | None
OE-26-000187 | 6732 | 132 | 51 | BY-S18-04 | Bayou | 2026-01-20 | 9 | Animal | Lateral fuse | Forced | None
OE-26-000188 | 7308 | 58 | 126 | PR-S18-03 | Prairie | 2026-01-20 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000189 | 2650 | 25 | 106 | CR-S20-01 | Crossroads | 2026-01-20 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000190 | 2940 | 10 | 294 | BY-S09-04 | Bayou | 2026-01-20 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000191 | 1144 | 8 | 143 | PR-S14-04 | Prairie | 2026-01-20 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000192 | 316 | 2 | 158 | HB-S18-01 | Harbor | 2026-01-20 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-26-000193 | 1968 | 12 | 164 | BY-S26-02 | Bayou | 2026-01-20 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-000194 | 726 | 11 | 66 | CR-S27-02 | Crossroads | 2026-01-20 | 23 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000195 | 34881 | 231 | 151 | BY-S04-02 | Bayou | 2026-01-21 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000196 | 14790 | 87 | 170 | PR-S19-05 | Prairie | 2026-01-21 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-000197 | 3952 | 38 | 104 | BY-S18-05 | Bayou | 2026-01-21 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000198 | 5225 | 25 | 209 | CR-S04-03 | Crossroads | 2026-01-21 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000199 | 7626 | 123 | 62 | CR-S09-05 | Crossroads | 2026-01-21 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000200 | 390 | 3 | 130 | HB-S20-02 | Harbor | 2026-01-21 | 14 | Animal | Transformer fuse | Forced | None
OE-26-000201 | 158 | 2 | 79 | CR-S05-02 | Crossroads | 2026-01-21 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000202 | 536142 | 4703 | 114 | HB-S12-02 | Harbor | 2026-01-21 | 16 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000203 | 1240 | 10 | 124 | BY-S06-02 | Bayou | 2026-01-21 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000204 | 166192 | 1222 | 136 | PR-S03-02 | Prairie | 2026-01-21 | 22 | Animal | Substation breaker | Forced | None
OE-26-000205 | 16524 | 153 | 108 | BY-S15-02 | Bayou | 2026-01-22 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000206 | 2379 | 13 | 183 | PR-S11-02 | Prairie | 2026-01-22 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000207 | 693 | 3 | 231 | CR-S06-02 | Crossroads | 2026-01-22 | 8 | Animal | Transformer fuse | Forced | None
OE-26-000208 | 112750 | 1025 | 110 | PR-S14-03 | Prairie | 2026-01-22 | 10 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000209 | 1216 | 38 | 32 | CR-S18-02 | Crossroads | 2026-01-22 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000210 | 2940 | 14 | 210 | PR-S06-01 | Prairie | 2026-01-22 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-000211 | 938 | 7 | 134 | PR-S17-01 | Prairie | 2026-01-22 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-000212 | 672 | 6 | 112 | BY-S27-05 | Bayou | 2026-01-22 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-000213 | 680 | 10 | 68 | CR-S05-01 | Crossroads | 2026-01-22 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000214 | 36905 | 605 | 61 | PR-S02-02 | Prairie | 2026-01-22 | 18 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000215 | 15884 | 76 | 209 | CR-S17-02 | Crossroads | 2026-01-22 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-000216 | 1620 | 9 | 180 | HB-S08-04 | Harbor | 2026-01-22 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000217 | 186538 | 1342 | 139 | HB-S08-05 | Harbor | 2026-01-23 | 7 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000218 | 10506 | 34 | 309 | PR-S13-03 | Prairie | 2026-01-23 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000219 | 14688 | 102 | 144 | BY-S28-01 | Bayou | 2026-01-23 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000220 | 3213 | 27 | 119 | BY-S07-01 | Bayou | 2026-01-23 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000221 | 177468 | 1286 | 138 | BY-S13-06 | Bayou | 2026-01-23 | 13 | Vegetation | Feeder recloser | Forced | None
OE-26-000222 | 3880 | 10 | 388 | CR-S04-06 | Crossroads | 2026-01-23 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-000223 | 294 | 6 | 49 | BY-S05-02 | Bayou | 2026-01-23 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-000224 | 2535 | 13 | 195 | BY-S06-01 | Bayou | 2026-01-23 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-000225 | 1904 | 7 | 272 | HB-S18-03 | Harbor | 2026-01-23 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-000226 | 13940 | 68 | 205 | BY-S15-05 | Bayou | 2026-01-23 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-000227 | 43292 | 316 | 137 | PR-S01-01 | Prairie | 2026-01-23 | 21 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000228 | 1323 | 7 | 189 | BY-S03-02 | Bayou | 2026-01-23 | 22 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000229 | 1650 | 50 | 33 | HB-S01-01 | Harbor | 2026-01-24 | 5 | Vegetation | Lateral fuse | Forced | None
OE-26-000230 | 3600 | 60 | 60 | CR-S31-02 | Crossroads | 2026-01-24 | 6 | Vehicle or public | Lateral fuse | Forced | None
OE-26-000231 | 213 | 1 | 213 | BY-S18-02 | Bayou | 2026-01-24 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-000232 | 24824 | 214 | 116 | HB-S14-03 | Harbor | 2026-01-24 | 9 | Weather - wind | IGSD-isolated section | Forced | None
OE-26-000233 | 51865 | 253 | 205 | PR-S15-02 | Prairie | 2026-01-24 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000234 | 2499 | 51 | 49 | BY-S16-05 | Bayou | 2026-01-24 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-000235 | 2574 | 26 | 99 | BY-S29-05 | Bayou | 2026-01-24 | 10 | Unknown | Lateral fuse | Forced | None
OE-26-000236 | 1656 | 12 | 138 | PR-S19-05 | Prairie | 2026-01-24 | 10 | Animal | Transformer fuse | Forced | None
OE-26-000237 | 649 | 11 | 59 | CR-S28-02 | Crossroads | 2026-01-24 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-000238 | 1980 | 10 | 198 | BY-S29-01 | Bayou | 2026-01-24 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000239 | 25636 | 754 | 34 | PR-S19-05 | Prairie | 2026-01-24 | 14 | Vegetation | Feeder recloser | Forced | None
OE-26-000240 | 640 | 10 | 64 | BY-S01-01 | Bayou | 2026-01-24 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-000241 | 2409 | 11 | 219 | CR-S08-05 | Crossroads | 2026-01-24 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000242 | 41785 | 305 | 137 | BY-S11-03 | Bayou | 2026-01-24 | 18 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-000243 | 1222 | 13 | 94 | BY-S26-01 | Bayou | 2026-01-24 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-000244 | 7276 | 214 | 34 | HB-S01-02 | Harbor | 2026-01-24 | 18 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000245 | 295 | 5 | 59 | CR-S07-07 | Crossroads | 2026-01-25 | 9 | Unknown | Transformer fuse | Forced | None
OE-26-000246 | 1391 | 13 | 107 | CR-S14-06 | Crossroads | 2026-01-25 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000247 | 864 | 6 | 144 | CR-S15-02 | Crossroads | 2026-01-25 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000248 | 1344 | 8 | 168 | BY-S07-06 | Bayou | 2026-01-25 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-000249 | 22770 | 495 | 46 | CR-S28-03 | Crossroads | 2026-01-25 | 14 | Vehicle or public | IGSD-isolated section | Forced | None
OE-26-000250 | 2968 | 14 | 212 | HB-S19-04 | Harbor | 2026-01-25 | 14 | Animal | Transformer fuse | Forced | None
OE-26-000251 | 60760 | 620 | 98 | HB-S20-02 | Harbor | 2026-01-25 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000252 | 2992 | 68 | 44 | CR-S01-02 | Crossroads | 2026-01-25 | 16 | Animal | Lateral fuse | Forced | None
OE-26-000253 | 61705 | 301 | 205 | CR-S13-01 | Crossroads | 2026-01-25 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000254 | 301822 | 1318 | 229 | CR-S01-03 | Crossroads | 2026-01-25 | 20 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000255 | 670 | 5 | 134 | BY-S02-02 | Bayou | 2026-01-25 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-000256 | 2211 | 11 | 201 | CR-S14-04 | Crossroads | 2026-01-26 | 9 | Animal | Transformer fuse | Forced | None
OE-26-000257 | 9912 | 56 | 177 | PR-S07-06 | Prairie | 2026-01-26 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-000258 | 17613 | 103 | 171 | BY-S06-01 | Bayou | 2026-01-26 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000259 | 2535 | 13 | 195 | PR-S15-01 | Prairie | 2026-01-26 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000260 | 4278 | 46 | 93 | PR-S18-01 | Prairie | 2026-01-26 | 12 | Unknown | Lateral fuse | Forced | None
OE-26-000261 | 6162 | 39 | 158 | PR-S18-06 | Prairie | 2026-01-26 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000262 | 4446 | 39 | 114 | BY-S11-01 | Bayou | 2026-01-26 | 18 | Animal | Lateral fuse | Forced | None
OE-26-000263 | 1796 | 4 | 449 | PR-S13-06 | Prairie | 2026-01-26 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000264 | 4002 | 46 | 87 | BY-S16-01 | Bayou | 2026-01-26 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-26-000265 | 69030 | 885 | 78 | CR-S09-03 | Crossroads | 2026-01-26 | 20 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000266 | 2884 | 14 | 206 | CR-S16-06 | Crossroads | 2026-01-26 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000267 | 2870 | 41 | 70 | CR-S07-01 | Crossroads | 2026-01-27 | 0 | Vegetation | Lateral fuse | Forced | None
OE-26-000268 | 24552 | 132 | 186 | PR-S18-03 | Prairie | 2026-01-27 | 0 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000269 | 19602 | 54 | 363 | PR-S15-04 | Prairie | 2026-01-27 | 2 | Weather - wind | Lateral fuse | Forced | None
OE-26-000270 | 12627 | 69 | 183 | BY-S24-01 | Bayou | 2026-01-27 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000271 | 2769 | 13 | 213 | PR-S14-01 | Prairie | 2026-01-27 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-000272 | 3014 | 11 | 274 | BY-S25-05 | Bayou | 2026-01-27 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-000273 | 113 | 1 | 113 | BY-S27-04 | Bayou | 2026-01-27 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000274 | 1469 | 13 | 113 | HB-S15-02 | Harbor | 2026-01-27 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000275 | 19317 | 141 | 137 | PR-S17-01 | Prairie | 2026-01-27 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000276 | 29222 | 769 | 38 | CR-S19-02 | Crossroads | 2026-01-27 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000277 | 8536 | 44 | 194 | PR-S05-01 | Prairie | 2026-01-27 | 19 | Animal | Lateral fuse | Forced | None
OE-26-000278 | 800 | 4 | 200 | HB-S20-03 | Harbor | 2026-01-27 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000279 | 508 | 4 | 127 | HB-S15-02 | Harbor | 2026-01-28 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000280 | 8250 | 55 | 150 | BY-S18-03 | Bayou | 2026-01-28 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000281 | 4320 | 45 | 96 | PR-S16-02 | Prairie | 2026-01-28 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000282 | 100842 | 1029 | 98 | BY-S23-01 | Bayou | 2026-01-28 | 11 | Animal | Feeder recloser | Forced | None
OE-26-000283 | 39240 | 1308 | 30 | HB-S06-01 | Harbor | 2026-01-28 | 11 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-000284 | 2054 | 13 | 158 | PR-S01-03 | Prairie | 2026-01-28 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000285 | 5781 | 47 | 123 | CR-S09-02 | Crossroads | 2026-01-28 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000286 | 122400 | 1200 | 102 | CR-S10-01 | Crossroads | 2026-01-28 | 13 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-000287 | 9592 | 88 | 109 | HB-S05-05 | Harbor | 2026-01-28 | 13 | Vehicle or public | Lateral fuse | Forced | None
OE-26-000288 | 3564 | 54 | 66 | PR-S01-01 | Prairie | 2026-01-28 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-000289 | 12312 | 114 | 108 | BY-S10-02 | Bayou | 2026-01-28 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000290 | 38976 | 1624 | 24 | HB-S09-02 | Harbor | 2026-01-28 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000291 | 230955 | 865 | 267 | CR-S05-01 | Crossroads | 2026-01-28 | 19 | Vegetation | Feeder recloser | Forced | None
OE-26-000292 | 783 | 9 | 87 | CR-S25-03 | Crossroads | 2026-01-28 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000293 | 6027 | 41 | 147 | PR-S15-02 | Prairie | 2026-01-29 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000294 | 3052 | 14 | 218 | HB-S09-05 | Harbor | 2026-01-29 | 11 | Animal | Transformer fuse | Forced | None
OE-26-000295 | 245674 | 859 | 286 | PR-S02-03 | Prairie | 2026-01-29 | 11 | Animal | Substation breaker | Forced | None
OE-26-000296 | 9324 | 111 | 84 | CR-S18-02 | Crossroads | 2026-01-29 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000297 | 34104 | 232 | 147 | BY-S26-02 | Bayou | 2026-01-29 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-000298 | 128338 | 1246 | 103 | BY-S17-02 | Bayou | 2026-01-29 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-26-000299 | 755 | 5 | 151 | HB-S03-01 | Harbor | 2026-01-29 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-000300 | 2484 | 9 | 276 | PR-S09-04 | Prairie | 2026-01-29 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000301 | 1074 | 6 | 179 | PR-S18-01 | Prairie | 2026-01-29 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000302 | 972 | 9 | 108 | HB-S05-01 | Harbor | 2026-01-29 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000303 | 2169 | 9 | 241 | HB-S20-02 | Harbor | 2026-01-30 | 5 | Weather - wind | Transformer fuse | Forced | None
OE-26-000304 | 3108 | 42 | 74 | HB-S02-01 | Harbor | 2026-01-30 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000305 | 2079 | 21 | 99 | CR-S10-02 | Crossroads | 2026-01-30 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-000306 | 950 | 10 | 95 | CR-S32-03 | Crossroads | 2026-01-30 | 10 | Unknown | Transformer fuse | Forced | None
OE-26-000307 | 7670 | 118 | 65 | BY-S16-06 | Bayou | 2026-01-30 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-000308 | 32754 | 309 | 106 | PR-S03-04 | Prairie | 2026-01-30 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-000309 | 2123 | 11 | 193 | BY-S20-01 | Bayou | 2026-01-30 | 16 | Unknown | Transformer fuse | Forced | None
OE-26-000310 | 3864 | 42 | 92 | BY-S16-06 | Bayou | 2026-01-31 | 3 | Weather - wind | Lateral fuse | Forced | None
OE-26-000311 | 31080 | 518 | 60 | BY-S17-03 | Bayou | 2026-01-31 | 8 | Vegetation | Feeder recloser | Forced | None
OE-26-000312 | 501 | 3 | 167 | BY-S29-02 | Bayou | 2026-01-31 | 8 | Animal | Transformer fuse | Forced | None
OE-26-000313 | 822 | 2 | 411 | BY-S25-03 | Bayou | 2026-01-31 | 15 | Animal | Transformer fuse | Forced | None
OE-26-000314 | 15708 | 231 | 68 | HB-S07-02 | Harbor | 2026-01-31 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000315 | 29596 | 196 | 151 | HB-S20-04 | Harbor | 2026-01-31 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000316 | 1813 | 37 | 49 | PR-S18-01 | Prairie | 2026-01-31 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-26-000317 | 1729 | 13 | 133 | HB-S10-01 | Harbor | 2026-01-31 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000318 | 62750 | 1255 | 50 | CR-S31-01 | Crossroads | 2026-02-01 | 7 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000319 | 44370 | 510 | 87 | HB-S09-03 | Harbor | 2026-02-01 | 7 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-000320 | 55106 | 467 | 118 | HB-S16-04 | Harbor | 2026-02-01 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000321 | 1110 | 10 | 111 | CR-S17-01 | Crossroads | 2026-02-01 | 14 | Animal | Transformer fuse | Forced | None
OE-26-000322 | 1446 | 6 | 241 | PR-S11-01 | Prairie | 2026-02-01 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000323 | 408 | 4 | 102 | PR-S05-01 | Prairie | 2026-02-01 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-000324 | 64512 | 512 | 126 | BY-S07-02 | Bayou | 2026-02-01 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-000325 | 33975 | 225 | 151 | HB-S09-03 | Harbor | 2026-02-01 | 22 | Vegetation | IGSD-isolated section | Forced | None
OE-26-000326 | 8636 | 34 | 254 | CR-S04-01 | Crossroads | 2026-02-02 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000327 | 22176 | 224 | 99 | BY-S07-04 | Bayou | 2026-02-02 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000328 | 2390 | 10 | 239 | PR-S03-05 | Prairie | 2026-02-02 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-000329 | 10428 | 79 | 132 | BY-S23-02 | Bayou | 2026-02-02 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000330 | 10692 | 66 | 162 | CR-S22-04 | Crossroads | 2026-02-02 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000331 | 3796 | 26 | 146 | PR-S16-05 | Prairie | 2026-02-02 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000332 | 56375 | 1025 | 55 | BY-S29-05 | Bayou | 2026-02-02 | 14 | Vegetation | Substation breaker | Forced | None
OE-26-000333 | 8343 | 103 | 81 | CR-S03-03 | Crossroads | 2026-02-02 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-000334 | 5143 | 139 | 37 | CR-S32-01 | Crossroads | 2026-02-02 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000335 | 47249 | 1277 | 37 | HB-S02-03 | Harbor | 2026-02-03 | 3 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000336 | 1936 | 8 | 242 | PR-S05-01 | Prairie | 2026-02-03 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-000337 | 632 | 8 | 79 | BY-S19-04 | Bayou | 2026-02-03 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000338 | 2400 | 40 | 60 | CR-S28-03 | Crossroads | 2026-02-03 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000339 | 5828 | 31 | 188 | HB-S08-05 | Harbor | 2026-02-03 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000340 | 316 | 1 | 316 | PR-S11-03 | Prairie | 2026-02-03 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-000341 | 1632 | 12 | 136 | HB-S14-04 | Harbor | 2026-02-04 | 12 | Animal | Transformer fuse | Forced | None
OE-26-000342 | 186098 | 1538 | 121 | BY-S29-02 | Bayou | 2026-02-04 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000343 | 12408 | 132 | 94 | CR-S25-05 | Crossroads | 2026-02-04 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000344 | 8910 | 45 | 198 | BY-S29-01 | Bayou | 2026-02-04 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000345 | 459 | 3 | 153 | BY-S12-04 | Bayou | 2026-02-04 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-000346 | 3680 | 40 | 92 | BY-S18-01 | Bayou | 2026-02-05 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000347 | 2388 | 12 | 199 | PR-S07-05 | Prairie | 2026-02-05 | 11 | Animal | Transformer fuse | Forced | None
OE-26-000348 | 3416 | 28 | 122 | BY-S14-02 | Bayou | 2026-02-05 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000349 | 16465 | 445 | 37 | BY-S14-03 | Bayou | 2026-02-05 | 12 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000350 | 30450 | 350 | 87 | CR-S09-05 | Crossroads | 2026-02-05 | 13 | Vehicle or public | Feeder recloser | Forced | None
OE-26-000351 | 48755 | 1393 | 35 | CR-S17-03 | Crossroads | 2026-02-05 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000352 | 7476 | 89 | 84 | PR-S11-01 | Prairie | 2026-02-05 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000353 | 3066 | 42 | 73 | HB-S15-02 | Harbor | 2026-02-05 | 14 | Animal | Lateral fuse | Forced | None
OE-26-000354 | 41912 | 676 | 62 | CR-S30-05 | Crossroads | 2026-02-05 | 16 | Animal | Feeder recloser | Forced | None
OE-26-000355 | 46102 | 74 | 623 | BY-S10-01 | Bayou | 2026-02-05 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000356 | 57939 | 623 | 93 | CR-S17-01 | Crossroads | 2026-02-05 | 23 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-000357 | 4343 | 43 | 101 | CR-S09-01 | Crossroads | 2026-02-06 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000358 | 13348 | 71 | 188 | BY-S13-05 | Bayou | 2026-02-06 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-000359 | 17324 | 142 | 122 | HB-S17-02 | Harbor | 2026-02-06 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000360 | 13608 | 252 | 54 | CR-S07-02 | Crossroads | 2026-02-06 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-000361 | 1690 | 10 | 169 | CR-S09-01 | Crossroads | 2026-02-06 | 11 | Animal | Transformer fuse | Forced | None
OE-26-000362 | 4042 | 47 | 86 | CR-S09-03 | Crossroads | 2026-02-06 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000363 | 25311 | 143 | 177 | BY-S19-01 | Bayou | 2026-02-06 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-000364 | 24645 | 159 | 155 | PR-S07-02 | Prairie | 2026-02-06 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000365 | 11102 | 91 | 122 | BY-S01-02 | Bayou | 2026-02-06 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-26-000366 | 630 | 7 | 90 | CR-S14-01 | Crossroads | 2026-02-07 | 2 | Vegetation | Transformer fuse | Forced | None
OE-26-000367 | 39596 | 521 | 76 | HB-S16-05 | Harbor | 2026-02-07 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000368 | 1127 | 7 | 161 | CR-S23-01 | Crossroads | 2026-02-07 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000369 | 3948 | 14 | 282 | PR-S02-02 | Prairie | 2026-02-07 | 8 | Unknown | Transformer fuse | Forced | None
OE-26-000370 | 5454 | 54 | 101 | PR-S10-01 | Prairie | 2026-02-07 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000371 | 11400 | 150 | 76 | BY-S13-05 | Bayou | 2026-02-07 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000372 | 56502 | 1314 | 43 | CR-S05-01 | Crossroads | 2026-02-07 | 10 | Equipment - underground | Substation breaker | Forced | None
OE-26-000373 | 3649 | 41 | 89 | PR-S01-03 | Prairie | 2026-02-07 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-000374 | 66430 | 910 | 73 | BY-S17-01 | Bayou | 2026-02-07 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000375 | 1235 | 19 | 65 | HB-S08-03 | Harbor | 2026-02-07 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000376 | 1896 | 12 | 158 | BY-S16-05 | Bayou | 2026-02-07 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-000377 | 1935 | 15 | 129 | HB-S09-04 | Harbor | 2026-02-07 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000378 | 532 | 2 | 266 | HB-S06-02 | Harbor | 2026-02-07 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-000379 | 1716 | 39 | 44 | HB-S17-02 | Harbor | 2026-02-07 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000380 | 6510 | 70 | 93 | HB-S19-01 | Harbor | 2026-02-07 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000381 | 27018 | 171 | 158 | BY-S19-01 | Bayou | 2026-02-08 | 5 | Animal | Lateral fuse | Forced | None
OE-26-000382 | 73040 | 1328 | 55 | CR-S15-01 | Crossroads | 2026-02-08 | 7 | Vehicle or public | Feeder recloser | Forced | None
OE-26-000383 | 14476 | 44 | 329 | CR-S20-03 | Crossroads | 2026-02-08 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-26-000384 | 1785 | 5 | 357 | BY-S11-01 | Bayou | 2026-02-08 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-000385 | 185194 | 1798 | 103 | HB-S20-01 | Harbor | 2026-02-08 | 11 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000386 | 37920 | 790 | 48 | CR-S23-02 | Crossroads | 2026-02-08 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000387 | 1340 | 10 | 134 | PR-S06-03 | Prairie | 2026-02-08 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000388 | 3696 | 42 | 88 | PR-S07-06 | Prairie | 2026-02-08 | 15 | Unknown | Lateral fuse | Forced | None
OE-26-000389 | 1350 | 9 | 150 | PR-S20-03 | Prairie | 2026-02-08 | 19 | Animal | Transformer fuse | Forced | None
OE-26-000390 | 182736 | 1128 | 162 | BY-S17-04 | Bayou | 2026-02-08 | 20 | Weather - wind | Feeder recloser | Forced | None
OE-26-000391 | 2496 | 32 | 78 | HB-S03-03 | Harbor | 2026-02-08 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000392 | 642 | 6 | 107 | HB-S15-03 | Harbor | 2026-02-08 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000393 | 1350 | 10 | 135 | CR-S32-05 | Crossroads | 2026-02-09 | 0 | Animal | Transformer fuse | Forced | None
OE-26-000394 | 24073 | 1267 | 19 | BY-S06-03 | Bayou | 2026-02-09 | 2 | Unknown | Substation breaker | Outside cause | None
OE-26-000395 | 61901 | 259 | 239 | PR-S17-02 | Prairie | 2026-02-09 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-26-000396 | 112 | 2 | 56 | BY-S08-01 | Bayou | 2026-02-09 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-000397 | 8646 | 33 | 262 | BY-S16-02 | Bayou | 2026-02-09 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000398 | 900 | 5 | 180 | BY-S20-01 | Bayou | 2026-02-09 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-000399 | 637 | 7 | 91 | PR-S03-02 | Prairie | 2026-02-09 | 12 | Animal | Transformer fuse | Forced | None
OE-26-000400 | 22344 | 84 | 266 | BY-S24-02 | Bayou | 2026-02-09 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000401 | 294 | 3 | 98 | CR-S16-06 | Crossroads | 2026-02-09 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000402 | 516 | 6 | 86 | HB-S07-03 | Harbor | 2026-02-09 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000403 | 5412 | 44 | 123 | PR-S03-02 | Prairie | 2026-02-09 | 16 | Animal | Lateral fuse | Forced | None
OE-26-000404 | 28060 | 115 | 244 | PR-S20-01 | Prairie | 2026-02-09 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-000405 | 38054 | 106 | 359 | HB-S20-05 | Harbor | 2026-02-09 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000406 | 2320 | 40 | 58 | HB-S15-03 | Harbor | 2026-02-09 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-000407 | 1880 | 5 | 376 | CR-S21-01 | Crossroads | 2026-02-09 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000408 | 848 | 8 | 106 | CR-S25-06 | Crossroads | 2026-02-10 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000409 | 194 | 2 | 97 | BY-S26-02 | Bayou | 2026-02-10 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-000410 | 17510 | 170 | 103 | BY-S28-03 | Bayou | 2026-02-10 | 11 | Animal | Lateral fuse | Forced | None
OE-26-000411 | 1211 | 7 | 173 | BY-S16-04 | Bayou | 2026-02-10 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000412 | 38766 | 497 | 78 | PR-S07-03 | Prairie | 2026-02-10 | 14 | Vegetation | Feeder recloser | Forced | None
OE-26-000413 | 1309 | 7 | 187 | PR-S03-03 | Prairie | 2026-02-10 | 16 | Animal | Transformer fuse | Forced | None
OE-26-000414 | 1572 | 12 | 131 | CR-S23-05 | Crossroads | 2026-02-10 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000415 | 3150 | 14 | 225 | PR-S01-04 | Prairie | 2026-02-10 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000416 | 1376 | 4 | 344 | HB-S14-01 | Harbor | 2026-02-11 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-000417 | 20193 | 159 | 127 | CR-S15-03 | Crossroads | 2026-02-11 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000418 | 34918 | 158 | 221 | PR-S14-04 | Prairie | 2026-02-11 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000419 | 13450 | 50 | 269 | CR-S20-05 | Crossroads | 2026-02-11 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000420 | 4738 | 46 | 103 | CR-S05-03 | Crossroads | 2026-02-11 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000421 | 29555 | 115 | 257 | BY-S24-03 | Bayou | 2026-02-11 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000422 | 1736 | 8 | 217 | BY-S24-04 | Bayou | 2026-02-11 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000423 | 1232 | 14 | 88 | CR-S05-01 | Crossroads | 2026-02-11 | 14 | Animal | Transformer fuse | Forced | None
OE-26-000424 | 448 | 14 | 32 | CR-S21-03 | Crossroads | 2026-02-11 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000425 | 64554 | 742 | 87 | CR-S20-02 | Crossroads | 2026-02-11 | 17 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-000426 | 117856 | 928 | 127 | PR-S15-03 | Prairie | 2026-02-11 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000427 | 14986 | 118 | 127 | BY-S17-04 | Bayou | 2026-02-11 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000428 | 1856 | 8 | 232 | BY-S19-03 | Bayou | 2026-02-11 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000429 | 2236 | 13 | 172 | BY-S16-06 | Bayou | 2026-02-12 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000430 | 4329 | 37 | 117 | CR-S12-01 | Crossroads | 2026-02-12 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-26-000431 | 56286 | 531 | 106 | PR-S16-05 | Prairie | 2026-02-12 | 11 | Vegetation | Feeder recloser | Forced | None
OE-26-000432 | 5796 | 36 | 161 | BY-S16-01 | Bayou | 2026-02-12 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000433 | 36516 | 1074 | 34 | CR-S03-01 | Crossroads | 2026-02-12 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000434 | 56744 | 328 | 173 | BY-S22-01 | Bayou | 2026-02-12 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000435 | 280 | 5 | 56 | BY-S17-02 | Bayou | 2026-02-12 | 15 | Animal | Lateral fuse | Forced | None
OE-26-000436 | 156 | 2 | 78 | CR-S09-01 | Crossroads | 2026-02-13 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000437 | 3197 | 23 | 139 | BY-S25-04 | Bayou | 2026-02-13 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000438 | 2494 | 43 | 58 | PR-S05-02 | Prairie | 2026-02-13 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000439 | 74 | 2 | 37 | BY-S10-05 | Bayou | 2026-02-14 | 4 | Animal | Transformer fuse | Forced | None
OE-26-000440 | 33888 | 353 | 96 | CR-S05-03 | Crossroads | 2026-02-14 | 6 | Weather - wind | IGSD-isolated section | Forced | None
OE-26-000441 | 2990 | 13 | 230 | CR-S13-06 | Crossroads | 2026-02-14 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-000442 | 2280 | 12 | 190 | CR-S04-03 | Crossroads | 2026-02-14 | 9 | Unknown | Transformer fuse | Forced | None
OE-26-000443 | 670 | 10 | 67 | BY-S29-05 | Bayou | 2026-02-14 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000444 | 900 | 5 | 180 | BY-S05-02 | Bayou | 2026-02-14 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000445 | 845 | 5 | 169 | BY-S09-01 | Bayou | 2026-02-14 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000446 | 2241 | 27 | 83 | BY-S09-03 | Bayou | 2026-02-14 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000447 | 417605 | 1445 | 289 | HB-S12-01 | Harbor | 2026-02-14 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-000448 | 648 | 8 | 81 | PR-S17-01 | Prairie | 2026-02-14 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000449 | 1764 | 12 | 147 | BY-S23-03 | Bayou | 2026-02-14 | 17 | Animal | Transformer fuse | Forced | None
OE-26-000450 | 1456 | 14 | 104 | HB-S01-01 | Harbor | 2026-02-14 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000451 | 12610 | 130 | 97 | PR-S02-02 | Prairie | 2026-02-14 | 17 | Animal | Lateral fuse | Forced | None
OE-26-000452 | 1242 | 9 | 138 | HB-S19-04 | Harbor | 2026-02-14 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000453 | 1267 | 7 | 181 | CR-S12-02 | Crossroads | 2026-02-15 | 5 | Unknown | Transformer fuse | Forced | None
OE-26-000454 | 3290 | 14 | 235 | CR-S14-01 | Crossroads | 2026-02-15 | 8 | Unknown | Transformer fuse | Forced | None
OE-26-000455 | 38700 | 129 | 300 | PR-S15-01 | Prairie | 2026-02-15 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000456 | 13261 | 89 | 149 | BY-S21-04 | Bayou | 2026-02-15 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-26-000457 | 3003 | 13 | 231 | CR-S09-01 | Crossroads | 2026-02-15 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000458 | 420 | 21 | 20 | CR-S16-05 | Crossroads | 2026-02-15 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000459 | 17640 | 126 | 140 | CR-S18-04 | Crossroads | 2026-02-15 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000460 | 26403 | 677 | 39 | BY-S13-06 | Bayou | 2026-02-15 | 15 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-000461 | 21505 | 935 | 23 | CR-S09-01 | Crossroads | 2026-02-15 | 15 | Unknown | Feeder recloser | Forced | None
OE-26-000462 | 2392 | 23 | 104 | BY-S23-01 | Bayou | 2026-02-15 | 16 | Animal | Lateral fuse | Forced | None
OE-26-000463 | 64757 | 2233 | 29 | PR-S10-03 | Prairie | 2026-02-15 | 19 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000464 | 1640 | 5 | 328 | BY-S07-02 | Bayou | 2026-02-15 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-000465 | 60984 | 847 | 72 | CR-S14-01 | Crossroads | 2026-02-16 | 7 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000466 | 2080 | 13 | 160 | HB-S14-01 | Harbor | 2026-02-16 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000467 | 1112 | 4 | 278 | BY-S16-04 | Bayou | 2026-02-16 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000468 | 615 | 5 | 123 | CR-S09-01 | Crossroads | 2026-02-16 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000469 | 76137 | 1857 | 41 | CR-S14-05 | Crossroads | 2026-02-16 | 13 | Equipment - underground | Substation breaker | Forced | None
OE-26-000470 | 1494 | 9 | 166 | BY-S24-01 | Bayou | 2026-02-16 | 14 | Animal | Lateral fuse | Forced | None
OE-26-000471 | 2220 | 60 | 37 | CR-S04-01 | Crossroads | 2026-02-16 | 16 | Animal | Lateral fuse | Forced | None
OE-26-000472 | 762 | 6 | 127 | BY-S16-04 | Bayou | 2026-02-16 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000473 | 825 | 3 | 275 | BY-S01-01 | Bayou | 2026-02-16 | 22 | Vegetation | Transformer fuse | Forced | None
OE-26-000474 | 1365 | 5 | 273 | HB-S15-02 | Harbor | 2026-02-16 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000475 | 1008 | 8 | 126 | CR-S15-01 | Crossroads | 2026-02-17 | 1 | Animal | Transformer fuse | Forced | None
OE-26-000476 | 15618 | 137 | 114 | BY-S24-01 | Bayou | 2026-02-17 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000477 | 3192 | 28 | 114 | CR-S25-01 | Crossroads | 2026-02-17 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000478 | 152 | 1 | 152 | PR-S05-02 | Prairie | 2026-02-17 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-000479 | 852 | 6 | 142 | BY-S20-03 | Bayou | 2026-02-17 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000480 | 1352 | 8 | 169 | BY-S08-03 | Bayou | 2026-02-17 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000481 | 75735 | 459 | 165 | BY-S12-02 | Bayou | 2026-02-17 | 11 | Unknown | Lateral fuse | Forced | None
OE-26-000482 | 1140 | 12 | 95 | CR-S04-05 | Crossroads | 2026-02-17 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-000483 | 3266 | 23 | 142 | HB-S05-01 | Harbor | 2026-02-17 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-000484 | 4681 | 31 | 151 | CR-S05-05 | Crossroads | 2026-02-17 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000485 | 1812 | 12 | 151 | HB-S08-05 | Harbor | 2026-02-17 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-000486 | 10080 | 168 | 60 | HB-S12-01 | Harbor | 2026-02-17 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000487 | 1190 | 10 | 119 | PR-S08-03 | Prairie | 2026-02-17 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000488 | 44330 | 286 | 155 | BY-S19-02 | Bayou | 2026-02-17 | 22 | Animal | Lateral fuse | Forced | None
OE-26-000489 | 994 | 7 | 142 | PR-S07-05 | Prairie | 2026-02-18 | 3 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000490 | 5198 | 46 | 113 | PR-S06-03 | Prairie | 2026-02-18 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-000491 | 1764 | 14 | 126 | CR-S07-03 | Crossroads | 2026-02-18 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000492 | 55278 | 666 | 83 | CR-S07-01 | Crossroads | 2026-02-18 | 12 | Weather - wind | Feeder recloser | Forced | None
OE-26-000493 | 61065 | 885 | 69 | BY-S27-06 | Bayou | 2026-02-18 | 13 | Animal | Feeder recloser | Forced | None
OE-26-000494 | 35728 | 638 | 56 | CR-S31-01 | Crossroads | 2026-02-18 | 13 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-000495 | 6120 | 102 | 60 | BY-S14-01 | Bayou | 2026-02-18 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-000496 | 1470 | 10 | 147 | BY-S15-01 | Bayou | 2026-02-18 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-000497 | 363 | 1 | 363 | BY-S17-03 | Bayou | 2026-02-18 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000498 | 582 | 6 | 97 | CR-S07-07 | Crossroads | 2026-02-18 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000499 | 7906 | 67 | 118 | HB-S05-03 | Harbor | 2026-02-18 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-000500 | 5310 | 59 | 90 | BY-S07-02 | Bayou | 2026-02-18 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-000501 | 2575 | 25 | 103 | CR-S25-01 | Crossroads | 2026-02-19 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000502 | 1099 | 7 | 157 | PR-S10-02 | Prairie | 2026-02-19 | 13 | Animal | Transformer fuse | Forced | None
OE-26-000503 | 5850 | 90 | 65 | CR-S19-02 | Crossroads | 2026-02-19 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-000504 | 620 | 5 | 124 | BY-S02-01 | Bayou | 2026-02-19 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000505 | 1085 | 7 | 155 | HB-S12-02 | Harbor | 2026-02-19 | 16 | Animal | Transformer fuse | Forced | None
OE-26-000506 | 159732 | 918 | 174 | PR-S08-01 | Prairie | 2026-02-19 | 17 | Vegetation | Feeder recloser | Forced | None
OE-26-000507 | 2898 | 23 | 126 | CR-S16-04 | Crossroads | 2026-02-19 | 18 | Animal | Lateral fuse | Forced | None
OE-26-000508 | 2700 | 6 | 450 | PR-S17-02 | Prairie | 2026-02-20 | 1 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000509 | 966 | 7 | 138 | HB-S16-01 | Harbor | 2026-02-20 | 6 | Animal | Transformer fuse | Forced | None
OE-26-000510 | 18054 | 153 | 118 | CR-S01-04 | Crossroads | 2026-02-20 | 8 | Animal | Lateral fuse | Forced | None
OE-26-000511 | 16019 | 83 | 193 | PR-S01-02 | Prairie | 2026-02-20 | 8 | Animal | Lateral fuse | Forced | None
OE-26-000512 | 7644 | 84 | 91 | BY-S21-04 | Bayou | 2026-02-20 | 10 | Animal | Lateral fuse | Forced | None
OE-26-000513 | 52130 | 802 | 65 | CR-S09-05 | Crossroads | 2026-02-20 | 11 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000514 | 1616 | 8 | 202 | PR-S01-03 | Prairie | 2026-02-20 | 11 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000515 | 1812 | 12 | 151 | PR-S07-03 | Prairie | 2026-02-20 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000516 | 999 | 3 | 333 | PR-S10-02 | Prairie | 2026-02-20 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-000517 | 251 | 1 | 251 | PR-S10-03 | Prairie | 2026-02-20 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000518 | 1834 | 7 | 262 | PR-S14-04 | Prairie | 2026-02-20 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-000519 | 186 | 1 | 186 | BY-S03-01 | Bayou | 2026-02-20 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000520 | 993 | 3 | 331 | BY-S21-03 | Bayou | 2026-02-20 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-000521 | 1540 | 5 | 308 | PR-S03-06 | Prairie | 2026-02-20 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000522 | 875 | 7 | 125 | BY-S07-03 | Bayou | 2026-02-20 | 22 | Vegetation | Transformer fuse | Forced | None
OE-26-000523 | 124542 | 1887 | 66 | CR-S04-06 | Crossroads | 2026-02-21 | 7 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000524 | 1428 | 12 | 119 | BY-S05-01 | Bayou | 2026-02-21 | 8 | Animal | Transformer fuse | Forced | None
OE-26-000525 | 7946 | 58 | 137 | HB-S05-05 | Harbor | 2026-02-21 | 18 | Animal | Lateral fuse | Forced | None
OE-26-000526 | 1600 | 8 | 200 | BY-S27-06 | Bayou | 2026-02-22 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-000527 | 640 | 5 | 128 | HB-S20-04 | Harbor | 2026-02-22 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000528 | 6165 | 137 | 45 | CR-S09-03 | Crossroads | 2026-02-22 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-26-000529 | 104 | 1 | 104 | CR-S04-01 | Crossroads | 2026-02-22 | 18 | Unknown | Transformer fuse | Forced | None
OE-26-000530 | 5859 | 31 | 189 | PR-S04-03 | Prairie | 2026-02-22 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-000531 | 113 | 1 | 113 | BY-S15-03 | Bayou | 2026-02-22 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000532 | 56430 | 285 | 198 | BY-S14-01 | Bayou | 2026-02-22 | 23 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000533 | 3591 | 9 | 399 | BY-S30-03 | Bayou | 2026-02-23 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000534 | 1364 | 11 | 124 | HB-S11-01 | Harbor | 2026-02-23 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-000535 | 5185 | 85 | 61 | CR-S15-01 | Crossroads | 2026-02-23 | 10 | Animal | Lateral fuse | Forced | None
OE-26-000536 | 1128 | 12 | 94 | CR-S08-05 | Crossroads | 2026-02-23 | 12 | Animal | Transformer fuse | Forced | None
OE-26-000537 | 8704 | 68 | 128 | CR-S28-03 | Crossroads | 2026-02-23 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000538 | 1320 | 10 | 132 | PR-S12-02 | Prairie | 2026-02-23 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-000539 | 1660 | 5 | 332 | PR-S01-01 | Prairie | 2026-02-23 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000540 | 69048 | 548 | 126 | CR-S30-05 | Crossroads | 2026-02-24 | 0 | Vegetation | Lateral fuse | Forced | None
OE-26-000541 | 510 | 2 | 255 | HB-S01-03 | Harbor | 2026-02-24 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-000542 | 1296 | 12 | 108 | BY-S09-02 | Bayou | 2026-02-24 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000543 | 2982 | 21 | 142 | BY-S24-02 | Bayou | 2026-02-24 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000544 | 17976 | 42 | 428 | BY-S07-03 | Bayou | 2026-02-24 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000545 | 9373 | 103 | 91 | BY-S13-01 | Bayou | 2026-02-24 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000546 | 49539 | 1011 | 49 | CR-S16-03 | Crossroads | 2026-02-24 | 22 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000547 | 1694 | 14 | 121 | CR-S30-06 | Crossroads | 2026-02-25 | 6 | Weather - wind | Transformer fuse | Forced | None
OE-26-000548 | 44100 | 900 | 49 | BY-S09-04 | Bayou | 2026-02-25 | 9 | Weather - wind | Feeder recloser | Forced | None
OE-26-000549 | 13685 | 85 | 161 | PR-S07-04 | Prairie | 2026-02-25 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000550 | 2346 | 69 | 34 | PR-S15-06 | Prairie | 2026-02-25 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000551 | 10045 | 41 | 245 | CR-S01-02 | Crossroads | 2026-02-25 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000552 | 2450 | 14 | 175 | PR-S01-02 | Prairie | 2026-02-25 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-000553 | 1179 | 9 | 131 | PR-S14-04 | Prairie | 2026-02-25 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-000554 | 146 | 2 | 73 | BY-S29-02 | Bayou | 2026-02-25 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000555 | 36652 | 374 | 98 | PR-S18-03 | Prairie | 2026-02-25 | 17 | Weather - wind | Feeder recloser | Forced | None
OE-26-000556 | 17724 | 84 | 211 | HB-S06-04 | Harbor | 2026-02-25 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000557 | 203830 | 1199 | 170 | PR-S07-02 | Prairie | 2026-02-26 | 5 | Equipment - overhead | Substation breaker | Outside cause | None
OE-26-000558 | 19908 | 158 | 126 | PR-S07-01 | Prairie | 2026-02-26 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000559 | 28125 | 125 | 225 | HB-S20-04 | Harbor | 2026-02-26 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000560 | 2316 | 12 | 193 | PR-S18-02 | Prairie | 2026-02-26 | 9 | Animal | Transformer fuse | Forced | None
OE-26-000561 | 2992 | 8 | 374 | PR-S08-01 | Prairie | 2026-02-26 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000562 | 1963 | 13 | 151 | BY-S28-01 | Bayou | 2026-02-26 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-000563 | 7320 | 61 | 120 | BY-S25-03 | Bayou | 2026-02-26 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-000564 | 48909 | 357 | 137 | BY-S03-02 | Bayou | 2026-02-26 | 16 | Vehicle or public | Lateral fuse | Forced | None
OE-26-000565 | 405 | 5 | 81 | BY-S07-06 | Bayou | 2026-02-26 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000566 | 7569 | 87 | 87 | BY-S30-01 | Bayou | 2026-02-26 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000567 | 4851 | 63 | 77 | PR-S15-06 | Prairie | 2026-02-26 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000568 | 2538 | 9 | 282 | BY-S17-01 | Bayou | 2026-02-26 | 18 | Unknown | Transformer fuse | Forced | None
OE-26-000569 | 23439 | 601 | 39 | CR-S29-02 | Crossroads | 2026-02-26 | 18 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000570 | 10620 | 118 | 90 | BY-S07-06 | Bayou | 2026-02-27 | 1 | Vegetation | Lateral fuse | Forced | None
OE-26-000571 | 808 | 8 | 101 | BY-S16-03 | Bayou | 2026-02-27 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-000572 | 14276 | 83 | 172 | BY-S26-01 | Bayou | 2026-02-27 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000573 | 1918 | 14 | 137 | CR-S03-01 | Crossroads | 2026-02-27 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000574 | 3000 | 24 | 125 | BY-S21-02 | Bayou | 2026-02-27 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000575 | 9936 | 92 | 108 | BY-S14-03 | Bayou | 2026-02-27 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000576 | 22950 | 150 | 153 | BY-S24-02 | Bayou | 2026-02-27 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000577 | 10890 | 99 | 110 | PR-S09-03 | Prairie | 2026-02-27 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-000578 | 938 | 7 | 134 | HB-S09-04 | Harbor | 2026-02-27 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000579 | 125888 | 1967 | 64 | PR-S17-01 | Prairie | 2026-02-27 | 13 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000580 | 5250 | 30 | 175 | BY-S01-01 | Bayou | 2026-02-27 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-000581 | 1440 | 15 | 96 | BY-S17-04 | Bayou | 2026-02-27 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-000582 | 207711 | 4239 | 49 | HB-S12-02 | Harbor | 2026-02-27 | 19 | Animal | Substation breaker | Forced | None
OE-26-000583 | 12958 | 38 | 341 | BY-S13-04 | Bayou | 2026-02-28 | 5 | Vegetation | Lateral fuse | Forced | None
OE-26-000584 | 1330 | 10 | 133 | HB-S04-01 | Harbor | 2026-02-28 | 7 | Animal | Transformer fuse | Forced | None
OE-26-000585 | 1001 | 11 | 91 | BY-S06-02 | Bayou | 2026-02-28 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000586 | 2052 | 12 | 171 | HB-S04-02 | Harbor | 2026-02-28 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000587 | 56814 | 557 | 102 | CR-S04-06 | Crossroads | 2026-02-28 | 15 | Vegetation | IGSD-isolated section | Forced | None
OE-26-000588 | 7957 | 109 | 73 | CR-S13-05 | Crossroads | 2026-02-28 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000589 | 1988 | 14 | 142 | CR-S05-03 | Crossroads | 2026-02-28 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000590 | 92323 | 763 | 121 | BY-S06-01 | Bayou | 2026-02-28 | 19 | Vegetation | Feeder recloser | Forced | None
OE-26-000591 | 4876 | 23 | 212 | BY-S14-01 | Bayou | 2026-03-01 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000592 | 78848 | 256 | 308 | BY-S21-05 | Bayou | 2026-03-01 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-000593 | 1944 | 8 | 243 | PR-S18-01 | Prairie | 2026-03-01 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000594 | 15200 | 304 | 50 | CR-S08-03 | Crossroads | 2026-03-01 | 11 | Weather - lightning | Feeder recloser | Forced | None
OE-26-000595 | 978 | 6 | 163 | BY-S19-01 | Bayou | 2026-03-01 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000596 | 1925 | 7 | 275 | BY-S21-02 | Bayou | 2026-03-01 | 15 | Animal | Transformer fuse | Forced | None
OE-26-000597 | 795 | 5 | 159 | PR-S06-02 | Prairie | 2026-03-01 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000598 | 4712 | 62 | 76 | CR-S25-06 | Crossroads | 2026-03-01 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000599 | 7668 | 71 | 108 | PR-S14-04 | Prairie | 2026-03-01 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-000600 | 2197 | 13 | 169 | BY-S24-03 | Bayou | 2026-03-02 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-000601 | 11920 | 80 | 149 | BY-S22-04 | Bayou | 2026-03-02 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000602 | 27664 | 364 | 76 | BY-S18-03 | Bayou | 2026-03-02 | 9 | Vegetation | Feeder recloser | Forced | None
OE-26-000603 | 1110 | 10 | 111 | CR-S06-02 | Crossroads | 2026-03-02 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000604 | 1332 | 12 | 111 | HB-S18-03 | Harbor | 2026-03-02 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000605 | 52768 | 776 | 68 | BY-S09-04 | Bayou | 2026-03-02 | 13 | Vegetation | Feeder recloser | Forced | None
OE-26-000606 | 81438 | 1662 | 49 | BY-S17-01 | Bayou | 2026-03-02 | 15 | Vehicle or public | Substation breaker | Forced | None
OE-26-000607 | 4462 | 46 | 97 | CR-S08-03 | Crossroads | 2026-03-02 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000608 | 1260 | 9 | 140 | BY-S09-03 | Bayou | 2026-03-03 | 1 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000609 | 3168 | 11 | 288 | CR-S15-01 | Crossroads | 2026-03-03 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-000610 | 3406 | 13 | 262 | PR-S06-01 | Prairie | 2026-03-03 | 6 | Animal | Transformer fuse | Forced | None
OE-26-000611 | 3666 | 13 | 282 | PR-S15-02 | Prairie | 2026-03-03 | 9 | Unknown | Transformer fuse | Forced | None
OE-26-000612 | 1320 | 11 | 120 | PR-S17-01 | Prairie | 2026-03-03 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000613 | 266 | 2 | 133 | PR-S18-05 | Prairie | 2026-03-03 | 15 | Animal | Transformer fuse | Forced | None
OE-26-000614 | 39015 | 459 | 85 | CR-S20-01 | Crossroads | 2026-03-03 | 16 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-000615 | 79249 | 817 | 97 | CR-S14-02 | Crossroads | 2026-03-03 | 19 | Vegetation | IGSD-isolated section | Forced | None
OE-26-000616 | 63724 | 358 | 178 | CR-S08-02 | Crossroads | 2026-03-03 | 20 | Animal | Lateral fuse | Forced | None
OE-26-000617 | 756 | 9 | 84 | HB-S05-06 | Harbor | 2026-03-03 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-000618 | 1356 | 6 | 226 | PR-S19-02 | Prairie | 2026-03-03 | 20 | Unknown | Transformer fuse | Forced | None
OE-26-000619 | 117702 | 503 | 234 | BY-S18-05 | Bayou | 2026-03-04 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-26-000620 | 178126 | 2873 | 62 | BY-S29-04 | Bayou | 2026-03-04 | 8 | Weather - wind | Substation breaker | Forced | None
OE-26-000621 | 348 | 3 | 116 | BY-S30-01 | Bayou | 2026-03-04 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-000622 | 76608 | 1197 | 64 | BY-S06-02 | Bayou | 2026-03-04 | 9 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000623 | 11655 | 111 | 105 | CR-S18-04 | Crossroads | 2026-03-04 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-000624 | 525 | 7 | 75 | HB-S19-04 | Harbor | 2026-03-04 | 9 | Unknown | Transformer fuse | Forced | None
OE-26-000625 | 15939 | 63 | 253 | CR-S18-03 | Crossroads | 2026-03-04 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000626 | 774 | 9 | 86 | PR-S11-03 | Prairie | 2026-03-04 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-000627 | 2925 | 45 | 65 | BY-S09-03 | Bayou | 2026-03-04 | 12 | Animal | Lateral fuse | Forced | None
OE-26-000628 | 16660 | 68 | 245 | PR-S08-02 | Prairie | 2026-03-04 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-000629 | 665 | 7 | 95 | PR-S16-04 | Prairie | 2026-03-04 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000630 | 2492 | 14 | 178 | BY-S04-02 | Bayou | 2026-03-04 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000631 | 428 | 4 | 107 | BY-S19-02 | Bayou | 2026-03-04 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-000632 | 113242 | 1381 | 82 | BY-S26-04 | Bayou | 2026-03-04 | 17 | Weather - wind | Substation breaker | Forced | None
OE-26-000633 | 420 | 3 | 140 | CR-S05-02 | Crossroads | 2026-03-05 | 0 | Unknown | Transformer fuse | Forced | None
OE-26-000634 | 290 | 2 | 145 | CR-S06-02 | Crossroads | 2026-03-05 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000635 | 1078 | 7 | 154 | PR-S13-06 | Prairie | 2026-03-05 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000636 | 3360 | 21 | 160 | PR-S02-02 | Prairie | 2026-03-05 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000637 | 1480 | 40 | 37 | CR-S09-04 | Crossroads | 2026-03-05 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000638 | 10660 | 82 | 130 | HB-S10-02 | Harbor | 2026-03-05 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000639 | 1484 | 14 | 106 | BY-S29-03 | Bayou | 2026-03-05 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000640 | 1810 | 10 | 181 | CR-S04-01 | Crossroads | 2026-03-06 | 3 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000641 | 95910 | 417 | 230 | BY-S01-01 | Bayou | 2026-03-06 | 6 | Vegetation | Lateral fuse | Forced | None
OE-26-000642 | 864 | 9 | 96 | PR-S03-01 | Prairie | 2026-03-06 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000643 | 61835 | 745 | 83 | CR-S16-05 | Crossroads | 2026-03-06 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000644 | 330 | 5 | 66 | HB-S08-01 | Harbor | 2026-03-06 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000645 | 1507 | 11 | 137 | CR-S07-02 | Crossroads | 2026-03-06 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000646 | 1150 | 5 | 230 | BY-S15-06 | Bayou | 2026-03-06 | 12 | Animal | Transformer fuse | Forced | None
OE-26-000647 | 67650 | 825 | 82 | PR-S08-02 | Prairie | 2026-03-06 | 12 | Unknown | Feeder recloser | Forced | None
OE-26-000648 | 618 | 6 | 103 | PR-S16-03 | Prairie | 2026-03-06 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000649 | 69138 | 501 | 138 | BY-S06-02 | Bayou | 2026-03-06 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000650 | 4248 | 12 | 354 | PR-S18-05 | Prairie | 2026-03-06 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000651 | 2254 | 14 | 161 | BY-S16-06 | Bayou | 2026-03-06 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-000652 | 145180 | 1037 | 140 | HB-S17-01 | Harbor | 2026-03-06 | 19 | Unknown | Feeder recloser | Forced | None
OE-26-000653 | 1653 | 29 | 57 | PR-S01-03 | Prairie | 2026-03-06 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-000654 | 1340 | 5 | 268 | PR-S17-01 | Prairie | 2026-03-06 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000655 | 13689 | 117 | 117 | BY-S08-02 | Bayou | 2026-03-06 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000656 | 98900 | 2300 | 43 | HB-S13-02 | Harbor | 2026-03-06 | 20 | Animal | Substation breaker | Forced | None
OE-26-000657 | 2464 | 32 | 77 | PR-S14-04 | Prairie | 2026-03-06 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000658 | 20868 | 111 | 188 | CR-S05-03 | Crossroads | 2026-03-07 | 1 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000659 | 8618 | 139 | 62 | CR-S25-03 | Crossroads | 2026-03-07 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-26-000660 | 440 | 2 | 220 | PR-S12-03 | Prairie | 2026-03-07 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000661 | 19893 | 349 | 57 | BY-S03-02 | Bayou | 2026-03-07 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-26-000662 | 872 | 4 | 218 | BY-S07-02 | Bayou | 2026-03-07 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000663 | 4674 | 57 | 82 | CR-S12-01 | Crossroads | 2026-03-07 | 10 | Unknown | Lateral fuse | Forced | None
OE-26-000664 | 13216 | 112 | 118 | PR-S07-01 | Prairie | 2026-03-07 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000665 | 19404 | 198 | 98 | PR-S03-04 | Prairie | 2026-03-07 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000666 | 438 | 6 | 73 | PR-S16-05 | Prairie | 2026-03-07 | 12 | Animal | Transformer fuse | Forced | None
OE-26-000667 | 39176 | 166 | 236 | BY-S12-02 | Bayou | 2026-03-07 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-000668 | 3431 | 47 | 73 | PR-S03-06 | Prairie | 2026-03-07 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-26-000669 | 11400 | 114 | 100 | BY-S29-01 | Bayou | 2026-03-08 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000670 | 143152 | 778 | 184 | CR-S05-01 | Crossroads | 2026-03-08 | 5 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000671 | 19320 | 120 | 161 | PR-S14-04 | Prairie | 2026-03-08 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-26-000672 | 846 | 6 | 141 | HB-S18-03 | Harbor | 2026-03-08 | 9 | Animal | Transformer fuse | Forced | None
OE-26-000673 | 10370 | 61 | 170 | PR-S19-02 | Prairie | 2026-03-08 | 9 | Animal | Lateral fuse | Forced | None
OE-26-000674 | 4256 | 32 | 133 | CR-S30-04 | Crossroads | 2026-03-08 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000675 | 4116 | 28 | 147 | BY-S29-02 | Bayou | 2026-03-08 | 11 | Unknown | Lateral fuse | Forced | None
OE-26-000676 | 12080 | 151 | 80 | CR-S28-02 | Crossroads | 2026-03-08 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000677 | 556 | 2 | 278 | BY-S01-01 | Bayou | 2026-03-08 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-000678 | 4000 | 25 | 160 | PR-S07-04 | Prairie | 2026-03-08 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000679 | 12827 | 127 | 101 | BY-S07-02 | Bayou | 2026-03-08 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-000680 | 105894 | 477 | 222 | BY-S27-01 | Bayou | 2026-03-08 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000681 | 2244 | 11 | 204 | PR-S09-04 | Prairie | 2026-03-08 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000682 | 1216 | 8 | 152 | BY-S17-02 | Bayou | 2026-03-08 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-000683 | 33488 | 161 | 208 | CR-S13-01 | Crossroads | 2026-03-08 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000684 | 1885 | 29 | 65 | BY-S06-03 | Bayou | 2026-03-09 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000685 | 4043 | 13 | 311 | PR-S03-04 | Prairie | 2026-03-09 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-000686 | 15678 | 78 | 201 | BY-S13-04 | Bayou | 2026-03-09 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000687 | 2736 | 18 | 152 | CR-S03-03 | Crossroads | 2026-03-09 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000688 | 186 | 1 | 186 | BY-S15-02 | Bayou | 2026-03-09 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-000689 | 11972 | 82 | 146 | HB-S03-03 | Harbor | 2026-03-09 | 15 | Animal | Lateral fuse | Forced | None
OE-26-000690 | 30012 | 122 | 246 | PR-S04-03 | Prairie | 2026-03-09 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-000691 | 243628 | 2156 | 113 | PR-S08-01 | Prairie | 2026-03-09 | 15 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000692 | 302 | 2 | 151 | BY-S07-03 | Bayou | 2026-03-09 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000693 | 25080 | 330 | 76 | PR-S03-05 | Prairie | 2026-03-10 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000694 | 895 | 5 | 179 | PR-S13-02 | Prairie | 2026-03-10 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-000695 | 3498 | 11 | 318 | BY-S12-01 | Bayou | 2026-03-10 | 10 | Animal | Transformer fuse | Forced | None
OE-26-000696 | 4030 | 26 | 155 | BY-S22-02 | Bayou | 2026-03-10 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000697 | 37673 | 373 | 101 | HB-S09-01 | Harbor | 2026-03-10 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000698 | 54740 | 644 | 85 | PR-S13-06 | Prairie | 2026-03-10 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000699 | 6510 | 35 | 186 | BY-S17-01 | Bayou | 2026-03-10 | 13 | Animal | Lateral fuse | Forced | None
OE-26-000700 | 4788 | 12 | 399 | PR-S19-02 | Prairie | 2026-03-10 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-26-000701 | 4004 | 22 | 182 | CR-S18-02 | Crossroads | 2026-03-10 | 14 | Animal | Lateral fuse | Forced | None
OE-26-000702 | 70 | 1 | 70 | HB-S05-01 | Harbor | 2026-03-10 | 14 | Animal | Transformer fuse | Forced | None
OE-26-000703 | 350 | 5 | 70 | HB-S10-03 | Harbor | 2026-03-10 | 14 | Animal | Transformer fuse | Forced | None
OE-26-000704 | 38024 | 392 | 97 | BY-S13-02 | Bayou | 2026-03-10 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000705 | 16731 | 99 | 169 | BY-S25-04 | Bayou | 2026-03-10 | 15 | Weather - wind | Lateral fuse | Forced | None
OE-26-000706 | 1368 | 9 | 152 | HB-S07-01 | Harbor | 2026-03-10 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-000707 | 13440 | 120 | 112 | HB-S08-02 | Harbor | 2026-03-10 | 17 | Animal | Lateral fuse | Forced | None
OE-26-000708 | 1992 | 8 | 249 | BY-S13-06 | Bayou | 2026-03-10 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-000709 | 5512 | 212 | 26 | PR-S16-03 | Prairie | 2026-03-11 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000710 | 6160 | 14 | 440 | BY-S09-04 | Bayou | 2026-03-11 | 4 | Vegetation | Transformer fuse | Forced | None
OE-26-000711 | 242 | 2 | 121 | PR-S01-03 | Prairie | 2026-03-11 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000712 | 32775 | 69 | 475 | PR-S11-02 | Prairie | 2026-03-11 | 7 | Vegetation | Lateral fuse | Forced | None
OE-26-000713 | 6804 | 84 | 81 | BY-S06-01 | Bayou | 2026-03-11 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000714 | 292 | 2 | 146 | CR-S24-03 | Crossroads | 2026-03-11 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-000715 | 20664 | 72 | 287 | CR-S26-04 | Crossroads | 2026-03-11 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000716 | 6930 | 55 | 126 | BY-S07-02 | Bayou | 2026-03-11 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000717 | 2679 | 19 | 141 | HB-S19-04 | Harbor | 2026-03-11 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000718 | 1722 | 6 | 287 | PR-S10-03 | Prairie | 2026-03-11 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-000719 | 12120 | 120 | 101 | PR-S08-02 | Prairie | 2026-03-11 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-000720 | 1971 | 9 | 219 | CR-S19-03 | Crossroads | 2026-03-11 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000721 | 21112 | 104 | 203 | BY-S24-02 | Bayou | 2026-03-11 | 23 | Weather - wind | Lateral fuse | Forced | None
OE-26-000722 | 2510 | 10 | 251 | PR-S01-06 | Prairie | 2026-03-12 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000723 | 2240 | 14 | 160 | BY-S04-01 | Bayou | 2026-03-12 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-000724 | 1968 | 12 | 164 | CR-S07-02 | Crossroads | 2026-03-12 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000725 | 5544 | 18 | 308 | CR-S08-06 | Crossroads | 2026-03-12 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000726 | 448 | 4 | 112 | HB-S06-01 | Harbor | 2026-03-12 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000727 | 3330 | 9 | 370 | HB-S06-01 | Harbor | 2026-03-12 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000728 | 2520 | 12 | 210 | PR-S18-04 | Prairie | 2026-03-12 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-000729 | 1968 | 8 | 246 | PR-S03-03 | Prairie | 2026-03-12 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-000730 | 77 | 1 | 77 | BY-S07-02 | Bayou | 2026-03-13 | 4 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000731 | 59110 | 514 | 115 | CR-S05-06 | Crossroads | 2026-03-13 | 4 | Vegetation | Feeder recloser | Forced | None
OE-26-000732 | 118110 | 635 | 186 | CR-S03-03 | Crossroads | 2026-03-13 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000733 | 1856 | 29 | 64 | CR-S22-01 | Crossroads | 2026-03-13 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000734 | 18054 | 1062 | 17 | CR-S04-04 | Crossroads | 2026-03-13 | 9 | Equipment - overhead | Substation breaker | Forced | None
OE-26-000735 | 1280 | 10 | 128 | CR-S17-01 | Crossroads | 2026-03-13 | 13 | Animal | Transformer fuse | Forced | None
OE-26-000736 | 12640 | 79 | 160 | HB-S17-02 | Harbor | 2026-03-13 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000737 | 6732 | 51 | 132 | BY-S22-04 | Bayou | 2026-03-13 | 15 | Unknown | Lateral fuse | Forced | None
OE-26-000738 | 11613 | 79 | 147 | CR-S08-06 | Crossroads | 2026-03-13 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-000739 | 3278 | 11 | 298 | CR-S19-03 | Crossroads | 2026-03-13 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000740 | 6916 | 76 | 91 | PR-S14-04 | Prairie | 2026-03-13 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000741 | 52520 | 520 | 101 | BY-S13-04 | Bayou | 2026-03-13 | 17 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000742 | 9790 | 89 | 110 | PR-S15-06 | Prairie | 2026-03-13 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-000743 | 176 | 2 | 88 | CR-S20-03 | Crossroads | 2026-03-13 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000744 | 1422 | 9 | 158 | CR-S13-01 | Crossroads | 2026-03-13 | 21 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000745 | 670 | 5 | 134 | BY-S10-05 | Bayou | 2026-03-14 | 7 | Animal | Transformer fuse | Forced | None
OE-26-000746 | 10580 | 115 | 92 | HB-S06-04 | Harbor | 2026-03-14 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-000747 | 1995 | 35 | 57 | CR-S14-02 | Crossroads | 2026-03-14 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000748 | 4278 | 69 | 62 | BY-S18-06 | Bayou | 2026-03-14 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-000749 | 2310 | 14 | 165 | CR-S02-03 | Crossroads | 2026-03-14 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000750 | 14381 | 197 | 73 | CR-S17-02 | Crossroads | 2026-03-14 | 12 | Unknown | Feeder recloser | Forced | None
OE-26-000751 | 138918 | 822 | 169 | BY-S20-02 | Bayou | 2026-03-14 | 13 | Animal | Feeder recloser | Forced | None
OE-26-000752 | 18688 | 146 | 128 | BY-S25-04 | Bayou | 2026-03-14 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-000753 | 52882 | 193 | 274 | BY-S04-02 | Bayou | 2026-03-14 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-000754 | 777 | 7 | 111 | BY-S25-05 | Bayou | 2026-03-14 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-000755 | 4888 | 52 | 94 | CR-S31-02 | Crossroads | 2026-03-14 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-000756 | 1422 | 6 | 237 | PR-S17-01 | Prairie | 2026-03-14 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000757 | 48018 | 906 | 53 | CR-S30-03 | Crossroads | 2026-03-14 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000758 | 666 | 6 | 111 | CR-S28-03 | Crossroads | 2026-03-14 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000759 | 384 | 6 | 64 | PR-S04-02 | Prairie | 2026-03-14 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000760 | 190 | 2 | 95 | BY-S29-05 | Bayou | 2026-03-15 | 5 | Animal | Transformer fuse | Forced | None
OE-26-000761 | 414 | 3 | 138 | HB-S12-02 | Harbor | 2026-03-15 | 6 | Weather - wind | Transformer fuse | Forced | None
OE-26-000762 | 676 | 13 | 52 | CR-S25-03 | Crossroads | 2026-03-15 | 9 | Animal | Transformer fuse | Forced | None
OE-26-000763 | 2214 | 18 | 123 | PR-S01-05 | Prairie | 2026-03-15 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-000764 | 10000 | 400 | 25 | CR-S29-03 | Crossroads | 2026-03-15 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000765 | 43566 | 411 | 106 | PR-S20-04 | Prairie | 2026-03-15 | 17 | Weather - wind | Substation breaker | Forced | None
OE-26-000766 | 178 | 2 | 89 | PR-S09-03 | Prairie | 2026-03-15 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000767 | 546 | 6 | 91 | HB-S14-04 | Harbor | 2026-03-15 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000768 | 3465 | 63 | 55 | PR-S07-01 | Prairie | 2026-03-15 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000769 | 1757 | 7 | 251 | BY-S18-05 | Bayou | 2026-03-15 | 22 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000770 | 2952 | 8 | 369 | PR-S18-05 | Prairie | 2026-03-16 | 1 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000771 | 3640 | 14 | 260 | PR-S07-02 | Prairie | 2026-03-16 | 6 | Animal | Transformer fuse | Forced | None
OE-26-000772 | 264 | 4 | 66 | HB-S09-02 | Harbor | 2026-03-16 | 9 | Animal | Transformer fuse | Forced | None
OE-26-000773 | 8614 | 73 | 118 | HB-S16-01 | Harbor | 2026-03-16 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000774 | 5664 | 48 | 118 | HB-S18-04 | Harbor | 2026-03-16 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000775 | 4141 | 101 | 41 | BY-S23-03 | Bayou | 2026-03-16 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-000776 | 1500 | 12 | 125 | BY-S08-03 | Bayou | 2026-03-16 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000777 | 228732 | 1167 | 196 | BY-S18-06 | Bayou | 2026-03-16 | 13 | Vegetation | Substation breaker | Forced | None
OE-26-000778 | 1152 | 6 | 192 | BY-S13-05 | Bayou | 2026-03-16 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-000779 | 228 | 2 | 114 | CR-S13-06 | Crossroads | 2026-03-16 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-000780 | 2025 | 25 | 81 | CR-S24-03 | Crossroads | 2026-03-16 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000781 | 1870 | 17 | 110 | BY-S12-03 | Bayou | 2026-03-16 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-000782 | 15147 | 153 | 99 | HB-S09-03 | Harbor | 2026-03-16 | 23 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000783 | 900 | 6 | 150 | CR-S07-03 | Crossroads | 2026-03-17 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000784 | 73983 | 813 | 91 | PR-S01-03 | Prairie | 2026-03-17 | 7 | Vegetation | Feeder recloser | Forced | None
OE-26-000785 | 2142 | 9 | 238 | PR-S10-01 | Prairie | 2026-03-17 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000786 | 26988 | 156 | 173 | CR-S07-05 | Crossroads | 2026-03-17 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000787 | 3699 | 27 | 137 | HB-S01-05 | Harbor | 2026-03-17 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000788 | 84016 | 1424 | 59 | PR-S04-01 | Prairie | 2026-03-17 | 11 | Weather - lightning | Substation breaker | Forced | None
OE-26-000789 | 3330 | 37 | 90 | PR-S18-05 | Prairie | 2026-03-17 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000790 | 784 | 7 | 112 | PR-S09-03 | Prairie | 2026-03-17 | 13 | Unknown | Transformer fuse | Forced | None
OE-26-000791 | 1995 | 35 | 57 | PR-S19-05 | Prairie | 2026-03-17 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000792 | 932 | 4 | 233 | PR-S16-03 | Prairie | 2026-03-17 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-26-000793 | 8176 | 14 | 584 | BY-S04-03 | Bayou | 2026-03-17 | 22 | Animal | Transformer fuse | Forced | None
OE-26-000794 | 202 | 2 | 101 | BY-S21-02 | Bayou | 2026-03-18 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-26-000795 | 40050 | 450 | 89 | HB-S20-02 | Harbor | 2026-03-18 | 0 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-000796 | 12575 | 503 | 25 | CR-S05-04 | Crossroads | 2026-03-18 | 7 | Animal | Feeder recloser | Forced | None
OE-26-000797 | 264 | 3 | 88 | CR-S21-01 | Crossroads | 2026-03-18 | 10 | Animal | Transformer fuse | Forced | None
OE-26-000798 | 6885 | 45 | 153 | BY-S03-01 | Bayou | 2026-03-18 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000799 | 780 | 10 | 78 | BY-S13-03 | Bayou | 2026-03-18 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-000800 | 11250 | 75 | 150 | BY-S23-04 | Bayou | 2026-03-18 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000801 | 11122 | 67 | 166 | CR-S10-03 | Crossroads | 2026-03-18 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000802 | 2409 | 33 | 73 | CR-S01-01 | Crossroads | 2026-03-18 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000803 | 5915 | 65 | 91 | PR-S05-01 | Prairie | 2026-03-18 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000804 | 1434 | 6 | 239 | CR-S26-01 | Crossroads | 2026-03-18 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-000805 | 160 | 1 | 160 | PR-S07-01 | Prairie | 2026-03-18 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-000806 | 1045 | 11 | 95 | BY-S27-03 | Bayou | 2026-03-18 | 19 | Weather - wind | Transformer fuse | Forced | None
OE-26-000807 | 2320 | 10 | 232 | HB-S05-01 | Harbor | 2026-03-18 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-000808 | 2976 | 12 | 248 | PR-S03-03 | Prairie | 2026-03-19 | 0 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000809 | 2088 | 12 | 174 | BY-S26-01 | Bayou | 2026-03-19 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000810 | 1930 | 10 | 193 | BY-S18-06 | Bayou | 2026-03-19 | 17 | Animal | Transformer fuse | Forced | None
OE-26-000811 | 1002 | 6 | 167 | HB-S07-01 | Harbor | 2026-03-19 | 19 | Weather - wind | Transformer fuse | Forced | None
OE-26-000812 | 1554 | 14 | 111 | BY-S04-03 | Bayou | 2026-03-20 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000813 | 14718 | 66 | 223 | PR-S15-02 | Prairie | 2026-03-20 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000814 | 9090 | 45 | 202 | BY-S11-01 | Bayou | 2026-03-20 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-000815 | 1630 | 10 | 163 | BY-S12-04 | Bayou | 2026-03-20 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000816 | 2460 | 30 | 82 | PR-S15-06 | Prairie | 2026-03-20 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-000817 | 3878 | 7 | 554 | PR-S19-04 | Prairie | 2026-03-20 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000818 | 896 | 14 | 64 | BY-S17-02 | Bayou | 2026-03-20 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000819 | 44667 | 709 | 63 | CR-S08-06 | Crossroads | 2026-03-20 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000820 | 1638 | 9 | 182 | BY-S18-04 | Bayou | 2026-03-20 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000821 | 2096 | 8 | 262 | PR-S04-03 | Prairie | 2026-03-20 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000822 | 37368 | 2076 | 18 | BY-S07-02 | Bayou | 2026-03-21 | 2 | Unknown | Substation breaker | Outside cause | None
OE-26-000823 | 232 | 1 | 232 | BY-S26-02 | Bayou | 2026-03-21 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000824 | 4680 | 36 | 130 | HB-S05-03 | Harbor | 2026-03-21 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-000825 | 61422 | 706 | 87 | BY-S07-06 | Bayou | 2026-03-21 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000826 | 20097 | 77 | 261 | BY-S30-01 | Bayou | 2026-03-21 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-26-000827 | 10058 | 107 | 94 | CR-S10-01 | Crossroads | 2026-03-21 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000828 | 1368 | 12 | 114 | HB-S14-04 | Harbor | 2026-03-21 | 15 | Animal | Transformer fuse | Forced | None
OE-26-000829 | 5704 | 23 | 248 | PR-S17-02 | Prairie | 2026-03-21 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000830 | 21525 | 105 | 205 | CR-S18-03 | Crossroads | 2026-03-21 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-26-000831 | 1272 | 8 | 159 | CR-S07-02 | Crossroads | 2026-03-21 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000832 | 2442 | 11 | 222 | PR-S03-03 | Prairie | 2026-03-21 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-000833 | 114872 | 692 | 166 | BY-S23-04 | Bayou | 2026-03-21 | 19 | Vegetation | IGSD-isolated section | Forced | None
OE-26-000834 | 79104 | 824 | 96 | CR-S23-04 | Crossroads | 2026-03-21 | 19 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000835 | 960 | 20 | 48 | HB-S07-05 | Harbor | 2026-03-21 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-000836 | 3066 | 14 | 219 | PR-S19-04 | Prairie | 2026-03-21 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-000837 | 74816 | 1169 | 64 | CR-S23-03 | Crossroads | 2026-03-22 | 10 | Equipment - underground | Substation breaker | Forced | None
OE-26-000838 | 3024 | 84 | 36 | CR-S08-04 | Crossroads | 2026-03-22 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-000839 | 9660 | 46 | 210 | HB-S02-02 | Harbor | 2026-03-22 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-000840 | 8512 | 76 | 112 | CR-S27-02 | Crossroads | 2026-03-22 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000841 | 2668 | 23 | 116 | PR-S06-01 | Prairie | 2026-03-22 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000842 | 200 | 2 | 100 | BY-S16-01 | Bayou | 2026-03-22 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000843 | 16128 | 192 | 84 | PR-S18-01 | Prairie | 2026-03-22 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000844 | 1716 | 11 | 156 | HB-S07-05 | Harbor | 2026-03-23 | 5 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000845 | 1113 | 7 | 159 | HB-S15-03 | Harbor | 2026-03-23 | 5 | Weather - wind | Transformer fuse | Forced | None
OE-26-000846 | 3122 | 14 | 223 | BY-S12-01 | Bayou | 2026-03-23 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-000847 | 71706 | 629 | 114 | BY-S27-03 | Bayou | 2026-03-23 | 7 | Vehicle or public | Feeder recloser | Forced | None
OE-26-000848 | 600 | 12 | 50 | CR-S19-03 | Crossroads | 2026-03-23 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-26-000849 | 1582 | 7 | 226 | HB-S07-02 | Harbor | 2026-03-23 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000850 | 966 | 7 | 138 | BY-S07-03 | Bayou | 2026-03-23 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-000851 | 3800 | 50 | 76 | BY-S16-01 | Bayou | 2026-03-23 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000852 | 700 | 14 | 50 | HB-S05-06 | Harbor | 2026-03-23 | 11 | Animal | Transformer fuse | Forced | None
OE-26-000853 | 498 | 6 | 83 | PR-S06-01 | Prairie | 2026-03-23 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-000854 | 101871 | 1029 | 99 | BY-S18-05 | Bayou | 2026-03-23 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000855 | 1824 | 12 | 152 | HB-S13-02 | Harbor | 2026-03-23 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000856 | 636 | 4 | 159 | PR-S01-03 | Prairie | 2026-03-23 | 14 | Unknown | Transformer fuse | Forced | None
OE-26-000857 | 248 | 2 | 124 | CR-S24-04 | Crossroads | 2026-03-23 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000858 | 10615 | 55 | 193 | PR-S09-03 | Prairie | 2026-03-23 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000859 | 313 | 1 | 313 | HB-S10-02 | Harbor | 2026-03-23 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-000860 | 69 | 1 | 69 | CR-S05-01 | Crossroads | 2026-03-23 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000861 | 10621 | 43 | 247 | BY-S20-01 | Bayou | 2026-03-23 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000862 | 24786 | 486 | 51 | BY-S25-04 | Bayou | 2026-03-23 | 22 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000863 | 9999 | 101 | 99 | CR-S07-05 | Crossroads | 2026-03-23 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000864 | 1855 | 7 | 265 | BY-S03-02 | Bayou | 2026-03-23 | 23 | Vehicle or public | Lateral fuse | Forced | None
OE-26-000865 | 5452 | 47 | 116 | CR-S14-02 | Crossroads | 2026-03-24 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000866 | 21924 | 108 | 203 | PR-S05-03 | Prairie | 2026-03-24 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000867 | 8410 | 29 | 290 | CR-S32-03 | Crossroads | 2026-03-24 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000868 | 42800 | 428 | 100 | CR-S09-02 | Crossroads | 2026-03-24 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-000869 | 980 | 7 | 140 | HB-S20-03 | Harbor | 2026-03-24 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-000870 | 16800 | 105 | 160 | CR-S01-01 | Crossroads | 2026-03-25 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000871 | 3190 | 11 | 290 | PR-S04-02 | Prairie | 2026-03-25 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000872 | 7930 | 26 | 305 | BY-S29-03 | Bayou | 2026-03-25 | 9 | Unknown | Lateral fuse | Forced | None
OE-26-000873 | 8174 | 67 | 122 | BY-S20-02 | Bayou | 2026-03-25 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000874 | 816 | 8 | 102 | BY-S29-02 | Bayou | 2026-03-25 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000875 | 2100 | 12 | 175 | CR-S14-01 | Crossroads | 2026-03-25 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000876 | 784 | 8 | 98 | CR-S32-01 | Crossroads | 2026-03-25 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000877 | 3648 | 57 | 64 | PR-S07-03 | Prairie | 2026-03-25 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000878 | 13482 | 63 | 214 | BY-S15-05 | Bayou | 2026-03-25 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000879 | 268 | 2 | 134 | HB-S05-04 | Harbor | 2026-03-25 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000880 | 99 | 1 | 99 | HB-S20-05 | Harbor | 2026-03-25 | 20 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000881 | 1344 | 7 | 192 | BY-S02-02 | Bayou | 2026-03-25 | 22 | Animal | Transformer fuse | Forced | None
OE-26-000882 | 1830 | 30 | 61 | CR-S18-04 | Crossroads | 2026-03-25 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000883 | 15190 | 217 | 70 | BY-S16-01 | Bayou | 2026-03-26 | 3 | Animal | Lateral fuse | Forced | None
OE-26-000884 | 872 | 8 | 109 | BY-S23-01 | Bayou | 2026-03-26 | 3 | Vegetation | Transformer fuse | Forced | None
OE-26-000885 | 53724 | 363 | 148 | HB-S09-03 | Harbor | 2026-03-26 | 8 | Vegetation | IGSD-isolated section | Forced | None
OE-26-000886 | 1652 | 14 | 118 | HB-S15-03 | Harbor | 2026-03-26 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000887 | 1998 | 9 | 222 | HB-S18-04 | Harbor | 2026-03-26 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000888 | 43769 | 173 | 253 | PR-S07-06 | Prairie | 2026-03-26 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-000889 | 154 | 2 | 77 | BY-S29-03 | Bayou | 2026-03-26 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000890 | 8646 | 66 | 131 | BY-S24-03 | Bayou | 2026-03-26 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000891 | 23364 | 99 | 236 | CR-S30-02 | Crossroads | 2026-03-26 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000892 | 2044 | 14 | 146 | BY-S08-01 | Bayou | 2026-03-26 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000893 | 10800 | 80 | 135 | CR-S31-01 | Crossroads | 2026-03-26 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000894 | 2187 | 9 | 243 | CR-S13-06 | Crossroads | 2026-03-26 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-000895 | 536 | 8 | 67 | HB-S04-01 | Harbor | 2026-03-26 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-000896 | 131452 | 557 | 236 | PR-S19-01 | Prairie | 2026-03-26 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000897 | 1980 | 10 | 198 | BY-S13-04 | Bayou | 2026-03-26 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-000898 | 980 | 10 | 98 | BY-S21-03 | Bayou | 2026-03-26 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000899 | 2208 | 12 | 184 | CR-S18-04 | Crossroads | 2026-03-26 | 15 | Unknown | Transformer fuse | Forced | None
OE-26-000900 | 1090 | 5 | 218 | CR-S18-05 | Crossroads | 2026-03-26 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000901 | 140 | 2 | 70 | PR-S18-04 | Prairie | 2026-03-26 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000902 | 2847 | 13 | 219 | BY-S23-01 | Bayou | 2026-03-26 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-000903 | 864 | 6 | 144 | HB-S17-02 | Harbor | 2026-03-26 | 20 | Animal | Transformer fuse | Forced | None
OE-26-000904 | 702 | 6 | 117 | HB-S19-02 | Harbor | 2026-03-27 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000905 | 39456 | 144 | 274 | BY-S10-03 | Bayou | 2026-03-27 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000906 | 3048 | 12 | 254 | BY-S03-02 | Bayou | 2026-03-27 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-000907 | 23660 | 140 | 169 | CR-S04-03 | Crossroads | 2026-03-27 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000908 | 3503 | 31 | 113 | CR-S30-07 | Crossroads | 2026-03-27 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000909 | 1157 | 13 | 89 | PR-S03-03 | Prairie | 2026-03-27 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000910 | 3379 | 31 | 109 | PR-S10-03 | Prairie | 2026-03-27 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000911 | 333 | 3 | 111 | BY-S09-02 | Bayou | 2026-03-27 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-000912 | 267 | 1 | 267 | HB-S01-01 | Harbor | 2026-03-27 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-000913 | 1554 | 7 | 222 | HB-S19-03 | Harbor | 2026-03-27 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000914 | 2910 | 10 | 291 | BY-S29-04 | Bayou | 2026-03-27 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-000915 | 28080 | 144 | 195 | CR-S19-04 | Crossroads | 2026-03-28 | 1 | Vegetation | Lateral fuse | Forced | None
OE-26-000916 | 708 | 3 | 236 | CR-S12-01 | Crossroads | 2026-03-28 | 2 | Vegetation | Transformer fuse | Forced | None
OE-26-000917 | 675 | 3 | 225 | BY-S03-03 | Bayou | 2026-03-28 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-26-000918 | 1608 | 12 | 134 | HB-S01-01 | Harbor | 2026-03-28 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000919 | 3458 | 14 | 247 | PR-S17-01 | Prairie | 2026-03-28 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-000920 | 816 | 12 | 68 | BY-S26-01 | Bayou | 2026-03-28 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-000921 | 100620 | 1548 | 65 | BY-S23-03 | Bayou | 2026-03-28 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000922 | 624 | 13 | 48 | CR-S30-07 | Crossroads | 2026-03-28 | 17 | Animal | Transformer fuse | Forced | None
OE-26-000923 | 5031 | 43 | 117 | PR-S01-04 | Prairie | 2026-03-28 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-000924 | 2444 | 13 | 188 | CR-S21-02 | Crossroads | 2026-03-28 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000925 | 3530 | 10 | 353 | BY-S12-04 | Bayou | 2026-03-28 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000926 | 2444 | 13 | 188 | PR-S16-04 | Prairie | 2026-03-28 | 22 | Vehicle or public | Transformer fuse | Forced | None
OE-26-000927 | 18426 | 83 | 222 | PR-S07-05 | Prairie | 2026-03-29 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000928 | 9039 | 69 | 131 | BY-S20-01 | Bayou | 2026-03-29 | 12 | Animal | Lateral fuse | Forced | None
OE-26-000929 | 1992 | 24 | 83 | PR-S06-01 | Prairie | 2026-03-29 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000930 | 4636 | 76 | 61 | PR-S02-03 | Prairie | 2026-03-29 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-000931 | 2190 | 10 | 219 | PR-S14-01 | Prairie | 2026-03-29 | 13 | Unknown | Transformer fuse | Forced | None
OE-26-000932 | 44550 | 495 | 90 | PR-S15-05 | Prairie | 2026-03-29 | 16 | Vehicle or public | Substation breaker | Forced | None
OE-26-000933 | 3360 | 14 | 240 | PR-S14-01 | Prairie | 2026-03-29 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-000934 | 1397 | 11 | 127 | HB-S20-04 | Harbor | 2026-03-29 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000935 | 832 | 13 | 64 | CR-S02-03 | Crossroads | 2026-03-29 | 20 | Animal | Transformer fuse | Forced | None
OE-26-000936 | 7881 | 37 | 213 | CR-S31-02 | Crossroads | 2026-03-30 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000937 | 11700 | 65 | 180 | BY-S18-05 | Bayou | 2026-03-30 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-000938 | 1480 | 10 | 148 | BY-S07-02 | Bayou | 2026-03-30 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-000939 | 1160 | 5 | 232 | BY-S16-04 | Bayou | 2026-03-30 | 13 | Animal | Transformer fuse | Forced | None
OE-26-000940 | 4736 | 37 | 128 | CR-S18-01 | Crossroads | 2026-03-30 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000941 | 288 | 2 | 144 | CR-S20-03 | Crossroads | 2026-03-30 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000942 | 2366 | 13 | 182 | BY-S02-01 | Bayou | 2026-03-30 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-000943 | 10780 | 110 | 98 | CR-S20-04 | Crossroads | 2026-03-30 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000944 | 35784 | 126 | 284 | BY-S17-02 | Bayou | 2026-03-30 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000945 | 302895 | 1143 | 265 | HB-S02-03 | Harbor | 2026-03-30 | 17 | Vegetation | Feeder recloser | Forced | None
OE-26-000946 | 9541 | 329 | 29 | CR-S01-01 | Crossroads | 2026-03-30 | 18 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000947 | 2808 | 12 | 234 | PR-S19-05 | Prairie | 2026-03-30 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-000948 | 35090 | 605 | 58 | CR-S20-05 | Crossroads | 2026-03-30 | 23 | Weather - lightning | IGSD-isolated section | Forced | None
OE-26-000949 | 26754 | 686 | 39 | CR-S10-03 | Crossroads | 2026-03-31 | 3 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000950 | 3002 | 38 | 79 | HB-S18-01 | Harbor | 2026-03-31 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000951 | 7119 | 63 | 113 | CR-S32-01 | Crossroads | 2026-03-31 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-000952 | 1355 | 5 | 271 | PR-S13-05 | Prairie | 2026-03-31 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000953 | 2134 | 11 | 194 | HB-S18-01 | Harbor | 2026-03-31 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-000954 | 23042 | 82 | 281 | PR-S13-03 | Prairie | 2026-03-31 | 12 | Vegetation | IGSD-isolated section | Forced | None
OE-26-000955 | 25330 | 149 | 170 | PR-S17-02 | Prairie | 2026-03-31 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000956 | 7314 | 69 | 106 | CR-S13-03 | Crossroads | 2026-03-31 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000957 | 9360 | 130 | 72 | PR-S01-06 | Prairie | 2026-03-31 | 15 | Animal | Lateral fuse | Forced | None
OE-26-000958 | 688 | 8 | 86 | BY-S10-02 | Bayou | 2026-03-31 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-26-000959 | 13407 | 109 | 123 | BY-S13-02 | Bayou | 2026-03-31 | 16 | Unknown | Lateral fuse | Forced | None
OE-26-000960 | 6084 | 156 | 39 | CR-S20-02 | Crossroads | 2026-03-31 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000961 | 24500 | 125 | 196 | CR-S12-03 | Crossroads | 2026-03-31 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000962 | 6840 | 72 | 95 | CR-S25-01 | Crossroads | 2026-03-31 | 23 | Vegetation | Lateral fuse | Forced | None
OE-26-000963 | 4662 | 37 | 126 | HB-S05-04 | Harbor | 2026-04-01 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000964 | 14544 | 202 | 72 | BY-S21-05 | Bayou | 2026-04-01 | 6 | Animal | IGSD-isolated section | Forced | None
OE-26-000965 | 2288 | 26 | 88 | CR-S31-01 | Crossroads | 2026-04-01 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000966 | 1464 | 12 | 122 | CR-S05-03 | Crossroads | 2026-04-01 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000967 | 7665 | 35 | 219 | CR-S05-06 | Crossroads | 2026-04-01 | 11 | Animal | Lateral fuse | Forced | None
OE-26-000968 | 52960 | 662 | 80 | PR-S18-02 | Prairie | 2026-04-01 | 12 | Vehicle or public | Feeder recloser | Forced | None
OE-26-000969 | 57050 | 2282 | 25 | BY-S18-04 | Bayou | 2026-04-01 | 13 | Vegetation | Substation breaker | Forced | None
OE-26-000970 | 744 | 8 | 93 | HB-S07-04 | Harbor | 2026-04-01 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000971 | 345 | 5 | 69 | CR-S26-05 | Crossroads | 2026-04-01 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000972 | 606 | 6 | 101 | CR-S28-02 | Crossroads | 2026-04-01 | 17 | Unknown | Transformer fuse | Forced | None
OE-26-000973 | 2535 | 13 | 195 | HB-S14-04 | Harbor | 2026-04-01 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000974 | 15264 | 159 | 96 | CR-S12-01 | Crossroads | 2026-04-01 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000975 | 5773 | 23 | 251 | PR-S02-01 | Prairie | 2026-04-02 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000976 | 600 | 3 | 200 | BY-S30-01 | Bayou | 2026-04-02 | 8 | Animal | Transformer fuse | Forced | None
OE-26-000977 | 2574 | 11 | 234 | CR-S21-03 | Crossroads | 2026-04-02 | 11 | Animal | Transformer fuse | Forced | None
OE-26-000978 | 26520 | 136 | 195 | CR-S28-03 | Crossroads | 2026-04-02 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000979 | 2058 | 14 | 147 | PR-S01-03 | Prairie | 2026-04-02 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000980 | 180 | 3 | 60 | HB-S09-02 | Harbor | 2026-04-02 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000981 | 3510 | 9 | 390 | HB-S20-04 | Harbor | 2026-04-02 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-000982 | 3339 | 53 | 63 | BY-S03-02 | Bayou | 2026-04-02 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000983 | 51912 | 309 | 168 | CR-S08-01 | Crossroads | 2026-04-02 | 23 | Equipment - underground | Feeder recloser | Forced | None
OE-26-000984 | 3248 | 29 | 112 | CR-S21-03 | Crossroads | 2026-04-03 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-000985 | 41038 | 578 | 71 | BY-S23-04 | Bayou | 2026-04-03 | 9 | Weather - wind | IGSD-isolated section | Forced | None
OE-26-000986 | 1665 | 9 | 185 | CR-S14-02 | Crossroads | 2026-04-03 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000987 | 9408 | 96 | 98 | PR-S02-02 | Prairie | 2026-04-03 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-000988 | 1656 | 9 | 184 | BY-S16-01 | Bayou | 2026-04-03 | 11 | Animal | Transformer fuse | Forced | None
OE-26-000989 | 520 | 5 | 104 | CR-S29-02 | Crossroads | 2026-04-03 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-000990 | 15604 | 47 | 332 | BY-S12-01 | Bayou | 2026-04-03 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-000991 | 2800 | 35 | 80 | PR-S19-03 | Prairie | 2026-04-03 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-000992 | 69007 | 457 | 151 | PR-S08-03 | Prairie | 2026-04-04 | 8 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-000993 | 4896 | 96 | 51 | BY-S29-02 | Bayou | 2026-04-04 | 9 | Animal | Lateral fuse | Forced | None
OE-26-000994 | 4218 | 37 | 114 | BY-S27-02 | Bayou | 2026-04-04 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-26-000995 | 1485 | 5 | 297 | PR-S03-04 | Prairie | 2026-04-04 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000996 | 5940 | 66 | 90 | BY-S27-03 | Bayou | 2026-04-04 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-000997 | 247520 | 1190 | 208 | HB-S02-02 | Harbor | 2026-04-04 | 12 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-000998 | 6706 | 14 | 479 | PR-S19-04 | Prairie | 2026-04-04 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-000999 | 388 | 2 | 194 | CR-S13-06 | Crossroads | 2026-04-04 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001000 | 8008 | 88 | 91 | CR-S31-01 | Crossroads | 2026-04-04 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001001 | 1606 | 11 | 146 | BY-S22-03 | Bayou | 2026-04-04 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001002 | 2470 | 13 | 190 | BY-S29-05 | Bayou | 2026-04-04 | 15 | Unknown | Transformer fuse | Forced | None
OE-26-001003 | 11356 | 167 | 68 | CR-S23-03 | Crossroads | 2026-04-04 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001004 | 1043 | 7 | 149 | HB-S07-05 | Harbor | 2026-04-04 | 17 | Animal | Transformer fuse | Forced | None
OE-26-001005 | 4347 | 63 | 69 | CR-S06-01 | Crossroads | 2026-04-04 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001006 | 1170 | 6 | 195 | HB-S02-01 | Harbor | 2026-04-04 | 19 | Animal | Transformer fuse | Forced | None
OE-26-001007 | 177 | 1 | 177 | PR-S02-01 | Prairie | 2026-04-04 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001008 | 2079 | 11 | 189 | PR-S06-01 | Prairie | 2026-04-05 | 2 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001009 | 350 | 2 | 175 | BY-S06-03 | Bayou | 2026-04-05 | 9 | Animal | Transformer fuse | Forced | None
OE-26-001010 | 16544 | 94 | 176 | BY-S16-05 | Bayou | 2026-04-05 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-001011 | 5310 | 45 | 118 | BY-S17-03 | Bayou | 2026-04-05 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001012 | 18144 | 72 | 252 | CR-S12-03 | Crossroads | 2026-04-05 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001013 | 14496 | 453 | 32 | PR-S13-05 | Prairie | 2026-04-05 | 9 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001014 | 1568 | 32 | 49 | CR-S13-05 | Crossroads | 2026-04-05 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-001015 | 24418 | 421 | 58 | PR-S02-03 | Prairie | 2026-04-05 | 11 | Weather - lightning | Feeder recloser | Forced | None
OE-26-001016 | 19080 | 530 | 36 | CR-S26-05 | Crossroads | 2026-04-05 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-001017 | 2338 | 14 | 167 | PR-S07-04 | Prairie | 2026-04-05 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-001018 | 1940 | 10 | 194 | PR-S18-05 | Prairie | 2026-04-05 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-001019 | 1360 | 10 | 136 | HB-S10-02 | Harbor | 2026-04-05 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001020 | 146328 | 728 | 201 | PR-S11-03 | Prairie | 2026-04-05 | 17 | Vegetation | Feeder recloser | Forced | None
OE-26-001021 | 312 | 1 | 312 | BY-S14-01 | Bayou | 2026-04-05 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001022 | 77308 | 251 | 308 | BY-S23-02 | Bayou | 2026-04-05 | 22 | Animal | Lateral fuse | Forced | None
OE-26-001023 | 756 | 7 | 108 | HB-S03-01 | Harbor | 2026-04-06 | 0 | Animal | Transformer fuse | Forced | None
OE-26-001024 | 48360 | 620 | 78 | HB-S09-01 | Harbor | 2026-04-06 | 4 | Weather - wind | Feeder recloser | Forced | None
OE-26-001025 | 2023 | 17 | 119 | BY-S08-03 | Bayou | 2026-04-06 | 10 | Animal | Lateral fuse | Forced | None
OE-26-001026 | 136305 | 1165 | 117 | BY-S10-05 | Bayou | 2026-04-06 | 12 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-001027 | 9741 | 51 | 191 | CR-S16-01 | Crossroads | 2026-04-06 | 16 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001028 | 1908 | 12 | 159 | BY-S26-02 | Bayou | 2026-04-06 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001029 | 2356 | 19 | 124 | HB-S19-03 | Harbor | 2026-04-06 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001030 | 1112 | 8 | 139 | PR-S09-02 | Prairie | 2026-04-06 | 17 | Animal | Transformer fuse | Forced | None
OE-26-001031 | 6608 | 118 | 56 | CR-S26-04 | Crossroads | 2026-04-06 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001032 | 438 | 3 | 146 | BY-S14-03 | Bayou | 2026-04-07 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-001033 | 2080 | 10 | 208 | CR-S07-06 | Crossroads | 2026-04-07 | 7 | Animal | Transformer fuse | Forced | None
OE-26-001034 | 9039 | 131 | 69 | CR-S30-07 | Crossroads | 2026-04-07 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001035 | 4992 | 78 | 64 | CR-S28-01 | Crossroads | 2026-04-07 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001036 | 138573 | 519 | 267 | PR-S13-04 | Prairie | 2026-04-07 | 12 | Weather - lightning | Feeder recloser | Forced | None
OE-26-001037 | 69600 | 400 | 174 | HB-S20-03 | Harbor | 2026-04-07 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001038 | 6314 | 154 | 41 | BY-S12-01 | Bayou | 2026-04-07 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-001039 | 120274 | 1694 | 71 | CR-S09-01 | Crossroads | 2026-04-07 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001040 | 144002 | 809 | 178 | PR-S01-03 | Prairie | 2026-04-07 | 14 | Weather - wind | Feeder recloser | Forced | None
OE-26-001041 | 924 | 14 | 66 | CR-S23-05 | Crossroads | 2026-04-07 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001042 | 158424 | 1288 | 123 | BY-S16-02 | Bayou | 2026-04-07 | 16 | Weather - lightning | Feeder recloser | Forced | None
OE-26-001043 | 6897 | 57 | 121 | CR-S14-03 | Crossroads | 2026-04-07 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001044 | 1098 | 9 | 122 | PR-S04-02 | Prairie | 2026-04-07 | 18 | Animal | Transformer fuse | Forced | None
OE-26-001045 | 161 | 1 | 161 | PR-S18-04 | Prairie | 2026-04-07 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001046 | 888 | 3 | 296 | PR-S19-03 | Prairie | 2026-04-07 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001047 | 3657 | 159 | 23 | CR-S18-01 | Crossroads | 2026-04-08 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001048 | 940 | 10 | 94 | BY-S14-02 | Bayou | 2026-04-08 | 8 | Animal | Transformer fuse | Forced | None
OE-26-001049 | 834 | 3 | 278 | CR-S05-05 | Crossroads | 2026-04-08 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001050 | 11050 | 85 | 130 | CR-S07-04 | Crossroads | 2026-04-08 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001051 | 9891 | 157 | 63 | CR-S05-04 | Crossroads | 2026-04-08 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001052 | 2814 | 21 | 134 | CR-S14-05 | Crossroads | 2026-04-08 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001053 | 29250 | 1125 | 26 | CR-S02-05 | Crossroads | 2026-04-08 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001054 | 1755 | 27 | 65 | CR-S16-01 | Crossroads | 2026-04-08 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001055 | 52000 | 650 | 80 | BY-S12-04 | Bayou | 2026-04-08 | 13 | Vegetation | Feeder recloser | Forced | None
OE-26-001056 | 1904 | 14 | 136 | CR-S24-03 | Crossroads | 2026-04-08 | 17 | Animal | Transformer fuse | Forced | None
OE-26-001057 | 69 | 1 | 69 | CR-S07-02 | Crossroads | 2026-04-08 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001058 | 931 | 7 | 133 | PR-S02-02 | Prairie | 2026-04-08 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001059 | 2627 | 37 | 71 | BY-S17-02 | Bayou | 2026-04-08 | 23 | Animal | Lateral fuse | Forced | None
OE-26-001060 | 6890 | 65 | 106 | BY-S19-04 | Bayou | 2026-04-09 | 0 | Vegetation | Lateral fuse | Forced | None
OE-26-001061 | 1210 | 10 | 121 | BY-S16-01 | Bayou | 2026-04-09 | 5 | Animal | Transformer fuse | Forced | None
OE-26-001062 | 177 | 1 | 177 | PR-S14-02 | Prairie | 2026-04-09 | 7 | Animal | Transformer fuse | Forced | None
OE-26-001063 | 459 | 3 | 153 | CR-S29-02 | Crossroads | 2026-04-09 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001064 | 1032 | 12 | 86 | CR-S16-06 | Crossroads | 2026-04-09 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001065 | 2262 | 13 | 174 | HB-S05-03 | Harbor | 2026-04-09 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001066 | 1917 | 9 | 213 | BY-S29-04 | Bayou | 2026-04-09 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001067 | 4077 | 9 | 453 | BY-S13-05 | Bayou | 2026-04-09 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-001068 | 150 | 3 | 50 | BY-S18-04 | Bayou | 2026-04-10 | 1 | Vegetation | Transformer fuse | Forced | None
OE-26-001069 | 270 | 2 | 135 | HB-S07-02 | Harbor | 2026-04-10 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001070 | 1386 | 11 | 126 | BY-S12-02 | Bayou | 2026-04-10 | 11 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001071 | 2718 | 9 | 302 | CR-S25-06 | Crossroads | 2026-04-10 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001072 | 1710 | 10 | 171 | PR-S03-06 | Prairie | 2026-04-10 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001073 | 830 | 5 | 166 | CR-S21-02 | Crossroads | 2026-04-10 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-001074 | 264 | 3 | 88 | HB-S11-03 | Harbor | 2026-04-10 | 13 | Animal | Transformer fuse | Forced | None
OE-26-001075 | 2604 | 21 | 124 | PR-S03-06 | Prairie | 2026-04-10 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001076 | 356 | 4 | 89 | HB-S20-01 | Harbor | 2026-04-10 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001077 | 615 | 3 | 205 | BY-S02-01 | Bayou | 2026-04-10 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001078 | 5642 | 182 | 31 | CR-S28-03 | Crossroads | 2026-04-10 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001079 | 4200 | 40 | 105 | CR-S24-04 | Crossroads | 2026-04-10 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-001080 | 5928 | 38 | 156 | CR-S07-03 | Crossroads | 2026-04-10 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001081 | 12376 | 104 | 119 | BY-S16-01 | Bayou | 2026-04-10 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-001082 | 630 | 7 | 90 | CR-S25-05 | Crossroads | 2026-04-10 | 19 | Animal | Transformer fuse | Forced | None
OE-26-001083 | 715 | 5 | 143 | BY-S16-01 | Bayou | 2026-04-10 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001084 | 9540 | 90 | 106 | CR-S21-01 | Crossroads | 2026-04-11 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001085 | 42500 | 850 | 50 | CR-S05-02 | Crossroads | 2026-04-11 | 10 | Weather - lightning | Feeder recloser | Forced | None
OE-26-001086 | 18680 | 467 | 40 | CR-S13-06 | Crossroads | 2026-04-11 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001087 | 104 | 1 | 104 | HB-S14-01 | Harbor | 2026-04-11 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001088 | 1440 | 12 | 120 | PR-S13-02 | Prairie | 2026-04-11 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001089 | 140372 | 1847 | 76 | CR-S14-05 | Crossroads | 2026-04-11 | 14 | Equipment - underground | Substation breaker | Forced | None
OE-26-001090 | 5148 | 33 | 156 | PR-S03-05 | Prairie | 2026-04-11 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-001091 | 13795 | 155 | 89 | HB-S20-01 | Harbor | 2026-04-11 | 15 | Animal | Lateral fuse | Forced | None
OE-26-001092 | 1400 | 8 | 175 | PR-S09-03 | Prairie | 2026-04-11 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001093 | 435 | 5 | 87 | BY-S24-05 | Bayou | 2026-04-11 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001094 | 12958 | 38 | 341 | PR-S05-03 | Prairie | 2026-04-11 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001095 | 522 | 6 | 87 | PR-S18-06 | Prairie | 2026-04-11 | 19 | Animal | Transformer fuse | Forced | None
OE-26-001096 | 654 | 3 | 218 | PR-S18-03 | Prairie | 2026-04-11 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-001097 | 6408 | 36 | 178 | PR-S16-05 | Prairie | 2026-04-11 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001098 | 6930 | 70 | 99 | PR-S17-01 | Prairie | 2026-04-12 | 0 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001099 | 2541 | 11 | 231 | BY-S25-02 | Bayou | 2026-04-12 | 6 | Animal | Transformer fuse | Forced | None
OE-26-001100 | 792 | 11 | 72 | CR-S21-03 | Crossroads | 2026-04-12 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001101 | 106262 | 871 | 122 | CR-S10-03 | Crossroads | 2026-04-12 | 9 | Weather - lightning | Feeder recloser | Forced | None
OE-26-001102 | 5730 | 30 | 191 | BY-S28-03 | Bayou | 2026-04-12 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-26-001103 | 1152 | 8 | 144 | CR-S32-05 | Crossroads | 2026-04-12 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001104 | 33280 | 208 | 160 | BY-S07-05 | Bayou | 2026-04-12 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-001105 | 37455 | 227 | 165 | BY-S26-04 | Bayou | 2026-04-12 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-001106 | 1067 | 11 | 97 | CR-S26-02 | Crossroads | 2026-04-12 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001107 | 8652 | 84 | 103 | BY-S25-01 | Bayou | 2026-04-12 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-001108 | 14224 | 56 | 254 | CR-S31-01 | Crossroads | 2026-04-12 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001109 | 382416 | 4112 | 93 | CR-S20-02 | Crossroads | 2026-04-12 | 19 | Equipment - overhead | Substation breaker | Forced | None
OE-26-001110 | 484 | 4 | 121 | BY-S09-04 | Bayou | 2026-04-12 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-001111 | 11853 | 439 | 27 | HB-S07-05 | Harbor | 2026-04-12 | 22 | Vegetation | Feeder recloser | Forced | None
OE-26-001112 | 1420 | 5 | 284 | BY-S09-01 | Bayou | 2026-04-13 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001113 | 417 | 3 | 139 | CR-S05-04 | Crossroads | 2026-04-13 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001114 | 1800 | 12 | 150 | BY-S22-04 | Bayou | 2026-04-13 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001115 | 486 | 3 | 162 | PR-S18-06 | Prairie | 2026-04-13 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-26-001116 | 1089 | 9 | 121 | CR-S23-04 | Crossroads | 2026-04-13 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001117 | 620 | 2 | 310 | BY-S09-04 | Bayou | 2026-04-13 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001118 | 1692 | 12 | 141 | BY-S10-04 | Bayou | 2026-04-13 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-001119 | 18120 | 302 | 60 | PR-S15-02 | Prairie | 2026-04-13 | 16 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-001120 | 3114 | 9 | 346 | BY-S13-04 | Bayou | 2026-04-13 | 17 | Unknown | Transformer fuse | Forced | None
OE-26-001121 | 2694 | 6 | 449 | BY-S27-02 | Bayou | 2026-04-13 | 17 | Animal | Transformer fuse | Forced | None
OE-26-001122 | 3948 | 12 | 329 | BY-S29-04 | Bayou | 2026-04-13 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-001123 | 4080 | 40 | 102 | HB-S17-02 | Harbor | 2026-04-13 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001124 | 1780 | 5 | 356 | CR-S14-02 | Crossroads | 2026-04-13 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-001125 | 30699 | 1137 | 27 | CR-S07-03 | Crossroads | 2026-04-13 | 21 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001126 | 1302 | 7 | 186 | HB-S10-03 | Harbor | 2026-04-13 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001127 | 1991 | 11 | 181 | PR-S20-02 | Prairie | 2026-04-14 | 2 | Weather - wind | Transformer fuse | Forced | None
OE-26-001128 | 1224 | 9 | 136 | BY-S15-02 | Bayou | 2026-04-14 | 7 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001129 | 27234 | 153 | 178 | HB-S14-01 | Harbor | 2026-04-14 | 8 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001130 | 28054 | 83 | 338 | PR-S02-02 | Prairie | 2026-04-14 | 8 | Animal | Lateral fuse | Forced | None
OE-26-001131 | 4240 | 53 | 80 | BY-S16-05 | Bayou | 2026-04-14 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001132 | 6720 | 21 | 320 | CR-S07-07 | Crossroads | 2026-04-14 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001133 | 18009 | 261 | 69 | BY-S27-06 | Bayou | 2026-04-14 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001134 | 3604 | 34 | 106 | CR-S16-03 | Crossroads | 2026-04-14 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001135 | 93 | 1 | 93 | CR-S26-04 | Crossroads | 2026-04-14 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001136 | 1561 | 7 | 223 | BY-S05-02 | Bayou | 2026-04-14 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001137 | 280 | 1 | 280 | BY-S08-01 | Bayou | 2026-04-14 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001138 | 10540 | 68 | 155 | CR-S12-03 | Crossroads | 2026-04-14 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001139 | 2516 | 37 | 68 | BY-S15-04 | Bayou | 2026-04-14 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001140 | 777 | 7 | 111 | HB-S12-02 | Harbor | 2026-04-14 | 18 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001141 | 18042 | 93 | 194 | BY-S27-04 | Bayou | 2026-04-14 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001142 | 7744 | 44 | 176 | CR-S26-03 | Crossroads | 2026-04-14 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001143 | 1791 | 9 | 199 | BY-S01-02 | Bayou | 2026-04-15 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001144 | 775 | 5 | 155 | BY-S06-03 | Bayou | 2026-04-15 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-001145 | 15594 | 46 | 339 | CR-S18-02 | Crossroads | 2026-04-15 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001146 | 4532 | 44 | 103 | CR-S29-02 | Crossroads | 2026-04-15 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-26-001147 | 25286 | 269 | 94 | BY-S27-02 | Bayou | 2026-04-15 | 10 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001148 | 164 | 1 | 164 | BY-S16-03 | Bayou | 2026-04-15 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001149 | 3328 | 13 | 256 | PR-S07-04 | Prairie | 2026-04-15 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001150 | 280 | 2 | 140 | BY-S01-01 | Bayou | 2026-04-15 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001151 | 660 | 11 | 60 | BY-S08-03 | Bayou | 2026-04-15 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001152 | 621 | 9 | 69 | BY-S26-04 | Bayou | 2026-04-15 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-001153 | 837 | 9 | 93 | CR-S05-02 | Crossroads | 2026-04-15 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001154 | 58 | 1 | 58 | PR-S01-06 | Prairie | 2026-04-15 | 18 | Unknown | Transformer fuse | Forced | None
OE-26-001155 | 1356 | 12 | 113 | BY-S21-02 | Bayou | 2026-04-15 | 19 | Weather - wind | Transformer fuse | Forced | None
OE-26-001156 | 2350 | 25 | 94 | BY-S14-01 | Bayou | 2026-04-15 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-001157 | 112428 | 3123 | 36 | BY-S19-02 | Bayou | 2026-04-15 | 20 | Unknown | Substation breaker | Outside cause | None
OE-26-001158 | 2380 | 28 | 85 | CR-S04-02 | Crossroads | 2026-04-15 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001159 | 1016 | 8 | 127 | PR-S03-01 | Prairie | 2026-04-16 | 4 | Animal | Transformer fuse | Forced | None
OE-26-001160 | 8120 | 29 | 280 | PR-S03-03 | Prairie | 2026-04-16 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001161 | 30173 | 211 | 143 | PR-S05-01 | Prairie | 2026-04-16 | 9 | Weather - lightning | Feeder recloser | Forced | None
OE-26-001162 | 1552 | 8 | 194 | BY-S02-02 | Bayou | 2026-04-16 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001163 | 8520 | 71 | 120 | BY-S23-02 | Bayou | 2026-04-16 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001164 | 24167 | 169 | 143 | BY-S23-04 | Bayou | 2026-04-16 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001165 | 1377 | 9 | 153 | PR-S01-05 | Prairie | 2026-04-16 | 12 | Animal | Transformer fuse | Forced | None
OE-26-001166 | 3773 | 49 | 77 | BY-S08-02 | Bayou | 2026-04-16 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001167 | 1326 | 13 | 102 | PR-S16-05 | Prairie | 2026-04-16 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-001168 | 8505 | 63 | 135 | BY-S29-03 | Bayou | 2026-04-16 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-001169 | 4284 | 51 | 84 | BY-S10-05 | Bayou | 2026-04-17 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001170 | 16950 | 50 | 339 | CR-S28-04 | Crossroads | 2026-04-17 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001171 | 12150 | 45 | 270 | CR-S32-05 | Crossroads | 2026-04-17 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001172 | 1410 | 10 | 141 | CR-S05-01 | Crossroads | 2026-04-17 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001173 | 2198 | 14 | 157 | BY-S16-05 | Bayou | 2026-04-17 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001174 | 10920 | 42 | 260 | BY-S22-01 | Bayou | 2026-04-17 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-001175 | 5290 | 46 | 115 | BY-S21-03 | Bayou | 2026-04-17 | 16 | Animal | Lateral fuse | Forced | None
OE-26-001176 | 410 | 5 | 82 | BY-S25-01 | Bayou | 2026-04-17 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-001177 | 492 | 6 | 82 | CR-S08-04 | Crossroads | 2026-04-17 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001178 | 60 | 1 | 60 | BY-S12-02 | Bayou | 2026-04-17 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-001179 | 5605 | 59 | 95 | CR-S19-04 | Crossroads | 2026-04-17 | 23 | Animal | Lateral fuse | Forced | None
OE-26-001180 | 18414 | 93 | 198 | CR-S30-01 | Crossroads | 2026-04-18 | 1 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001181 | 84940 | 620 | 137 | PR-S08-02 | Prairie | 2026-04-18 | 1 | Animal | Lateral fuse | Forced | None
OE-26-001182 | 13420 | 61 | 220 | BY-S29-04 | Bayou | 2026-04-18 | 5 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001183 | 4732 | 52 | 91 | BY-S20-02 | Bayou | 2026-04-18 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-26-001184 | 8239 | 77 | 107 | PR-S03-03 | Prairie | 2026-04-18 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001185 | 1456 | 7 | 208 | CR-S26-01 | Crossroads | 2026-04-18 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001186 | 89 | 1 | 89 | CR-S16-02 | Crossroads | 2026-04-18 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001187 | 37647 | 267 | 141 | BY-S22-04 | Bayou | 2026-04-18 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001188 | 2009 | 49 | 41 | HB-S20-04 | Harbor | 2026-04-18 | 23 | Weather - wind | Lateral fuse | Forced | None
OE-26-001189 | 3178 | 7 | 454 | PR-S15-05 | Prairie | 2026-04-19 | 0 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001190 | 5940 | 60 | 99 | BY-S02-02 | Bayou | 2026-04-19 | 1 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001191 | 4988 | 58 | 86 | CR-S17-02 | Crossroads | 2026-04-19 | 3 | Animal | Lateral fuse | Forced | None
OE-26-001192 | 2241 | 9 | 249 | BY-S16-02 | Bayou | 2026-04-19 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001193 | 1648 | 8 | 206 | PR-S18-06 | Prairie | 2026-04-19 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001194 | 50264 | 824 | 61 | PR-S15-03 | Prairie | 2026-04-19 | 10 | Vehicle or public | Feeder recloser | Forced | None
OE-26-001195 | 2200 | 11 | 200 | BY-S15-03 | Bayou | 2026-04-19 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001196 | 37236 | 174 | 214 | CR-S04-01 | Crossroads | 2026-04-19 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001197 | 216 | 2 | 108 | BY-S18-04 | Bayou | 2026-04-19 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001198 | 1510 | 5 | 302 | PR-S20-03 | Prairie | 2026-04-19 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001199 | 25098 | 178 | 141 | CR-S28-02 | Crossroads | 2026-04-19 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001200 | 8550 | 95 | 90 | BY-S28-01 | Bayou | 2026-04-20 | 7 | Unknown | Lateral fuse | Forced | None
OE-26-001201 | 35900 | 50 | 718 | PR-S07-05 | Prairie | 2026-04-20 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-26-001202 | 7395 | 51 | 145 | PR-S12-02 | Prairie | 2026-04-20 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001203 | 67782 | 2054 | 33 | BY-S07-02 | Bayou | 2026-04-20 | 12 | Vegetation | Substation breaker | Forced | None
OE-26-001204 | 3538 | 29 | 122 | PR-S12-02 | Prairie | 2026-04-20 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001205 | 87040 | 680 | 128 | PR-S17-01 | Prairie | 2026-04-20 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001206 | 9476 | 103 | 92 | BY-S10-01 | Bayou | 2026-04-20 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001207 | 8184 | 66 | 124 | PR-S14-02 | Prairie | 2026-04-20 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001208 | 76472 | 632 | 121 | CR-S07-03 | Crossroads | 2026-04-20 | 16 | Unknown | IGSD-isolated section | Forced | None
OE-26-001209 | 2345 | 7 | 335 | HB-S20-03 | Harbor | 2026-04-20 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001210 | 7450 | 10 | 745 | PR-S18-05 | Prairie | 2026-04-20 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001211 | 10287 | 81 | 127 | BY-S16-02 | Bayou | 2026-04-20 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-001212 | 102950 | 1450 | 71 | CR-S23-01 | Crossroads | 2026-04-20 | 23 | Equipment - underground | Substation breaker | Forced | None
OE-26-001213 | 87808 | 1372 | 64 | BY-S07-01 | Bayou | 2026-04-21 | 5 | Animal | Substation breaker | Forced | None
OE-26-001214 | 1650 | 22 | 75 | BY-S19-01 | Bayou | 2026-04-21 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001215 | 43008 | 168 | 256 | PR-S07-06 | Prairie | 2026-04-21 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001216 | 2292 | 12 | 191 | BY-S03-02 | Bayou | 2026-04-21 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001217 | 5054 | 38 | 133 | HB-S12-02 | Harbor | 2026-04-21 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001218 | 7670 | 13 | 590 | PR-S05-01 | Prairie | 2026-04-21 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001219 | 10640 | 133 | 80 | CR-S32-02 | Crossroads | 2026-04-21 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001220 | 18285 | 159 | 115 | BY-S27-05 | Bayou | 2026-04-21 | 19 | Weather - wind | Lateral fuse | Forced | None
OE-26-001221 | 495 | 3 | 165 | CR-S23-05 | Crossroads | 2026-04-22 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001222 | 3792 | 48 | 79 | CR-S18-06 | Crossroads | 2026-04-22 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001223 | 41480 | 305 | 136 | BY-S03-02 | Bayou | 2026-04-22 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001224 | 9856 | 64 | 154 | PR-S15-02 | Prairie | 2026-04-22 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001225 | 21584 | 142 | 152 | BY-S26-04 | Bayou | 2026-04-22 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001226 | 1476 | 12 | 123 | CR-S23-02 | Crossroads | 2026-04-22 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001227 | 204 | 2 | 102 | BY-S12-03 | Bayou | 2026-04-22 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001228 | 648 | 6 | 108 | CR-S20-02 | Crossroads | 2026-04-22 | 17 | Unknown | Transformer fuse | Forced | None
OE-26-001229 | 1230 | 6 | 205 | HB-S16-02 | Harbor | 2026-04-22 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001230 | 246 | 1 | 246 | HB-S05-05 | Harbor | 2026-04-22 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-001231 | 3114 | 9 | 346 | CR-S14-02 | Crossroads | 2026-04-23 | 1 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001232 | 2232 | 12 | 186 | CR-S07-03 | Crossroads | 2026-04-23 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001233 | 229460 | 770 | 298 | PR-S13-02 | Prairie | 2026-04-23 | 5 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001234 | 2676 | 12 | 223 | HB-S19-03 | Harbor | 2026-04-23 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001235 | 11781 | 51 | 231 | PR-S07-03 | Prairie | 2026-04-23 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001236 | 43344 | 172 | 252 | PR-S18-06 | Prairie | 2026-04-23 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-001237 | 5782 | 59 | 98 | PR-S15-04 | Prairie | 2026-04-23 | 21 | Weather - wind | Lateral fuse | Forced | None
OE-26-001238 | 18018 | 231 | 78 | HB-S20-01 | Harbor | 2026-04-23 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001239 | 7897 | 53 | 149 | PR-S18-01 | Prairie | 2026-04-24 | 5 | Animal | Lateral fuse | Forced | None
OE-26-001240 | 68 | 1 | 68 | BY-S25-05 | Bayou | 2026-04-24 | 9 | Animal | Transformer fuse | Forced | None
OE-26-001241 | 9928 | 73 | 136 | HB-S07-02 | Harbor | 2026-04-24 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001242 | 1240 | 10 | 124 | CR-S23-05 | Crossroads | 2026-04-24 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001243 | 46063 | 631 | 73 | CR-S23-05 | Crossroads | 2026-04-24 | 10 | Weather - lightning | Feeder recloser | Forced | None
OE-26-001244 | 10879 | 43 | 253 | CR-S28-01 | Crossroads | 2026-04-24 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001245 | 2223 | 13 | 171 | HB-S18-02 | Harbor | 2026-04-24 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001246 | 5616 | 8 | 702 | PR-S18-04 | Prairie | 2026-04-24 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-001247 | 1251 | 9 | 139 | HB-S02-03 | Harbor | 2026-04-24 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001248 | 2030 | 10 | 203 | PR-S20-01 | Prairie | 2026-04-24 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-001249 | 2592 | 12 | 216 | BY-S27-03 | Bayou | 2026-04-24 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001250 | 8976 | 34 | 264 | CR-S11-02 | Crossroads | 2026-04-24 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001251 | 492 | 3 | 164 | HB-S03-02 | Harbor | 2026-04-24 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001252 | 5934 | 86 | 69 | HB-S13-02 | Harbor | 2026-04-24 | 16 | Unknown | Lateral fuse | Forced | None
OE-26-001253 | 15520 | 388 | 40 | PR-S18-06 | Prairie | 2026-04-24 | 20 | Vegetation | Feeder recloser | Forced | None
OE-26-001254 | 8484 | 101 | 84 | HB-S12-01 | Harbor | 2026-04-24 | 22 | Animal | Lateral fuse | Forced | None
OE-26-001255 | 9548 | 44 | 217 | PR-S03-02 | Prairie | 2026-04-24 | 23 | Weather - wind | Lateral fuse | Forced | None
OE-26-001256 | 3321 | 27 | 123 | PR-S01-01 | Prairie | 2026-04-25 | 0 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001257 | 2070 | 6 | 345 | CR-S27-04 | Crossroads | 2026-04-25 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001258 | 2993 | 41 | 73 | BY-S07-02 | Bayou | 2026-04-25 | 7 | Vegetation | Lateral fuse | Forced | None
OE-26-001259 | 380 | 4 | 95 | BY-S14-01 | Bayou | 2026-04-25 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001260 | 26892 | 166 | 162 | CR-S04-01 | Crossroads | 2026-04-25 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001261 | 20367 | 93 | 219 | PR-S03-04 | Prairie | 2026-04-25 | 10 | Unknown | Lateral fuse | Forced | None
OE-26-001262 | 40565 | 665 | 61 | CR-S10-01 | Crossroads | 2026-04-25 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001263 | 16520 | 590 | 28 | BY-S21-01 | Bayou | 2026-04-25 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001264 | 2737 | 7 | 391 | CR-S29-03 | Crossroads | 2026-04-25 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001265 | 1212 | 4 | 303 | BY-S03-01 | Bayou | 2026-04-25 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-001266 | 3306 | 19 | 174 | CR-S29-03 | Crossroads | 2026-04-25 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-001267 | 1085 | 7 | 155 | BY-S25-02 | Bayou | 2026-04-25 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-001268 | 888 | 6 | 148 | CR-S09-03 | Crossroads | 2026-04-25 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001269 | 468 | 6 | 78 | HB-S02-01 | Harbor | 2026-04-25 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001270 | 32752 | 92 | 356 | PR-S03-02 | Prairie | 2026-04-25 | 23 | Animal | Lateral fuse | Forced | None
OE-26-001271 | 3996 | 12 | 333 | PR-S05-01 | Prairie | 2026-04-25 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-001272 | 632 | 8 | 79 | CR-S29-01 | Crossroads | 2026-04-26 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001273 | 935 | 11 | 85 | CR-S20-05 | Crossroads | 2026-04-26 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001274 | 9686 | 58 | 167 | PR-S03-02 | Prairie | 2026-04-26 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-26-001275 | 1176 | 6 | 196 | BY-S30-01 | Bayou | 2026-04-26 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001276 | 1736 | 8 | 217 | PR-S01-05 | Prairie | 2026-04-26 | 10 | Animal | Transformer fuse | Forced | None
OE-26-001277 | 2769 | 39 | 71 | BY-S29-01 | Bayou | 2026-04-26 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-001278 | 1788 | 12 | 149 | CR-S16-05 | Crossroads | 2026-04-26 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001279 | 45948 | 547 | 84 | BY-S12-01 | Bayou | 2026-04-26 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001280 | 4242 | 14 | 303 | BY-S26-01 | Bayou | 2026-04-26 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001281 | 1320 | 12 | 110 | HB-S14-01 | Harbor | 2026-04-26 | 15 | Animal | Transformer fuse | Forced | None
OE-26-001282 | 7644 | 84 | 91 | CR-S04-06 | Crossroads | 2026-04-26 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-001283 | 864 | 9 | 96 | CR-S09-03 | Crossroads | 2026-04-26 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-001284 | 380 | 2 | 190 | CR-S16-05 | Crossroads | 2026-04-26 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001285 | 4200 | 40 | 105 | HB-S07-03 | Harbor | 2026-04-26 | 22 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001286 | 17490 | 165 | 106 | PR-S14-04 | Prairie | 2026-04-27 | 0 | Weather - wind | Lateral fuse | Forced | None
OE-26-001287 | 1799 | 7 | 257 | BY-S13-06 | Bayou | 2026-04-27 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001288 | 35526 | 191 | 186 | CR-S25-06 | Crossroads | 2026-04-27 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001289 | 341 | 11 | 31 | CR-S07-01 | Crossroads | 2026-04-27 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001290 | 2925 | 25 | 117 | BY-S06-01 | Bayou | 2026-04-27 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001291 | 2590 | 74 | 35 | PR-S09-02 | Prairie | 2026-04-27 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-26-001292 | 4998 | 102 | 49 | CR-S15-01 | Crossroads | 2026-04-27 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-001293 | 390 | 3 | 130 | PR-S02-02 | Prairie | 2026-04-27 | 17 | Animal | Transformer fuse | Forced | None
OE-26-001294 | 3458 | 14 | 247 | BY-S27-04 | Bayou | 2026-04-27 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001295 | 12307 | 31 | 397 | CR-S22-04 | Crossroads | 2026-04-27 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-001296 | 2244 | 34 | 66 | HB-S10-02 | Harbor | 2026-04-27 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-001297 | 909 | 9 | 101 | BY-S07-02 | Bayou | 2026-04-27 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-001298 | 6270 | 22 | 285 | BY-S09-04 | Bayou | 2026-04-27 | 23 | Animal | Lateral fuse | Forced | None
OE-26-001299 | 27648 | 96 | 288 | CR-S08-02 | Crossroads | 2026-04-27 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001300 | 1884 | 12 | 157 | CR-S22-01 | Crossroads | 2026-04-28 | 3 | Unknown | Transformer fuse | Forced | None
OE-26-001301 | 5040 | 63 | 80 | PR-S07-06 | Prairie | 2026-04-28 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001302 | 94620 | 1140 | 83 | BY-S17-01 | Bayou | 2026-04-28 | 4 | Animal | Feeder recloser | Forced | None
OE-26-001303 | 10502 | 89 | 118 | CR-S07-07 | Crossroads | 2026-04-28 | 7 | Vegetation | Lateral fuse | Forced | None
OE-26-001304 | 6336 | 64 | 99 | PR-S13-06 | Prairie | 2026-04-28 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001305 | 60 | 1 | 60 | CR-S30-01 | Crossroads | 2026-04-28 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-001306 | 124928 | 1024 | 122 | PR-S04-02 | Prairie | 2026-04-28 | 12 | Equipment - overhead | Substation breaker | Forced | None
OE-26-001307 | 468 | 6 | 78 | CR-S06-02 | Crossroads | 2026-04-28 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001308 | 8195 | 55 | 149 | HB-S05-02 | Harbor | 2026-04-28 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001309 | 1240 | 8 | 155 | HB-S02-01 | Harbor | 2026-04-28 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001310 | 10640 | 95 | 112 | BY-S07-02 | Bayou | 2026-04-28 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001311 | 55 | 1 | 55 | CR-S02-02 | Crossroads | 2026-04-28 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001312 | 18960 | 1264 | 15 | HB-S02-01 | Harbor | 2026-04-29 | 6 | Unknown | Feeder recloser | Forced | None
OE-26-001313 | 15123 | 213 | 71 | CR-S01-03 | Crossroads | 2026-04-29 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001314 | 616 | 7 | 88 | CR-S27-02 | Crossroads | 2026-04-29 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001315 | 24960 | 192 | 130 | BY-S15-06 | Bayou | 2026-04-29 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001316 | 2070 | 15 | 138 | BY-S07-02 | Bayou | 2026-04-29 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-26-001317 | 798 | 14 | 57 | CR-S20-01 | Crossroads | 2026-04-29 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001318 | 193 | 1 | 193 | BY-S19-04 | Bayou | 2026-04-29 | 14 | Animal | Transformer fuse | Forced | None
OE-26-001319 | 1032 | 12 | 86 | CR-S17-01 | Crossroads | 2026-04-29 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001320 | 2430 | 54 | 45 | BY-S17-01 | Bayou | 2026-04-29 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-001321 | 1176 | 4 | 294 | CR-S25-03 | Crossroads | 2026-04-29 | 15 | Animal | Transformer fuse | Forced | None
OE-26-001322 | 7874 | 62 | 127 | BY-S25-01 | Bayou | 2026-04-29 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001323 | 1472 | 8 | 184 | PR-S03-01 | Prairie | 2026-04-29 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001324 | 4972 | 44 | 113 | BY-S29-05 | Bayou | 2026-04-29 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001325 | 373 | 1 | 373 | PR-S18-01 | Prairie | 2026-04-29 | 22 | Animal | Transformer fuse | Forced | None
OE-26-001326 | 1680 | 5 | 336 | BY-S29-01 | Bayou | 2026-04-30 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001327 | 600 | 10 | 60 | CR-S13-05 | Crossroads | 2026-04-30 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-26-001328 | 1482 | 13 | 114 | BY-S15-06 | Bayou | 2026-04-30 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001329 | 3551 | 67 | 53 | BY-S15-02 | Bayou | 2026-04-30 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-001330 | 1111 | 11 | 101 | PR-S04-03 | Prairie | 2026-04-30 | 10 | Animal | Transformer fuse | Forced | None
OE-26-001331 | 2200 | 10 | 220 | PR-S13-02 | Prairie | 2026-04-30 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-001332 | 1070 | 10 | 107 | HB-S16-03 | Harbor | 2026-04-30 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001333 | 1980 | 9 | 220 | CR-S22-04 | Crossroads | 2026-04-30 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001334 | 760 | 4 | 190 | PR-S05-02 | Prairie | 2026-04-30 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001335 | 6392 | 94 | 68 | CR-S13-03 | Crossroads | 2026-04-30 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001336 | 476 | 4 | 119 | BY-S03-02 | Bayou | 2026-04-30 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001337 | 10224 | 72 | 142 | BY-S10-03 | Bayou | 2026-04-30 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-001338 | 36288 | 216 | 168 | CR-S30-04 | Crossroads | 2026-04-30 | 17 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-001339 | 942 | 6 | 157 | BY-S22-03 | Bayou | 2026-04-30 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001340 | 331 | 1 | 331 | BY-S24-02 | Bayou | 2026-04-30 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-001341 | 14630 | 55 | 266 | PR-S15-06 | Prairie | 2026-05-01 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001342 | 4950 | 110 | 45 | BY-S13-01 | Bayou | 2026-05-01 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001343 | 339 | 3 | 113 | BY-S20-01 | Bayou | 2026-05-01 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001344 | 11050 | 130 | 85 | BY-S29-05 | Bayou | 2026-05-01 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001345 | 605 | 5 | 121 | CR-S32-03 | Crossroads | 2026-05-01 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001346 | 13694 | 167 | 82 | HB-S18-02 | Harbor | 2026-05-01 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001347 | 1728 | 9 | 192 | PR-S01-03 | Prairie | 2026-05-01 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-001348 | 3240 | 24 | 135 | HB-S06-04 | Harbor | 2026-05-01 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001349 | 2676 | 6 | 446 | PR-S19-05 | Prairie | 2026-05-01 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-001350 | 1791 | 9 | 199 | CR-S29-01 | Crossroads | 2026-05-01 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001351 | 21574 | 322 | 67 | HB-S15-01 | Harbor | 2026-05-01 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-26-001352 | 4620 | 77 | 60 | BY-S15-03 | Bayou | 2026-05-01 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-001353 | 15500 | 125 | 124 | BY-S15-05 | Bayou | 2026-05-01 | 14 | Animal | Lateral fuse | Forced | None
OE-26-001354 | 1974 | 47 | 42 | BY-S24-04 | Bayou | 2026-05-01 | 14 | Unknown | Lateral fuse | Forced | None
OE-26-001355 | 1890 | 10 | 189 | CR-S23-02 | Crossroads | 2026-05-01 | 14 | Unknown | Transformer fuse | Forced | None
OE-26-001356 | 3192 | 14 | 228 | BY-S08-02 | Bayou | 2026-05-01 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001357 | 693 | 11 | 63 | HB-S02-03 | Harbor | 2026-05-01 | 16 | Animal | Transformer fuse | Forced | None
OE-26-001358 | 48641 | 383 | 127 | PR-S15-02 | Prairie | 2026-05-01 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-001359 | 12031 | 53 | 227 | PR-S14-04 | Prairie | 2026-05-01 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001360 | 55224 | 531 | 104 | BY-S22-03 | Bayou | 2026-05-01 | 22 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001361 | 18290 | 155 | 118 | PR-S18-05 | Prairie | 2026-05-02 | 1 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001362 | 62 | 2 | 31 | CR-S16-01 | Crossroads | 2026-05-02 | 2 | Unknown | Transformer fuse | Forced | None
OE-26-001363 | 536 | 2 | 268 | BY-S10-03 | Bayou | 2026-05-02 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-001364 | 46332 | 572 | 81 | BY-S11-03 | Bayou | 2026-05-02 | 13 | Vegetation | Feeder recloser | Forced | None
OE-26-001365 | 366 | 2 | 183 | PR-S04-03 | Prairie | 2026-05-02 | 13 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001366 | 864 | 8 | 108 | BY-S13-02 | Bayou | 2026-05-02 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-001367 | 2376 | 8 | 297 | CR-S04-02 | Crossroads | 2026-05-02 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001368 | 6868 | 101 | 68 | CR-S21-03 | Crossroads | 2026-05-02 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001369 | 1566 | 9 | 174 | BY-S07-02 | Bayou | 2026-05-02 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001370 | 1333 | 31 | 43 | CR-S12-01 | Crossroads | 2026-05-02 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001371 | 4641 | 51 | 91 | CR-S22-01 | Crossroads | 2026-05-02 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-26-001372 | 1064 | 28 | 38 | BY-S30-03 | Bayou | 2026-05-02 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001373 | 2640 | 8 | 330 | BY-S21-04 | Bayou | 2026-05-02 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-001374 | 270 | 5 | 54 | CR-S24-01 | Crossroads | 2026-05-02 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001375 | 298 | 1 | 298 | BY-S09-01 | Bayou | 2026-05-02 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-001376 | 31900 | 110 | 290 | BY-S13-01 | Bayou | 2026-05-02 | 20 | Animal | Lateral fuse | Forced | None
OE-26-001377 | 21052 | 277 | 76 | CR-S10-02 | Crossroads | 2026-05-02 | 21 | Weather - wind | IGSD-isolated section | Forced | None
OE-26-001378 | 2989 | 49 | 61 | CR-S05-02 | Crossroads | 2026-05-03 | 0 | Animal | Lateral fuse | Forced | None
OE-26-001379 | 1008 | 12 | 84 | PR-S10-03 | Prairie | 2026-05-03 | 1 | Vegetation | Transformer fuse | Forced | None
OE-26-001380 | 2673 | 11 | 243 | PR-S09-04 | Prairie | 2026-05-03 | 3 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001381 | 13635 | 101 | 135 | BY-S01-02 | Bayou | 2026-05-03 | 6 | Vegetation | Lateral fuse | Forced | None
OE-26-001382 | 36934 | 59 | 626 | BY-S02-01 | Bayou | 2026-05-03 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001383 | 9261 | 189 | 49 | HB-S15-02 | Harbor | 2026-05-03 | 9 | Animal | Lateral fuse | Forced | None
OE-26-001384 | 1680 | 8 | 210 | CR-S18-06 | Crossroads | 2026-05-03 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-26-001385 | 8330 | 98 | 85 | BY-S28-02 | Bayou | 2026-05-03 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-001386 | 33405 | 255 | 131 | BY-S07-05 | Bayou | 2026-05-03 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001387 | 133722 | 1938 | 69 | BY-S19-02 | Bayou | 2026-05-03 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001388 | 4788 | 42 | 114 | BY-S24-02 | Bayou | 2026-05-03 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-001389 | 2268 | 14 | 162 | CR-S18-01 | Crossroads | 2026-05-03 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001390 | 2555 | 5 | 511 | BY-S16-01 | Bayou | 2026-05-03 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001391 | 12354 | 142 | 87 | CR-S04-01 | Crossroads | 2026-05-03 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001392 | 27720 | 99 | 280 | HB-S04-02 | Harbor | 2026-05-03 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001393 | 1080 | 6 | 180 | HB-S19-04 | Harbor | 2026-05-03 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-001394 | 1188 | 9 | 132 | HB-S16-01 | Harbor | 2026-05-03 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-26-001395 | 4810 | 13 | 370 | BY-S09-04 | Bayou | 2026-05-03 | 21 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001396 | 2185 | 19 | 115 | BY-S15-02 | Bayou | 2026-05-03 | 23 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001397 | 1176 | 12 | 98 | CR-S14-01 | Crossroads | 2026-05-03 | 23 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001398 | 216480 | 1760 | 123 | HB-S05-06 | Harbor | 2026-05-04 | 8 | Vegetation | Feeder recloser | Forced | None
OE-26-001399 | 4305 | 41 | 105 | PR-S13-05 | Prairie | 2026-05-04 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-001400 | 3872 | 32 | 121 | BY-S15-05 | Bayou | 2026-05-04 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001401 | 6993 | 21 | 333 | BY-S13-06 | Bayou | 2026-05-04 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-001402 | 1036 | 14 | 74 | BY-S19-01 | Bayou | 2026-05-04 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001403 | 17818 | 118 | 151 | BY-S25-04 | Bayou | 2026-05-04 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-001404 | 16720 | 176 | 95 | HB-S08-02 | Harbor | 2026-05-04 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-001405 | 1834 | 14 | 131 | CR-S14-01 | Crossroads | 2026-05-04 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001406 | 389 | 1 | 389 | CR-S19-04 | Crossroads | 2026-05-04 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001407 | 750 | 5 | 150 | CR-S19-04 | Crossroads | 2026-05-04 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001408 | 792 | 4 | 198 | BY-S02-02 | Bayou | 2026-05-04 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001409 | 2540 | 10 | 254 | BY-S30-02 | Bayou | 2026-05-04 | 23 | Animal | Transformer fuse | Forced | None
OE-26-001410 | 39468 | 253 | 156 | CR-S04-05 | Crossroads | 2026-05-04 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001411 | 624 | 3 | 208 | BY-S13-02 | Bayou | 2026-05-05 | 6 | Animal | Transformer fuse | Forced | None
OE-26-001412 | 15872 | 248 | 64 | BY-S16-05 | Bayou | 2026-05-05 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001413 | 26312 | 143 | 184 | CR-S21-01 | Crossroads | 2026-05-05 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001414 | 3325 | 19 | 175 | CR-S08-06 | Crossroads | 2026-05-05 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001415 | 50 | 1 | 50 | CR-S14-05 | Crossroads | 2026-05-05 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001416 | 2109 | 19 | 111 | HB-S06-04 | Harbor | 2026-05-05 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001417 | 984 | 4 | 246 | HB-S08-01 | Harbor | 2026-05-05 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-001418 | 33040 | 280 | 118 | BY-S26-03 | Bayou | 2026-05-05 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001419 | 28608 | 149 | 192 | BY-S30-01 | Bayou | 2026-05-05 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-001420 | 120 | 2 | 60 | HB-S15-02 | Harbor | 2026-05-05 | 22 | Vegetation | Transformer fuse | Forced | None
OE-26-001421 | 1832 | 8 | 229 | PR-S01-01 | Prairie | 2026-05-06 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-001422 | 1932 | 14 | 138 | BY-S28-03 | Bayou | 2026-05-06 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001423 | 684 | 6 | 114 | PR-S09-02 | Prairie | 2026-05-06 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001424 | 191 | 1 | 191 | PR-S02-02 | Prairie | 2026-05-06 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001425 | 1239 | 7 | 177 | PR-S04-01 | Prairie | 2026-05-06 | 9 | Unknown | Transformer fuse | Forced | None
OE-26-001426 | 2184 | 26 | 84 | BY-S10-04 | Bayou | 2026-05-06 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-001427 | 1677 | 13 | 129 | BY-S07-05 | Bayou | 2026-05-06 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001428 | 3648 | 38 | 96 | BY-S08-02 | Bayou | 2026-05-06 | 12 | Unknown | Lateral fuse | Forced | None
OE-26-001429 | 510 | 6 | 85 | HB-S08-03 | Harbor | 2026-05-06 | 13 | Unknown | Transformer fuse | Forced | None
OE-26-001430 | 2086 | 14 | 149 | BY-S22-04 | Bayou | 2026-05-06 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001431 | 536 | 4 | 134 | PR-S03-04 | Prairie | 2026-05-06 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001432 | 236 | 1 | 236 | BY-S05-01 | Bayou | 2026-05-06 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-001433 | 2256 | 12 | 188 | BY-S30-03 | Bayou | 2026-05-06 | 16 | Animal | Transformer fuse | Forced | None
OE-26-001434 | 1456 | 13 | 112 | BY-S25-04 | Bayou | 2026-05-06 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001435 | 2300 | 10 | 230 | HB-S05-06 | Harbor | 2026-05-06 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-001436 | 1235 | 5 | 247 | BY-S07-02 | Bayou | 2026-05-06 | 18 | Unknown | Transformer fuse | Forced | None
OE-26-001437 | 76734 | 1218 | 63 | HB-S03-01 | Harbor | 2026-05-06 | 18 | Vegetation | Substation breaker | Forced | None
OE-26-001438 | 1264 | 8 | 158 | BY-S24-04 | Bayou | 2026-05-06 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-001439 | 2212 | 14 | 158 | BY-S19-04 | Bayou | 2026-05-06 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-001440 | 4872 | 84 | 58 | CR-S23-04 | Crossroads | 2026-05-06 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-001441 | 363 | 3 | 121 | BY-S25-02 | Bayou | 2026-05-06 | 22 | Vegetation | Transformer fuse | Forced | None
OE-26-001442 | 4340 | 14 | 310 | CR-S09-05 | Crossroads | 2026-05-07 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001443 | 6050 | 50 | 121 | BY-S22-03 | Bayou | 2026-05-07 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001444 | 5412 | 44 | 123 | BY-S11-02 | Bayou | 2026-05-07 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-001445 | 4117 | 23 | 179 | HB-S12-03 | Harbor | 2026-05-07 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001446 | 1890 | 14 | 135 | HB-S16-01 | Harbor | 2026-05-07 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-001447 | 11592 | 72 | 161 | PR-S03-02 | Prairie | 2026-05-07 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001448 | 2079 | 33 | 63 | BY-S26-04 | Bayou | 2026-05-07 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001449 | 28440 | 948 | 30 | CR-S15-03 | Crossroads | 2026-05-07 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001450 | 1274 | 7 | 182 | PR-S08-01 | Prairie | 2026-05-07 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-26-001451 | 276 | 2 | 138 | CR-S26-02 | Crossroads | 2026-05-07 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001452 | 175086 | 2466 | 71 | CR-S17-01 | Crossroads | 2026-05-07 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001453 | 318150 | 1010 | 315 | CR-S20-05 | Crossroads | 2026-05-07 | 15 | Weather - lightning | Feeder recloser | Forced | None
OE-26-001454 | 536 | 8 | 67 | HB-S01-01 | Harbor | 2026-05-07 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001455 | 324 | 4 | 81 | CR-S14-03 | Crossroads | 2026-05-07 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001456 | 50862 | 173 | 294 | PR-S03-05 | Prairie | 2026-05-07 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001457 | 10985 | 65 | 169 | BY-S23-02 | Bayou | 2026-05-08 | 2 | Vegetation | Lateral fuse | Forced | None
OE-26-001458 | 1624 | 14 | 116 | BY-S10-02 | Bayou | 2026-05-08 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-001459 | 20500 | 100 | 205 | BY-S11-02 | Bayou | 2026-05-08 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-001460 | 952 | 8 | 119 | PR-S19-01 | Prairie | 2026-05-08 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001461 | 78540 | 935 | 84 | CR-S10-03 | Crossroads | 2026-05-08 | 13 | Animal | Feeder recloser | Forced | None
OE-26-001462 | 2320 | 4 | 580 | PR-S01-05 | Prairie | 2026-05-08 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001463 | 307 | 1 | 307 | PR-S10-01 | Prairie | 2026-05-08 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-001464 | 425 | 5 | 85 | BY-S13-01 | Bayou | 2026-05-08 | 14 | Unknown | Transformer fuse | Forced | None
OE-26-001465 | 540 | 6 | 90 | HB-S14-01 | Harbor | 2026-05-09 | 0 | Vegetation | Transformer fuse | Forced | None
OE-26-001466 | 13020 | 70 | 186 | BY-S24-05 | Bayou | 2026-05-09 | 1 | Vegetation | Lateral fuse | Forced | None
OE-26-001467 | 344 | 1 | 344 | CR-S05-06 | Crossroads | 2026-05-09 | 7 | Animal | Transformer fuse | Forced | None
OE-26-001468 | 4950 | 25 | 198 | BY-S22-04 | Bayou | 2026-05-09 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-001469 | 2088 | 36 | 58 | BY-S23-03 | Bayou | 2026-05-09 | 9 | Animal | Lateral fuse | Forced | None
OE-26-001470 | 990 | 9 | 110 | BY-S28-01 | Bayou | 2026-05-09 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-001471 | 2496 | 13 | 192 | CR-S23-05 | Crossroads | 2026-05-09 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001472 | 855 | 5 | 171 | HB-S09-03 | Harbor | 2026-05-09 | 11 | Weather - wind | Transformer fuse | Forced | None
OE-26-001473 | 3860 | 10 | 386 | PR-S06-03 | Prairie | 2026-05-09 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001474 | 37752 | 78 | 484 | BY-S23-03 | Bayou | 2026-05-09 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001475 | 690 | 10 | 69 | BY-S07-01 | Bayou | 2026-05-09 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-001476 | 2923 | 79 | 37 | CR-S07-01 | Crossroads | 2026-05-09 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001477 | 3900 | 12 | 325 | HB-S08-02 | Harbor | 2026-05-09 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-001478 | 8702 | 38 | 229 | HB-S14-03 | Harbor | 2026-05-09 | 21 | Weather - wind | Lateral fuse | Forced | None
OE-26-001479 | 66875 | 625 | 107 | HB-S15-02 | Harbor | 2026-05-10 | 1 | Vegetation | Feeder recloser | Forced | None
OE-26-001480 | 12312 | 38 | 324 | BY-S16-01 | Bayou | 2026-05-10 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-001481 | 4756 | 58 | 82 | PR-S18-01 | Prairie | 2026-05-10 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001482 | 3094 | 14 | 221 | BY-S23-04 | Bayou | 2026-05-10 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-001483 | 2952 | 9 | 328 | BY-S02-01 | Bayou | 2026-05-10 | 13 | Animal | Transformer fuse | Forced | None
OE-26-001484 | 21414 | 86 | 249 | BY-S30-02 | Bayou | 2026-05-10 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001485 | 1212 | 12 | 101 | BY-S18-05 | Bayou | 2026-05-10 | 14 | Animal | Transformer fuse | Forced | None
OE-26-001486 | 3589 | 37 | 97 | BY-S04-02 | Bayou | 2026-05-10 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-001487 | 10422 | 54 | 193 | BY-S11-01 | Bayou | 2026-05-10 | 16 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001488 | 37440 | 288 | 130 | HB-S04-02 | Harbor | 2026-05-10 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-26-001489 | 11607 | 159 | 73 | PR-S03-01 | Prairie | 2026-05-10 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-001490 | 8217 | 33 | 249 | HB-S08-04 | Harbor | 2026-05-10 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001491 | 180 | 2 | 90 | CR-S23-01 | Crossroads | 2026-05-10 | 22 | Weather - wind | Transformer fuse | Forced | None
OE-26-001492 | 468 | 6 | 78 | PR-S15-05 | Prairie | 2026-05-11 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001493 | 56 | 1 | 56 | CR-S13-01 | Crossroads | 2026-05-11 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001494 | 3670 | 10 | 367 | PR-S06-01 | Prairie | 2026-05-11 | 5 | Vegetation | Transformer fuse | Forced | None
OE-26-001495 | 9945 | 85 | 117 | PR-S07-04 | Prairie | 2026-05-11 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001496 | 1529 | 11 | 139 | CR-S20-05 | Crossroads | 2026-05-11 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001497 | 3348 | 12 | 279 | CR-S28-03 | Crossroads | 2026-05-11 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001498 | 27645 | 291 | 95 | BY-S28-01 | Bayou | 2026-05-11 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-001499 | 2860 | 13 | 220 | HB-S16-03 | Harbor | 2026-05-11 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-001500 | 45100 | 220 | 205 | HB-S16-03 | Harbor | 2026-05-11 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-001501 | 39186 | 311 | 126 | CR-S18-05 | Crossroads | 2026-05-11 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001502 | 7439 | 43 | 173 | PR-S04-02 | Prairie | 2026-05-11 | 21 | Animal | Lateral fuse | Forced | None
OE-26-001503 | 169740 | 943 | 180 | HB-S09-04 | Harbor | 2026-05-12 | 5 | Vegetation | Substation breaker | Forced | None
OE-26-001504 | 4964 | 68 | 73 | BY-S24-01 | Bayou | 2026-05-12 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001505 | 5472 | 12 | 456 | PR-S03-04 | Prairie | 2026-05-12 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001506 | 171404 | 1174 | 146 | BY-S03-02 | Bayou | 2026-05-12 | 8 | Weather - wind | Feeder recloser | Forced | None
OE-26-001507 | 6674 | 47 | 142 | BY-S22-04 | Bayou | 2026-05-12 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-001508 | 663 | 3 | 221 | BY-S03-02 | Bayou | 2026-05-12 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-26-001509 | 5304 | 39 | 136 | PR-S08-01 | Prairie | 2026-05-12 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001510 | 273 | 3 | 91 | CR-S05-05 | Crossroads | 2026-05-12 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001511 | 13845 | 213 | 65 | CR-S20-01 | Crossroads | 2026-05-12 | 11 | Vegetation | IGSD-isolated section | Forced | None
OE-26-001512 | 183 | 1 | 183 | CR-S24-01 | Crossroads | 2026-05-12 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001513 | 36246 | 863 | 42 | CR-S28-01 | Crossroads | 2026-05-12 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001514 | 3150 | 9 | 350 | CR-S13-06 | Crossroads | 2026-05-12 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001515 | 11342 | 107 | 106 | CR-S24-03 | Crossroads | 2026-05-12 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001516 | 1925 | 11 | 175 | HB-S01-01 | Harbor | 2026-05-12 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001517 | 6028 | 44 | 137 | PR-S19-02 | Prairie | 2026-05-12 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-001518 | 65200 | 1630 | 40 | PR-S06-01 | Prairie | 2026-05-12 | 18 | Equipment - overhead | Substation breaker | Outside cause | None
OE-26-001519 | 18109 | 91 | 199 | PR-S18-01 | Prairie | 2026-05-13 | 2 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001520 | 12320 | 80 | 154 | BY-S28-02 | Bayou | 2026-05-13 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001521 | 1353 | 11 | 123 | CR-S08-02 | Crossroads | 2026-05-13 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-26-001522 | 4325 | 25 | 173 | CR-S20-02 | Crossroads | 2026-05-13 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001523 | 214 | 1 | 214 | CR-S04-03 | Crossroads | 2026-05-13 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001524 | 18942 | 77 | 246 | CR-S12-03 | Crossroads | 2026-05-13 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001525 | 4988 | 29 | 172 | CR-S26-02 | Crossroads | 2026-05-13 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001526 | 2448 | 34 | 72 | PR-S03-02 | Prairie | 2026-05-13 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001527 | 1566 | 9 | 174 | BY-S15-02 | Bayou | 2026-05-13 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-26-001528 | 1544 | 8 | 193 | BY-S29-03 | Bayou | 2026-05-13 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001529 | 24576 | 768 | 32 | BY-S14-01 | Bayou | 2026-05-13 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001530 | 4920 | 40 | 123 | HB-S18-03 | Harbor | 2026-05-13 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001531 | 42401 | 389 | 109 | BY-S09-02 | Bayou | 2026-05-13 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001532 | 7400 | 40 | 185 | BY-S23-01 | Bayou | 2026-05-13 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001533 | 8938 | 82 | 109 | BY-S05-01 | Bayou | 2026-05-13 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-001534 | 790 | 10 | 79 | PR-S14-04 | Prairie | 2026-05-13 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001535 | 480 | 3 | 160 | CR-S16-06 | Crossroads | 2026-05-13 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001536 | 2422 | 14 | 173 | PR-S06-01 | Prairie | 2026-05-13 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001537 | 9900 | 55 | 180 | HB-S03-01 | Harbor | 2026-05-13 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-001538 | 140000 | 400 | 350 | HB-S19-04 | Harbor | 2026-05-13 | 20 | Unknown | Lateral fuse | Forced | None
OE-26-001539 | 1302 | 7 | 186 | BY-S21-04 | Bayou | 2026-05-13 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-001540 | 3477 | 61 | 57 | CR-S06-03 | Crossroads | 2026-05-14 | 6 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001541 | 1070 | 10 | 107 | BY-S02-01 | Bayou | 2026-05-14 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001542 | 3404 | 37 | 92 | BY-S23-04 | Bayou | 2026-05-14 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001543 | 4818 | 66 | 73 | BY-S26-05 | Bayou | 2026-05-14 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-001544 | 2240 | 14 | 160 | CR-S02-01 | Crossroads | 2026-05-14 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001545 | 2981 | 11 | 271 | CR-S27-04 | Crossroads | 2026-05-14 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001546 | 8277 | 89 | 93 | BY-S10-04 | Bayou | 2026-05-14 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001547 | 15060 | 60 | 251 | CR-S15-01 | Crossroads | 2026-05-14 | 13 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001548 | 64620 | 359 | 180 | PR-S11-01 | Prairie | 2026-05-14 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-26-001549 | 12285 | 65 | 189 | BY-S02-02 | Bayou | 2026-05-14 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-001550 | 1266 | 3 | 422 | BY-S24-02 | Bayou | 2026-05-14 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001551 | 945 | 9 | 105 | CR-S07-01 | Crossroads | 2026-05-14 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001552 | 47574 | 1762 | 27 | PR-S08-02 | Prairie | 2026-05-15 | 0 | Vehicle or public | Substation breaker | Forced | None
OE-26-001553 | 23940 | 90 | 266 | PR-S18-06 | Prairie | 2026-05-15 | 6 | Vegetation | Lateral fuse | Forced | None
OE-26-001554 | 469450 | 1145 | 410 | CR-S12-01 | Crossroads | 2026-05-15 | 7 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001555 | 846 | 9 | 94 | BY-S18-06 | Bayou | 2026-05-15 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-001556 | 13760 | 86 | 160 | PR-S05-01 | Prairie | 2026-05-15 | 8 | Animal | Lateral fuse | Forced | None
OE-26-001557 | 9536 | 149 | 64 | CR-S05-04 | Crossroads | 2026-05-15 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001558 | 3740 | 68 | 55 | CR-S25-06 | Crossroads | 2026-05-15 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-001559 | 721 | 7 | 103 | PR-S11-03 | Prairie | 2026-05-15 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001560 | 770 | 7 | 110 | BY-S13-06 | Bayou | 2026-05-15 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001561 | 23664 | 408 | 58 | CR-S25-04 | Crossroads | 2026-05-15 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001562 | 872 | 4 | 218 | HB-S07-02 | Harbor | 2026-05-15 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001563 | 4708 | 44 | 107 | HB-S09-02 | Harbor | 2026-05-15 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-001564 | 101355 | 699 | 145 | PR-S01-06 | Prairie | 2026-05-15 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-26-001565 | 760 | 8 | 95 | BY-S23-03 | Bayou | 2026-05-15 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001566 | 5208 | 21 | 248 | CR-S16-02 | Crossroads | 2026-05-15 | 15 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001567 | 143 | 1 | 143 | HB-S09-05 | Harbor | 2026-05-15 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001568 | 57954 | 1486 | 39 | HB-S17-01 | Harbor | 2026-05-15 | 17 | Weather - lightning | Substation breaker | Forced | None
OE-26-001569 | 3072 | 12 | 256 | HB-S17-03 | Harbor | 2026-05-15 | 17 | Unknown | Transformer fuse | Forced | None
OE-26-001570 | 10974 | 93 | 118 | CR-S04-06 | Crossroads | 2026-05-15 | 18 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001571 | 243 | 3 | 81 | CR-S12-02 | Crossroads | 2026-05-15 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001572 | 1344 | 8 | 168 | PR-S01-06 | Prairie | 2026-05-15 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001573 | 1820 | 13 | 140 | CR-S22-03 | Crossroads | 2026-05-15 | 19 | Animal | Transformer fuse | Forced | None
OE-26-001574 | 5440 | 160 | 34 | CR-S24-02 | Crossroads | 2026-05-15 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001575 | 9660 | 35 | 276 | HB-S15-03 | Harbor | 2026-05-15 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001576 | 66208 | 2069 | 32 | CR-S14-02 | Crossroads | 2026-05-15 | 23 | Unknown | Feeder recloser | Forced | None
OE-26-001577 | 270 | 1 | 270 | HB-S01-05 | Harbor | 2026-05-16 | 0 | Animal | Transformer fuse | Forced | None
OE-26-001578 | 855 | 3 | 285 | HB-S08-05 | Harbor | 2026-05-16 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-001579 | 636 | 3 | 212 | BY-S09-02 | Bayou | 2026-05-16 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001580 | 6804 | 108 | 63 | CR-S08-05 | Crossroads | 2026-05-16 | 8 | Animal | Lateral fuse | Forced | None
OE-26-001581 | 1826 | 11 | 166 | HB-S18-01 | Harbor | 2026-05-16 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-001582 | 18525 | 475 | 39 | CR-S30-01 | Crossroads | 2026-05-16 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-26-001583 | 715 | 5 | 143 | CR-S32-02 | Crossroads | 2026-05-16 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001584 | 5838 | 42 | 139 | PR-S13-03 | Prairie | 2026-05-16 | 14 | Animal | Lateral fuse | Forced | None
OE-26-001585 | 93636 | 1156 | 81 | CR-S23-02 | Crossroads | 2026-05-16 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001586 | 2529 | 9 | 281 | CR-S30-05 | Crossroads | 2026-05-16 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-001587 | 6816 | 142 | 48 | HB-S01-03 | Harbor | 2026-05-16 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001588 | 50128 | 208 | 241 | CR-S17-03 | Crossroads | 2026-05-16 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001589 | 23400 | 104 | 225 | HB-S09-03 | Harbor | 2026-05-16 | 18 | Unknown | Lateral fuse | Forced | None
OE-26-001590 | 5402 | 74 | 73 | HB-S05-06 | Harbor | 2026-05-16 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-001591 | 920 | 10 | 92 | PR-S15-06 | Prairie | 2026-05-16 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-001592 | 11045 | 235 | 47 | BY-S24-02 | Bayou | 2026-05-16 | 21 | Vehicle or public | Lateral fuse | Forced | None
OE-26-001593 | 1449 | 9 | 161 | CR-S24-04 | Crossroads | 2026-05-16 | 21 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001594 | 2115 | 9 | 235 | CR-S26-06 | Crossroads | 2026-05-16 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-001595 | 9600 | 64 | 150 | PR-S16-05 | Prairie | 2026-05-17 | 0 | Weather - wind | Lateral fuse | Forced | None
OE-26-001596 | 18972 | 62 | 306 | BY-S12-01 | Bayou | 2026-05-17 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001597 | 2124 | 6 | 354 | PR-S02-01 | Prairie | 2026-05-17 | 2 | Vegetation | Transformer fuse | Forced | None
OE-26-001598 | 3600 | 45 | 80 | BY-S26-05 | Bayou | 2026-05-17 | 6 | Vegetation | Lateral fuse | Forced | None
OE-26-001599 | 15812 | 134 | 118 | CR-S02-05 | Crossroads | 2026-05-17 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001600 | 15314 | 494 | 31 | HB-S06-05 | Harbor | 2026-05-17 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001601 | 13612 | 164 | 83 | BY-S14-03 | Bayou | 2026-05-17 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-001602 | 354 | 3 | 118 | CR-S06-01 | Crossroads | 2026-05-17 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-001603 | 8132 | 76 | 107 | CR-S12-03 | Crossroads | 2026-05-17 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001604 | 435 | 5 | 87 | HB-S02-01 | Harbor | 2026-05-17 | 15 | Animal | Transformer fuse | Forced | None
OE-26-001605 | 1236 | 12 | 103 | CR-S04-02 | Crossroads | 2026-05-17 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001606 | 720 | 4 | 180 | PR-S03-05 | Prairie | 2026-05-17 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-001607 | 47232 | 1312 | 36 | BY-S13-05 | Bayou | 2026-05-17 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001608 | 91 | 1 | 91 | PR-S09-02 | Prairie | 2026-05-17 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-001609 | 3770 | 10 | 377 | CR-S27-04 | Crossroads | 2026-05-17 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001610 | 3816 | 24 | 159 | HB-S14-01 | Harbor | 2026-05-17 | 22 | Vegetation | Lateral fuse | Forced | None
OE-26-001611 | 44352 | 176 | 252 | PR-S14-02 | Prairie | 2026-05-17 | 22 | Weather - wind | Feeder recloser | Forced | None
OE-26-001612 | 2340 | 39 | 60 | CR-S22-01 | Crossroads | 2026-05-17 | 23 | Vegetation | Lateral fuse | Forced | None
OE-26-001613 | 1749 | 11 | 159 | CR-S32-05 | Crossroads | 2026-05-18 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001614 | 1506 | 6 | 251 | PR-S06-01 | Prairie | 2026-05-18 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-001615 | 101080 | 1064 | 95 | BY-S10-05 | Bayou | 2026-05-18 | 12 | Weather - lightning | Substation breaker | Forced | None
OE-26-001616 | 2068 | 11 | 188 | PR-S13-01 | Prairie | 2026-05-18 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-001617 | 172 | 1 | 172 | HB-S07-04 | Harbor | 2026-05-18 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-001618 | 430 | 5 | 86 | HB-S16-04 | Harbor | 2026-05-18 | 14 | Animal | Transformer fuse | Forced | None
OE-26-001619 | 3726 | 46 | 81 | HB-S16-01 | Harbor | 2026-05-18 | 16 | Animal | Lateral fuse | Forced | None
OE-26-001620 | 16650 | 111 | 150 | HB-S16-04 | Harbor | 2026-05-18 | 17 | Unknown | Lateral fuse | Forced | None
OE-26-001621 | 22168 | 163 | 136 | HB-S12-01 | Harbor | 2026-05-18 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001622 | 2834 | 26 | 109 | BY-S07-01 | Bayou | 2026-05-19 | 3 | Vegetation | Lateral fuse | Forced | None
OE-26-001623 | 26780 | 130 | 206 | PR-S12-01 | Prairie | 2026-05-19 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001624 | 5687 | 47 | 121 | PR-S20-01 | Prairie | 2026-05-19 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001625 | 3056 | 8 | 382 | BY-S07-05 | Bayou | 2026-05-19 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001626 | 80662 | 1301 | 62 | BY-S27-06 | Bayou | 2026-05-19 | 11 | Animal | Feeder recloser | Forced | None
OE-26-001627 | 2211 | 11 | 201 | CR-S10-03 | Crossroads | 2026-05-19 | 11 | Vehicle or public | Transformer fuse | Forced | None
OE-26-001628 | 466500 | 933 | 500 | CR-S10-03 | Crossroads | 2026-05-19 | 11 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001629 | 26908 | 31 | 868 | PR-S03-03 | Prairie | 2026-05-19 | 11 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001630 | 317016 | 306 | 1036 | PR-S09-04 | Prairie | 2026-05-19 | 11 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001631 | 2673880 | 590 | 4532 | BY-S15-01 | Bayou | 2026-05-19 | 11 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001632 | 236700 | 180 | 1315 | BY-S18-05 | Bayou | 2026-05-19 | 11 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001633 | 20126 | 58 | 347 | BY-S22-04 | Bayou | 2026-05-19 | 11 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001634 | 117990 | 54 | 2185 | PR-S13-02 | Prairie | 2026-05-19 | 11 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001635 | 1063888 | 644 | 1652 | BY-S23-01 | Bayou | 2026-05-19 | 11 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001636 | 47700 | 36 | 1325 | BY-S09-05 | Bayou | 2026-05-19 | 11 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001637 | 319455 | 229 | 1395 | PR-S15-06 | Prairie | 2026-05-19 | 11 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001638 | 971290 | 1030 | 943 | CR-S06-02 | Crossroads | 2026-05-19 | 12 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001639 | 245927 | 283 | 869 | PR-S03-04 | Prairie | 2026-05-19 | 12 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001640 | 535829 | 287 | 1867 | PR-S19-02 | Prairie | 2026-05-19 | 12 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001641 | 15680 | 16 | 980 | CR-S16-01 | Crossroads | 2026-05-19 | 12 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001642 | 950242 | 1114 | 853 | PR-S03-05 | Prairie | 2026-05-19 | 12 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001643 | 397647 | 207 | 1921 | PR-S11-03 | Prairie | 2026-05-19 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001644 | 349856 | 754 | 464 | CR-S32-05 | Crossroads | 2026-05-19 | 12 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001645 | 234572 | 338 | 694 | PR-S12-02 | Prairie | 2026-05-19 | 12 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001646 | 8721 | 17 | 513 | CR-S20-05 | Crossroads | 2026-05-19 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001647 | 204194 | 529 | 386 | PR-S07-04 | Prairie | 2026-05-19 | 12 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001648 | 419577 | 969 | 433 | PR-S15-01 | Prairie | 2026-05-19 | 12 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001649 | 340416 | 432 | 788 | BY-S22-02 | Bayou | 2026-05-19 | 12 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001650 | 262430 | 230 | 1141 | CR-S14-04 | Crossroads | 2026-05-19 | 12 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001651 | 187332 | 233 | 804 | BY-S20-03 | Bayou | 2026-05-19 | 12 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001652 | 269814 | 1398 | 193 | HB-S14-04 | Harbor | 2026-05-19 | 12 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001653 | 36504 | 78 | 468 | PR-S09-02 | Prairie | 2026-05-19 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001654 | 235664 | 572 | 412 | HB-S03-01 | Harbor | 2026-05-19 | 12 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001655 | 391980 | 695 | 564 | BY-S21-02 | Bayou | 2026-05-19 | 12 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001656 | 1419244 | 538 | 2638 | PR-S08-02 | Prairie | 2026-05-19 | 12 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001657 | 271824 | 1618 | 168 | CR-S24-01 | Crossroads | 2026-05-19 | 12 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001658 | 53379 | 81 | 659 | BY-S02-02 | Bayou | 2026-05-19 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001659 | 695544 | 397 | 1752 | BY-S04-03 | Bayou | 2026-05-19 | 12 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001660 | 423720 | 642 | 660 | PR-S13-06 | Prairie | 2026-05-19 | 12 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001661 | 296603 | 179 | 1657 | BY-S27-05 | Bayou | 2026-05-19 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001662 | 51500 | 25 | 2060 | PR-S02-01 | Prairie | 2026-05-19 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001663 | 65132 | 38 | 1714 | BY-S07-05 | Bayou | 2026-05-19 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001664 | 188 | 2 | 94 | HB-S06-05 | Harbor | 2026-05-19 | 13 | Unknown | Transformer fuse | Forced | None
OE-26-001665 | 43632 | 16 | 2727 | PR-S19-03 | Prairie | 2026-05-19 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001666 | 337680 | 240 | 1407 | PR-S15-04 | Prairie | 2026-05-19 | 13 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001667 | 234784 | 352 | 667 | PR-S18-02 | Prairie | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001668 | 656185 | 499 | 1315 | PR-S16-02 | Prairie | 2026-05-19 | 13 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001669 | 251674 | 358 | 703 | CR-S07-04 | Crossroads | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001670 | 207075 | 251 | 825 | CR-S01-01 | Crossroads | 2026-05-19 | 13 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001671 | 462245 | 281 | 1645 | CR-S26-05 | Crossroads | 2026-05-19 | 13 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001672 | 154800 | 75 | 2064 | PR-S18-01 | Prairie | 2026-05-19 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001673 | 774200 | 490 | 1580 | BY-S18-06 | Bayou | 2026-05-19 | 13 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001674 | 475416 | 568 | 837 | PR-S07-06 | Prairie | 2026-05-19 | 13 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001675 | 71346 | 253 | 282 | CR-S01-02 | Crossroads | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001676 | 212688 | 252 | 844 | PR-S09-01 | Prairie | 2026-05-19 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001677 | 190247 | 589 | 323 | CR-S31-03 | Crossroads | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001678 | 46645 | 95 | 491 | PR-S02-02 | Prairie | 2026-05-19 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001679 | 1371052 | 971 | 1412 | BY-S08-03 | Bayou | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001680 | 792484 | 868 | 913 | HB-S16-03 | Harbor | 2026-05-19 | 13 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001681 | 3384041 | 2767 | 1223 | BY-S29-01 | Bayou | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001682 | 123804 | 342 | 362 | PR-S11-01 | Prairie | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001683 | 64064 | 208 | 308 | BY-S15-05 | Bayou | 2026-05-19 | 13 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001684 | 53676 | 378 | 142 | HB-S19-01 | Harbor | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001685 | 16200 | 36 | 450 | BY-S13-03 | Bayou | 2026-05-19 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001686 | 301857 | 421 | 717 | HB-S07-04 | Harbor | 2026-05-19 | 13 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001687 | 54549 | 99 | 551 | PR-S16-05 | Prairie | 2026-05-19 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001688 | 234567 | 603 | 389 | PR-S17-02 | Prairie | 2026-05-19 | 13 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001689 | 81228 | 84 | 967 | PR-S15-03 | Prairie | 2026-05-19 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001690 | 86240 | 110 | 784 | PR-S05-02 | Prairie | 2026-05-19 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001691 | 1463490 | 1035 | 1414 | BY-S19-01 | Bayou | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001692 | 682889 | 383 | 1783 | CR-S16-05 | Crossroads | 2026-05-19 | 13 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001693 | 617520 | 744 | 830 | PR-S04-02 | Prairie | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001694 | 258552 | 456 | 567 | BY-S11-02 | Bayou | 2026-05-19 | 13 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001695 | 847208 | 548 | 1546 | BY-S21-04 | Bayou | 2026-05-19 | 13 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001696 | 1190 | 10 | 119 | CR-S28-03 | Crossroads | 2026-05-19 | 14 | Unknown | Transformer fuse | Forced | None
OE-26-001697 | 63787 | 227 | 281 | CR-S12-02 | Crossroads | 2026-05-19 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001698 | 234724 | 202 | 1162 | HB-S05-04 | Harbor | 2026-05-19 | 14 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001699 | 32175 | 99 | 325 | HB-S08-02 | Harbor | 2026-05-19 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001700 | 549549 | 427 | 1287 | BY-S07-01 | Bayou | 2026-05-19 | 14 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001701 | 1719354 | 987 | 1742 | BY-S18-01 | Bayou | 2026-05-19 | 14 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001702 | 314238 | 498 | 631 | PR-S18-03 | Prairie | 2026-05-19 | 14 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001703 | 56000 | 80 | 700 | BY-S24-04 | Bayou | 2026-05-19 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001704 | 550676 | 554 | 994 | CR-S13-02 | Crossroads | 2026-05-19 | 14 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001705 | 492030 | 495 | 994 | CR-S23-03 | Crossroads | 2026-05-19 | 14 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001706 | 540600 | 1275 | 424 | HB-S06-01 | Harbor | 2026-05-19 | 14 | Vegetation | Substation breaker | Major event | May 2026 wind event
OE-26-001707 | 724661 | 643 | 1127 | PR-S19-05 | Prairie | 2026-05-19 | 14 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001708 | 45120 | 160 | 282 | CR-S28-03 | Crossroads | 2026-05-19 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001709 | 51603 | 167 | 309 | HB-S09-01 | Harbor | 2026-05-19 | 14 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001710 | 914592 | 672 | 1361 | PR-S03-02 | Prairie | 2026-05-19 | 14 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001711 | 5453 | 19 | 287 | HB-S06-04 | Harbor | 2026-05-19 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001712 | 598748 | 724 | 827 | BY-S19-04 | Bayou | 2026-05-19 | 14 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001713 | 1027180 | 1276 | 805 | BY-S30-01 | Bayou | 2026-05-19 | 14 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001714 | 121660 | 77 | 1580 | PR-S07-02 | Prairie | 2026-05-19 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001715 | 42196 | 154 | 274 | PR-S01-01 | Prairie | 2026-05-19 | 14 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001716 | 18304 | 26 | 704 | CR-S07-06 | Crossroads | 2026-05-19 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001717 | 1282032 | 1842 | 696 | BY-S05-02 | Bayou | 2026-05-19 | 14 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001718 | 1247002 | 842 | 1481 | BY-S17-01 | Bayou | 2026-05-19 | 14 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001719 | 383724 | 594 | 646 | CR-S25-04 | Crossroads | 2026-05-19 | 14 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001720 | 918090 | 909 | 1010 | BY-S12-03 | Bayou | 2026-05-19 | 14 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001721 | 274533 | 769 | 357 | HB-S20-01 | Harbor | 2026-05-19 | 14 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001722 | 198598 | 218 | 911 | PR-S01-03 | Prairie | 2026-05-19 | 14 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001723 | 1181754 | 747 | 1582 | PR-S14-04 | Prairie | 2026-05-19 | 14 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001724 | 473760 | 630 | 752 | BY-S03-01 | Bayou | 2026-05-19 | 14 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001725 | 330264 | 1251 | 264 | HB-S05-01 | Harbor | 2026-05-19 | 14 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001726 | 82308 | 76 | 1083 | CR-S04-04 | Crossroads | 2026-05-19 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001727 | 48276 | 108 | 447 | BY-S16-01 | Bayou | 2026-05-19 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001728 | 611387 | 1169 | 523 | BY-S26-05 | Bayou | 2026-05-19 | 14 | Vegetation | Substation breaker | Major event | May 2026 wind event
OE-26-001729 | 102268 | 74 | 1382 | PR-S16-01 | Prairie | 2026-05-19 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001730 | 193920 | 480 | 404 | PR-S20-03 | Prairie | 2026-05-19 | 14 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001731 | 4065 | 15 | 271 | PR-S03-01 | Prairie | 2026-05-19 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001732 | 2018124 | 919 | 2196 | BY-S29-03 | Bayou | 2026-05-19 | 14 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001733 | 122388 | 217 | 564 | CR-S02-02 | Crossroads | 2026-05-19 | 15 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001734 | 2059 | 29 | 71 | CR-S25-03 | Crossroads | 2026-05-19 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-001735 | 395444 | 812 | 487 | PR-S02-03 | Prairie | 2026-05-19 | 15 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001736 | 47124 | 51 | 924 | BY-S05-03 | Bayou | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001737 | 142631 | 107 | 1333 | BY-S18-07 | Bayou | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001738 | 33128 | 82 | 404 | CR-S09-05 | Crossroads | 2026-05-19 | 15 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001739 | 142096 | 214 | 664 | PR-S04-03 | Prairie | 2026-05-19 | 15 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001740 | 160506 | 241 | 666 | PR-S14-03 | Prairie | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001741 | 60358 | 206 | 293 | CR-S23-01 | Crossroads | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001742 | 183600 | 216 | 850 | PR-S11-02 | Prairie | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001743 | 240018 | 367 | 654 | PR-S04-01 | Prairie | 2026-05-19 | 15 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001744 | 260568 | 264 | 987 | PR-S03-06 | Prairie | 2026-05-19 | 15 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001745 | 22824 | 72 | 317 | PR-S18-05 | Prairie | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001746 | 34944 | 56 | 624 | BY-S24-05 | Bayou | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001747 | 1786967 | 949 | 1883 | BY-S10-04 | Bayou | 2026-05-19 | 15 | Vegetation | Substation breaker | Major event | May 2026 wind event
OE-26-001748 | 3276925 | 1025 | 3197 | PR-S09-03 | Prairie | 2026-05-19 | 15 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001749 | 42966 | 77 | 558 | HB-S07-05 | Harbor | 2026-05-19 | 15 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001750 | 783666 | 1182 | 663 | BY-S25-01 | Bayou | 2026-05-19 | 15 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001751 | 2623016 | 902 | 2908 | PR-S19-01 | Prairie | 2026-05-19 | 15 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001752 | 123082 | 38 | 3239 | BY-S25-04 | Bayou | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001753 | 482672 | 311 | 1552 | BY-S28-01 | Bayou | 2026-05-19 | 15 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001754 | 110229 | 87 | 1267 | PR-S07-03 | Prairie | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001755 | 181192 | 284 | 638 | CR-S29-02 | Crossroads | 2026-05-19 | 15 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001756 | 367092 | 1133 | 324 | HB-S13-02 | Harbor | 2026-05-19 | 15 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001757 | 301350 | 175 | 1722 | CR-S25-05 | Crossroads | 2026-05-19 | 15 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001758 | 1862976 | 1878 | 992 | BY-S16-06 | Bayou | 2026-05-19 | 15 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001759 | 135552 | 128 | 1059 | PR-S19-04 | Prairie | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001760 | 43168 | 32 | 1349 | BY-S27-06 | Bayou | 2026-05-19 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001761 | 113076 | 324 | 349 | PR-S14-01 | Prairie | 2026-05-19 | 15 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001762 | 64349 | 281 | 229 | PR-S06-02 | Prairie | 2026-05-19 | 15 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001763 | 724416 | 1056 | 686 | CR-S15-01 | Crossroads | 2026-05-19 | 15 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001764 | 441595 | 385 | 1147 | BY-S24-02 | Bayou | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001765 | 2440 | 20 | 122 | CR-S16-05 | Crossroads | 2026-05-19 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001766 | 113526 | 106 | 1071 | PR-S20-04 | Prairie | 2026-05-19 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001767 | 126824 | 166 | 764 | PR-S13-05 | Prairie | 2026-05-19 | 16 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001768 | 207552 | 138 | 1504 | PR-S17-01 | Prairie | 2026-05-19 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001769 | 16856 | 43 | 392 | PR-S18-04 | Prairie | 2026-05-19 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001770 | 1149600 | 1916 | 600 | PR-S08-01 | Prairie | 2026-05-19 | 16 | Vegetation | Substation breaker | Major event | May 2026 wind event
OE-26-001771 | 72380 | 70 | 1034 | PR-S15-02 | Prairie | 2026-05-19 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001772 | 101920 | 56 | 1820 | BY-S12-04 | Bayou | 2026-05-19 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001773 | 452427 | 631 | 717 | PR-S06-03 | Prairie | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001774 | 38837 | 71 | 547 | CR-S16-04 | Crossroads | 2026-05-19 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001775 | 136398 | 127 | 1074 | PR-S18-06 | Prairie | 2026-05-19 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001776 | 681849 | 1233 | 553 | BY-S04-01 | Bayou | 2026-05-19 | 16 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001777 | 1368752 | 847 | 1616 | PR-S07-05 | Prairie | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001778 | 344322 | 423 | 814 | PR-S20-01 | Prairie | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001779 | 1465068 | 1009 | 1452 | PR-S01-06 | Prairie | 2026-05-19 | 16 | Vegetation | Substation breaker | Major event | May 2026 wind event
OE-26-001780 | 28782 | 82 | 351 | CR-S13-05 | Crossroads | 2026-05-19 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001781 | 1667922 | 1074 | 1553 | BY-S29-02 | Bayou | 2026-05-19 | 16 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001782 | 1352877 | 697 | 1941 | BY-S28-03 | Bayou | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001783 | 103232 | 64 | 1613 | CR-S09-02 | Crossroads | 2026-05-19 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001784 | 569114 | 826 | 689 | PR-S07-01 | Prairie | 2026-05-19 | 16 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001785 | 84420 | 70 | 1206 | PR-S16-04 | Prairie | 2026-05-19 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001786 | 677206 | 1186 | 571 | BY-S09-04 | Bayou | 2026-05-19 | 16 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001787 | 1273978 | 878 | 1451 | BY-S23-02 | Bayou | 2026-05-19 | 16 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001788 | 138744 | 492 | 282 | HB-S20-05 | Harbor | 2026-05-19 | 16 | Vegetation | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001789 | 2522144 | 2152 | 1172 | BY-S08-01 | Bayou | 2026-05-19 | 16 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001790 | 512413 | 407 | 1259 | BY-S09-01 | Bayou | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001791 | 15747 | 29 | 543 | CR-S30-05 | Crossroads | 2026-05-19 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001792 | 79473 | 59 | 1347 | CR-S30-01 | Crossroads | 2026-05-19 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001793 | 96152 | 136 | 707 | PR-S01-04 | Prairie | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001794 | 33843 | 87 | 389 | BY-S07-02 | Bayou | 2026-05-19 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001795 | 1028425 | 1327 | 775 | PR-S10-03 | Prairie | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001796 | 842898 | 658 | 1281 | PR-S16-03 | Prairie | 2026-05-19 | 16 | Vegetation | Substation breaker | Major event | May 2026 wind event
OE-26-001797 | 61215 | 55 | 1113 | PR-S10-02 | Prairie | 2026-05-19 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001798 | 586752 | 1024 | 573 | BY-S28-02 | Bayou | 2026-05-19 | 16 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001799 | 100956 | 716 | 141 | BY-S29-05 | Bayou | 2026-05-19 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-001800 | 138348 | 63 | 2196 | PR-S05-01 | Prairie | 2026-05-19 | 17 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001801 | 126940 | 577 | 220 | BY-S24-03 | Bayou | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001802 | 252884 | 382 | 662 | PR-S05-03 | Prairie | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001803 | 290752 | 176 | 1652 | PR-S13-04 | Prairie | 2026-05-19 | 17 | Weather - wind | IGSD-isolated section | Major event | May 2026 wind event
OE-26-001804 | 1529440 | 1210 | 1264 | BY-S24-01 | Bayou | 2026-05-19 | 17 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001805 | 202794 | 463 | 438 | CR-S32-04 | Crossroads | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001806 | 621526 | 1369 | 454 | BY-S11-01 | Bayou | 2026-05-19 | 17 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001807 | 2265906 | 906 | 2501 | PR-S06-01 | Prairie | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001808 | 865444 | 818 | 1058 | CR-S07-02 | Crossroads | 2026-05-19 | 17 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001809 | 1478457 | 549 | 2693 | CR-S01-03 | Crossroads | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001810 | 881160 | 1049 | 840 | CR-S18-05 | Crossroads | 2026-05-19 | 17 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001811 | 18090 | 27 | 670 | BY-S09-02 | Bayou | 2026-05-19 | 17 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001812 | 135908 | 244 | 557 | BY-S27-04 | Bayou | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001813 | 414756 | 843 | 492 | HB-S05-05 | Harbor | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001814 | 572286 | 1794 | 319 | CR-S22-03 | Crossroads | 2026-05-19 | 17 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001815 | 1816146 | 619 | 2934 | BY-S06-03 | Bayou | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001816 | 1377324 | 972 | 1417 | BY-S25-02 | Bayou | 2026-05-19 | 17 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001817 | 1253331 | 887 | 1413 | PR-S08-03 | Prairie | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001818 | 5214954 | 2494 | 2091 | BY-S14-01 | Bayou | 2026-05-19 | 17 | Weather - wind | Substation breaker | Major event | May 2026 wind event
OE-26-001819 | 251258 | 274 | 917 | BY-S27-03 | Bayou | 2026-05-19 | 17 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001820 | 588960 | 818 | 720 | PR-S20-02 | Prairie | 2026-05-19 | 17 | Vegetation | Substation breaker | Major event | May 2026 wind event
OE-26-001821 | 30422 | 82 | 371 | BY-S07-03 | Bayou | 2026-05-19 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001822 | 84366 | 86 | 981 | BY-S26-06 | Bayou | 2026-05-19 | 17 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001823 | 102700 | 158 | 650 | BY-S22-03 | Bayou | 2026-05-19 | 17 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001824 | 40824 | 36 | 1134 | BY-S17-02 | Bayou | 2026-05-19 | 17 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001825 | 1137600 | 1185 | 960 | CR-S22-01 | Crossroads | 2026-05-19 | 17 | Vegetation | Feeder recloser | Major event | May 2026 wind event
OE-26-001826 | 98875 | 113 | 875 | CR-S07-03 | Crossroads | 2026-05-19 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001827 | 843922 | 829 | 1018 | CR-S09-03 | Crossroads | 2026-05-19 | 17 | Weather - wind | Feeder recloser | Major event | May 2026 wind event
OE-26-001828 | 33124 | 91 | 364 | CR-S17-01 | Crossroads | 2026-05-19 | 18 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001829 | 100738 | 241 | 418 | PR-S04-03 | Prairie | 2026-05-19 | 18 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001830 | 14632 | 59 | 248 | HB-S10-02 | Harbor | 2026-05-19 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001831 | 161604 | 268 | 603 | CR-S08-01 | Crossroads | 2026-05-19 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001832 | 19910 | 55 | 362 | PR-S01-03 | Prairie | 2026-05-19 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001833 | 12772 | 62 | 206 | BY-S16-04 | Bayou | 2026-05-19 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001834 | 32863 | 59 | 557 | BY-S07-05 | Bayou | 2026-05-19 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001835 | 10353 | 17 | 609 | HB-S12-02 | Harbor | 2026-05-19 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001836 | 109281 | 219 | 499 | BY-S13-03 | Bayou | 2026-05-19 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001837 | 55488 | 96 | 578 | BY-S12-01 | Bayou | 2026-05-19 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001838 | 36378 | 129 | 282 | PR-S07-01 | Prairie | 2026-05-19 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001839 | 52875 | 125 | 423 | PR-S20-04 | Prairie | 2026-05-19 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001840 | 43230 | 110 | 393 | PR-S01-03 | Prairie | 2026-05-19 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001841 | 11764 | 68 | 173 | PR-S04-01 | Prairie | 2026-05-19 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001842 | 19558 | 127 | 154 | BY-S27-04 | Bayou | 2026-05-19 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001843 | 14490 | 70 | 207 | HB-S13-01 | Harbor | 2026-05-19 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001844 | 32791 | 121 | 271 | PR-S03-05 | Prairie | 2026-05-19 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001845 | 31863 | 129 | 247 | CR-S18-05 | Crossroads | 2026-05-19 | 20 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001846 | 158466 | 147 | 1078 | BY-S18-07 | Bayou | 2026-05-19 | 20 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001847 | 178875 | 375 | 477 | HB-S12-01 | Harbor | 2026-05-19 | 20 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001848 | 61950 | 295 | 210 | BY-S09-05 | Bayou | 2026-05-19 | 20 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001849 | 4788 | 18 | 266 | BY-S25-04 | Bayou | 2026-05-19 | 20 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001850 | 6825 | 35 | 195 | PR-S12-03 | Prairie | 2026-05-19 | 20 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001851 | 5280 | 44 | 120 | PR-S15-06 | Prairie | 2026-05-19 | 20 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001852 | 23560 | 95 | 248 | BY-S18-03 | Bayou | 2026-05-19 | 20 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001853 | 14761 | 29 | 509 | BY-S29-02 | Bayou | 2026-05-19 | 21 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001854 | 77226 | 122 | 633 | BY-S15-02 | Bayou | 2026-05-19 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001855 | 3672 | 18 | 204 | PR-S14-02 | Prairie | 2026-05-19 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001856 | 29891 | 71 | 421 | HB-S07-05 | Harbor | 2026-05-19 | 21 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001857 | 15300 | 102 | 150 | PR-S09-04 | Prairie | 2026-05-19 | 21 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001858 | 5292 | 49 | 108 | CR-S18-06 | Crossroads | 2026-05-19 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001859 | 2954 | 14 | 211 | CR-S25-03 | Crossroads | 2026-05-19 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-26-001860 | 67980 | 206 | 330 | CR-S07-02 | Crossroads | 2026-05-19 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001861 | 27048 | 42 | 644 | CR-S32-02 | Crossroads | 2026-05-19 | 22 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001862 | 14060 | 74 | 190 | PR-S16-05 | Prairie | 2026-05-19 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001863 | 11616 | 66 | 176 | BY-S25-02 | Bayou | 2026-05-19 | 22 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001864 | 50196 | 141 | 356 | PR-S14-04 | Prairie | 2026-05-19 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001865 | 40968 | 72 | 569 | BY-S25-02 | Bayou | 2026-05-19 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001866 | 16380 | 70 | 234 | BY-S21-04 | Bayou | 2026-05-19 | 23 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001867 | 16309 | 47 | 347 | CR-S01-03 | Crossroads | 2026-05-19 | 23 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001868 | 9576 | 72 | 133 | CR-S23-05 | Crossroads | 2026-05-19 | 23 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001869 | 5658 | 41 | 138 | PR-S18-06 | Prairie | 2026-05-19 | 23 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001870 | 74807 | 313 | 239 | PR-S08-03 | Prairie | 2026-05-19 | 23 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001871 | 21609 | 147 | 147 | PR-S18-01 | Prairie | 2026-05-19 | 23 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001872 | 44540 | 131 | 340 | BY-S21-04 | Bayou | 2026-05-19 | 23 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001873 | 46904 | 143 | 328 | HB-S20-01 | Harbor | 2026-05-19 | 23 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001874 | 60480 | 105 | 576 | PR-S02-01 | Prairie | 2026-05-20 | 0 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001875 | 32076 | 81 | 396 | PR-S04-03 | Prairie | 2026-05-20 | 0 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001876 | 7725 | 75 | 103 | CR-S21-02 | Crossroads | 2026-05-20 | 0 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001877 | 17710 | 35 | 506 | BY-S13-02 | Bayou | 2026-05-20 | 0 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001878 | 42804 | 82 | 522 | PR-S01-05 | Prairie | 2026-05-20 | 0 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001879 | 51980 | 115 | 452 | CR-S03-02 | Crossroads | 2026-05-20 | 0 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001880 | 17850 | 35 | 510 | HB-S01-05 | Harbor | 2026-05-20 | 0 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001881 | 51450 | 70 | 735 | BY-S21-05 | Bayou | 2026-05-20 | 0 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001882 | 104706 | 126 | 831 | BY-S23-05 | Bayou | 2026-05-20 | 0 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001883 | 6390 | 90 | 71 | BY-S10-05 | Bayou | 2026-05-20 | 0 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001884 | 4980 | 30 | 166 | BY-S19-04 | Bayou | 2026-05-20 | 0 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001885 | 69222 | 83 | 834 | CR-S13-03 | Crossroads | 2026-05-20 | 0 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001886 | 23715 | 153 | 155 | CR-S06-01 | Crossroads | 2026-05-20 | 1 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001887 | 164580 | 195 | 844 | PR-S15-05 | Prairie | 2026-05-20 | 1 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001888 | 47082 | 59 | 798 | PR-S01-02 | Prairie | 2026-05-20 | 1 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001889 | 28764 | 102 | 282 | BY-S21-03 | Bayou | 2026-05-20 | 1 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001890 | 52712 | 88 | 599 | BY-S27-01 | Bayou | 2026-05-20 | 1 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001891 | 32976 | 48 | 687 | PR-S05-03 | Prairie | 2026-05-20 | 1 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001892 | 31980 | 60 | 533 | PR-S08-03 | Prairie | 2026-05-20 | 1 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001893 | 52381 | 49 | 1069 | PR-S13-01 | Prairie | 2026-05-20 | 1 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001894 | 391500 | 450 | 870 | BY-S22-02 | Bayou | 2026-05-20 | 1 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001895 | 101835 | 279 | 365 | HB-S07-05 | Harbor | 2026-05-20 | 1 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001896 | 41140 | 170 | 242 | CR-S27-03 | Crossroads | 2026-05-20 | 1 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001897 | 24852 | 109 | 228 | PR-S03-02 | Prairie | 2026-05-20 | 2 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001898 | 15444 | 117 | 132 | PR-S14-02 | Prairie | 2026-05-20 | 2 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001899 | 47498 | 127 | 374 | BY-S24-02 | Bayou | 2026-05-20 | 2 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001900 | 32065 | 53 | 605 | PR-S02-01 | Prairie | 2026-05-20 | 2 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001901 | 46138 | 59 | 782 | PR-S16-04 | Prairie | 2026-05-20 | 2 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001902 | 11426 | 29 | 394 | BY-S07-06 | Bayou | 2026-05-20 | 2 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001903 | 19817 | 149 | 133 | BY-S23-05 | Bayou | 2026-05-20 | 2 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001904 | 95205 | 165 | 577 | HB-S02-02 | Harbor | 2026-05-20 | 2 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001905 | 129312 | 96 | 1347 | BY-S13-06 | Bayou | 2026-05-20 | 2 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001906 | 93482 | 86 | 1087 | BY-S22-03 | Bayou | 2026-05-20 | 2 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001907 | 44640 | 40 | 1116 | BY-S08-03 | Bayou | 2026-05-20 | 2 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001908 | 46464 | 1408 | 33 | CR-S19-02 | Crossroads | 2026-05-20 | 3 | Equipment - overhead | Substation breaker | Forced | None
OE-26-001909 | 124187 | 157 | 791 | BY-S07-06 | Bayou | 2026-05-20 | 3 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001910 | 20557 | 61 | 337 | BY-S05-02 | Bayou | 2026-05-20 | 3 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001911 | 52136 | 152 | 343 | CR-S12-01 | Crossroads | 2026-05-20 | 3 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001912 | 12464 | 82 | 152 | PR-S10-02 | Prairie | 2026-05-20 | 3 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001913 | 20482 | 98 | 209 | BY-S07-03 | Bayou | 2026-05-20 | 3 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001914 | 55660 | 110 | 506 | PR-S09-04 | Prairie | 2026-05-20 | 3 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001915 | 17980 | 58 | 310 | PR-S07-03 | Prairie | 2026-05-20 | 3 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001916 | 31228 | 74 | 422 | CR-S07-07 | Crossroads | 2026-05-20 | 3 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001917 | 51188 | 191 | 268 | BY-S05-02 | Bayou | 2026-05-20 | 3 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001918 | 44758 | 139 | 322 | CR-S20-04 | Crossroads | 2026-05-20 | 4 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001919 | 82485 | 195 | 423 | PR-S03-02 | Prairie | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001920 | 4268 | 44 | 97 | CR-S15-03 | Crossroads | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001921 | 63923 | 97 | 659 | BY-S10-02 | Bayou | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001922 | 16269 | 29 | 561 | PR-S20-03 | Prairie | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001923 | 57590 | 65 | 886 | BY-S16-04 | Bayou | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001924 | 15354 | 18 | 853 | BY-S12-03 | Bayou | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001925 | 11194 | 58 | 193 | HB-S06-03 | Harbor | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001926 | 91317 | 183 | 499 | BY-S12-02 | Bayou | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001927 | 26052 | 78 | 334 | PR-S18-02 | Prairie | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001928 | 44233 | 71 | 623 | BY-S07-04 | Bayou | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001929 | 53400 | 75 | 712 | BY-S24-01 | Bayou | 2026-05-20 | 4 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001930 | 41400 | 138 | 300 | PR-S19-03 | Prairie | 2026-05-20 | 5 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001931 | 8200 | 40 | 205 | PR-S04-02 | Prairie | 2026-05-20 | 5 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001932 | 106666 | 266 | 401 | CR-S04-05 | Crossroads | 2026-05-20 | 5 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001933 | 83600 | 220 | 380 | BY-S10-03 | Bayou | 2026-05-20 | 5 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001934 | 78406 | 197 | 398 | BY-S05-03 | Bayou | 2026-05-20 | 5 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001935 | 24535 | 35 | 701 | PR-S01-03 | Prairie | 2026-05-20 | 5 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001936 | 30420 | 65 | 468 | PR-S03-05 | Prairie | 2026-05-20 | 5 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001937 | 10780 | 35 | 308 | HB-S05-02 | Harbor | 2026-05-20 | 5 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001938 | 61803 | 189 | 327 | CR-S28-04 | Crossroads | 2026-05-20 | 5 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001939 | 54530 | 205 | 266 | HB-S17-03 | Harbor | 2026-05-20 | 5 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001940 | 36000 | 72 | 500 | BY-S17-03 | Bayou | 2026-05-20 | 6 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001941 | 34822 | 46 | 757 | BY-S10-04 | Bayou | 2026-05-20 | 6 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001942 | 13048 | 28 | 466 | BY-S10-03 | Bayou | 2026-05-20 | 6 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001943 | 44145 | 81 | 545 | BY-S15-02 | Bayou | 2026-05-20 | 6 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001944 | 91805 | 301 | 305 | CR-S01-04 | Crossroads | 2026-05-20 | 6 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001945 | 88305 | 145 | 609 | PR-S09-01 | Prairie | 2026-05-20 | 6 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001946 | 60379 | 121 | 499 | BY-S10-04 | Bayou | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001947 | 26969 | 149 | 181 | BY-S19-03 | Bayou | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001948 | 16254 | 86 | 189 | PR-S07-06 | Prairie | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001949 | 16926 | 42 | 403 | PR-S03-01 | Prairie | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001950 | 65472 | 192 | 341 | HB-S07-05 | Harbor | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001951 | 31824 | 72 | 442 | BY-S25-02 | Bayou | 2026-05-20 | 7 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001952 | 22626 | 54 | 419 | BY-S22-03 | Bayou | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001953 | 3880 | 10 | 388 | BY-S29-02 | Bayou | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001954 | 220052 | 271 | 812 | PR-S02-03 | Prairie | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001955 | 68200 | 248 | 275 | HB-S05-06 | Harbor | 2026-05-20 | 7 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001956 | 2475 | 11 | 225 | BY-S17-01 | Bayou | 2026-05-20 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001957 | 6156 | 81 | 76 | CR-S04-05 | Crossroads | 2026-05-20 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-001958 | 22646 | 134 | 169 | HB-S03-02 | Harbor | 2026-05-20 | 8 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001959 | 10816 | 52 | 208 | CR-S05-02 | Crossroads | 2026-05-20 | 8 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001960 | 15174 | 54 | 281 | PR-S09-02 | Prairie | 2026-05-20 | 8 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001961 | 65995 | 335 | 197 | BY-S24-03 | Bayou | 2026-05-20 | 8 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001962 | 3774 | 51 | 74 | BY-S04-01 | Bayou | 2026-05-20 | 8 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001963 | 18810 | 55 | 342 | BY-S24-02 | Bayou | 2026-05-20 | 8 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001964 | 82315 | 163 | 505 | CR-S09-02 | Crossroads | 2026-05-20 | 8 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001965 | 16456 | 68 | 242 | PR-S15-03 | Prairie | 2026-05-20 | 8 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001966 | 13515 | 85 | 159 | CR-S06-01 | Crossroads | 2026-05-20 | 8 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001967 | 2255 | 11 | 205 | BY-S10-04 | Bayou | 2026-05-20 | 9 | Unknown | Transformer fuse | Forced | None
OE-26-001968 | 9310 | 35 | 266 | PR-S16-05 | Prairie | 2026-05-20 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-001969 | 90288 | 418 | 216 | BY-S26-03 | Bayou | 2026-05-20 | 9 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001970 | 141733 | 271 | 523 | BY-S09-01 | Bayou | 2026-05-20 | 9 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001971 | 31428 | 108 | 291 | CR-S08-03 | Crossroads | 2026-05-20 | 9 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001972 | 75888 | 248 | 306 | BY-S30-03 | Bayou | 2026-05-20 | 9 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001973 | 27048 | 84 | 322 | HB-S18-02 | Harbor | 2026-05-20 | 9 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001974 | 14427 | 63 | 229 | CR-S19-04 | Crossroads | 2026-05-20 | 9 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001975 | 145537 | 119 | 1223 | HB-S07-03 | Harbor | 2026-05-20 | 9 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001976 | 1752 | 12 | 146 | CR-S21-02 | Crossroads | 2026-05-20 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-001977 | 220410 | 186 | 1185 | BY-S07-01 | Bayou | 2026-05-20 | 10 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001978 | 17928 | 54 | 332 | CR-S17-03 | Crossroads | 2026-05-20 | 10 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001979 | 94800 | 395 | 240 | PR-S01-05 | Prairie | 2026-05-20 | 10 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001980 | 294574 | 397 | 742 | BY-S22-03 | Bayou | 2026-05-20 | 10 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001981 | 175338 | 153 | 1146 | BY-S27-01 | Bayou | 2026-05-20 | 10 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001982 | 31892 | 119 | 268 | PR-S15-03 | Prairie | 2026-05-20 | 10 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001983 | 3735 | 15 | 249 | BY-S04-02 | Bayou | 2026-05-20 | 10 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001984 | 20468 | 68 | 301 | PR-S05-01 | Prairie | 2026-05-20 | 10 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001985 | 27559 | 31 | 889 | BY-S03-01 | Bayou | 2026-05-20 | 10 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001986 | 54395 | 115 | 473 | PR-S08-01 | Prairie | 2026-05-20 | 10 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001987 | 61540 | 68 | 905 | BY-S12-03 | Bayou | 2026-05-20 | 10 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001988 | 33282 | 129 | 258 | PR-S09-02 | Prairie | 2026-05-20 | 10 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001989 | 9996 | 42 | 238 | BY-S14-01 | Bayou | 2026-05-20 | 10 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001990 | 43263 | 99 | 437 | BY-S05-02 | Bayou | 2026-05-20 | 11 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001991 | 18921 | 119 | 159 | BY-S22-04 | Bayou | 2026-05-20 | 11 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001992 | 22960 | 80 | 287 | HB-S03-03 | Harbor | 2026-05-20 | 11 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001993 | 103783 | 67 | 1549 | BY-S20-01 | Bayou | 2026-05-20 | 11 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001994 | 29450 | 190 | 155 | HB-S18-02 | Harbor | 2026-05-20 | 11 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001995 | 83980 | 190 | 442 | CR-S27-04 | Crossroads | 2026-05-20 | 11 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-001996 | 124684 | 292 | 427 | BY-S20-03 | Bayou | 2026-05-20 | 11 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001997 | 66096 | 243 | 272 | PR-S03-04 | Prairie | 2026-05-20 | 11 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001998 | 7227 | 73 | 99 | CR-S16-03 | Crossroads | 2026-05-20 | 11 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-001999 | 32940 | 180 | 183 | PR-S15-04 | Prairie | 2026-05-20 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002000 | 7381 | 61 | 121 | BY-S17-04 | Bayou | 2026-05-20 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002001 | 13920 | 60 | 232 | BY-S05-01 | Bayou | 2026-05-20 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002002 | 31702 | 131 | 242 | BY-S11-03 | Bayou | 2026-05-20 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002003 | 39600 | 150 | 264 | BY-S25-01 | Bayou | 2026-05-20 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002004 | 35757 | 87 | 411 | CR-S02-02 | Crossroads | 2026-05-20 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002005 | 23746 | 62 | 383 | HB-S16-05 | Harbor | 2026-05-20 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002006 | 50440 | 65 | 776 | CR-S08-02 | Crossroads | 2026-05-20 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002007 | 42300 | 100 | 423 | CR-S08-05 | Crossroads | 2026-05-20 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002008 | 56924 | 107 | 532 | BY-S12-02 | Bayou | 2026-05-20 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002009 | 11050 | 50 | 221 | BY-S04-01 | Bayou | 2026-05-20 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002010 | 13440 | 32 | 420 | PR-S04-01 | Prairie | 2026-05-20 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002011 | 9424 | 62 | 152 | PR-S09-01 | Prairie | 2026-05-20 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002012 | 65394 | 173 | 378 | CR-S22-01 | Crossroads | 2026-05-20 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002013 | 12084 | 76 | 159 | CR-S26-06 | Crossroads | 2026-05-20 | 12 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002014 | 120572 | 172 | 701 | CR-S27-02 | Crossroads | 2026-05-20 | 12 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002015 | 4921 | 37 | 133 | CR-S01-03 | Crossroads | 2026-05-20 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-002016 | 10624 | 83 | 128 | CR-S30-04 | Crossroads | 2026-05-20 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002017 | 40936 | 43 | 952 | BY-S08-03 | Bayou | 2026-05-20 | 13 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002018 | 39078 | 117 | 334 | BY-S15-03 | Bayou | 2026-05-20 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002019 | 49126 | 154 | 319 | BY-S06-03 | Bayou | 2026-05-20 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002020 | 21504 | 42 | 512 | BY-S18-06 | Bayou | 2026-05-20 | 13 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002021 | 35690 | 83 | 430 | PR-S09-01 | Prairie | 2026-05-20 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002022 | 58290 | 290 | 201 | PR-S12-01 | Prairie | 2026-05-20 | 13 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002023 | 11651 | 61 | 191 | PR-S06-02 | Prairie | 2026-05-20 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002024 | 82950 | 175 | 474 | PR-S19-04 | Prairie | 2026-05-20 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002025 | 55892 | 178 | 314 | PR-S11-02 | Prairie | 2026-05-20 | 13 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002026 | 19296 | 36 | 536 | PR-S01-06 | Prairie | 2026-05-20 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002027 | 24904 | 44 | 566 | PR-S09-01 | Prairie | 2026-05-20 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002028 | 54340 | 143 | 380 | PR-S14-01 | Prairie | 2026-05-20 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002029 | 26471 | 103 | 257 | BY-S08-01 | Bayou | 2026-05-20 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002030 | 94563 | 171 | 553 | BY-S08-03 | Bayou | 2026-05-20 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002031 | 35640 | 88 | 405 | PR-S07-05 | Prairie | 2026-05-20 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002032 | 406000 | 700 | 580 | BY-S15-03 | Bayou | 2026-05-20 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002033 | 80290 | 155 | 518 | PR-S07-01 | Prairie | 2026-05-20 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002034 | 50661 | 117 | 433 | PR-S13-03 | Prairie | 2026-05-20 | 14 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002035 | 60930 | 90 | 677 | BY-S01-01 | Bayou | 2026-05-20 | 14 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002036 | 149 | 1 | 149 | CR-S02-02 | Crossroads | 2026-05-20 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002037 | 5656 | 28 | 202 | HB-S02-01 | Harbor | 2026-05-20 | 15 | Unknown | Lateral fuse | Forced | None
OE-26-002038 | 211519 | 287 | 737 | PR-S13-04 | Prairie | 2026-05-20 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002039 | 46010 | 107 | 430 | PR-S06-01 | Prairie | 2026-05-20 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002040 | 30050 | 50 | 601 | BY-S04-03 | Bayou | 2026-05-20 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002041 | 33448 | 148 | 226 | CR-S16-01 | Crossroads | 2026-05-20 | 15 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002042 | 77418 | 198 | 391 | BY-S28-03 | Bayou | 2026-05-20 | 15 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002043 | 170968 | 172 | 994 | BY-S29-05 | Bayou | 2026-05-20 | 15 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002044 | 217699 | 293 | 743 | PR-S12-03 | Prairie | 2026-05-20 | 15 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002045 | 63720 | 60 | 1062 | HB-S09-02 | Harbor | 2026-05-20 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002046 | 14806 | 22 | 673 | HB-S17-01 | Harbor | 2026-05-20 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002047 | 31020 | 66 | 470 | CR-S18-06 | Crossroads | 2026-05-20 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002048 | 10908 | 54 | 202 | BY-S15-03 | Bayou | 2026-05-20 | 16 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002049 | 107856 | 252 | 428 | PR-S19-04 | Prairie | 2026-05-20 | 16 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002050 | 1435 | 7 | 205 | BY-S25-04 | Bayou | 2026-05-20 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002051 | 980 | 10 | 98 | HB-S20-04 | Harbor | 2026-05-20 | 17 | Unknown | Transformer fuse | Forced | None
OE-26-002052 | 76626 | 473 | 162 | PR-S16-04 | Prairie | 2026-05-20 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002053 | 221260 | 185 | 1196 | PR-S03-04 | Prairie | 2026-05-20 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002054 | 27307 | 83 | 329 | BY-S08-03 | Bayou | 2026-05-20 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002055 | 16388 | 68 | 241 | BY-S05-02 | Bayou | 2026-05-20 | 17 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002056 | 16008 | 116 | 138 | HB-S02-01 | Harbor | 2026-05-20 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002057 | 56173 | 149 | 377 | BY-S29-03 | Bayou | 2026-05-20 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002058 | 62510 | 133 | 470 | HB-S16-05 | Harbor | 2026-05-20 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002059 | 25488 | 144 | 177 | BY-S09-05 | Bayou | 2026-05-20 | 17 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002060 | 8432 | 34 | 248 | BY-S27-02 | Bayou | 2026-05-20 | 17 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002061 | 945 | 9 | 105 | HB-S20-02 | Harbor | 2026-05-20 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-002062 | 770 | 7 | 110 | PR-S03-01 | Prairie | 2026-05-20 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002063 | 9870 | 30 | 329 | HB-S04-02 | Harbor | 2026-05-20 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002064 | 10746 | 54 | 199 | PR-S07-01 | Prairie | 2026-05-20 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002065 | 32100 | 100 | 321 | BY-S15-03 | Bayou | 2026-05-20 | 18 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002066 | 85932 | 217 | 396 | BY-S16-03 | Bayou | 2026-05-20 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002067 | 22545 | 167 | 135 | PR-S07-02 | Prairie | 2026-05-20 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002068 | 209152 | 152 | 1376 | HB-S08-05 | Harbor | 2026-05-20 | 18 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002069 | 6132 | 28 | 219 | BY-S21-01 | Bayou | 2026-05-20 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002070 | 37151 | 97 | 383 | PR-S10-03 | Prairie | 2026-05-20 | 18 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002071 | 83049 | 93 | 893 | BY-S12-02 | Bayou | 2026-05-20 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002072 | 37008 | 144 | 257 | BY-S29-01 | Bayou | 2026-05-20 | 18 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002073 | 25296 | 34 | 744 | BY-S07-03 | Bayou | 2026-05-20 | 18 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002074 | 44370 | 174 | 255 | PR-S19-05 | Prairie | 2026-05-20 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002075 | 37673 | 101 | 373 | CR-S07-03 | Crossroads | 2026-05-20 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002076 | 11172 | 76 | 147 | BY-S13-06 | Bayou | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002077 | 13725 | 61 | 225 | CR-S04-05 | Crossroads | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002078 | 41760 | 96 | 435 | HB-S09-04 | Harbor | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002079 | 94472 | 392 | 241 | BY-S07-05 | Bayou | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002080 | 8520 | 60 | 142 | PR-S08-03 | Prairie | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002081 | 7140 | 51 | 140 | CR-S18-02 | Crossroads | 2026-05-20 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002082 | 47684 | 131 | 364 | CR-S26-04 | Crossroads | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002083 | 19525 | 71 | 275 | CR-S20-01 | Crossroads | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002084 | 26970 | 58 | 465 | PR-S20-02 | Prairie | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002085 | 76000 | 95 | 800 | PR-S20-04 | Prairie | 2026-05-20 | 19 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002086 | 24908 | 52 | 479 | CR-S21-03 | Crossroads | 2026-05-20 | 19 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002087 | 31560 | 120 | 263 | CR-S15-01 | Crossroads | 2026-05-20 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002088 | 127500 | 204 | 625 | CR-S03-02 | Crossroads | 2026-05-20 | 20 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002089 | 206403 | 321 | 643 | BY-S15-04 | Bayou | 2026-05-20 | 20 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002090 | 14820 | 38 | 390 | BY-S28-02 | Bayou | 2026-05-20 | 20 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002091 | 7965 | 135 | 59 | HB-S02-01 | Harbor | 2026-05-20 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002092 | 50318 | 181 | 278 | BY-S01-02 | Bayou | 2026-05-20 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002093 | 69750 | 279 | 250 | CR-S22-03 | Crossroads | 2026-05-20 | 21 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002094 | 41658 | 53 | 786 | PR-S16-01 | Prairie | 2026-05-20 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002095 | 22400 | 80 | 280 | CR-S02-04 | Crossroads | 2026-05-20 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002096 | 19754 | 83 | 238 | BY-S26-05 | Bayou | 2026-05-20 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002097 | 12348 | 28 | 441 | PR-S06-03 | Prairie | 2026-05-20 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002098 | 3828 | 44 | 87 | PR-S08-03 | Prairie | 2026-05-20 | 21 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002099 | 104104 | 169 | 616 | CR-S30-03 | Crossroads | 2026-05-20 | 21 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002100 | 55522 | 142 | 391 | BY-S27-01 | Bayou | 2026-05-20 | 22 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002101 | 18923 | 127 | 149 | PR-S15-01 | Prairie | 2026-05-20 | 22 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002102 | 9964 | 47 | 212 | BY-S28-03 | Bayou | 2026-05-20 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002103 | 35760 | 60 | 596 | BY-S25-03 | Bayou | 2026-05-20 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002104 | 99280 | 146 | 680 | PR-S05-02 | Prairie | 2026-05-20 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002105 | 145188 | 222 | 654 | CR-S24-03 | Crossroads | 2026-05-20 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002106 | 47458 | 122 | 389 | BY-S06-01 | Bayou | 2026-05-20 | 22 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002107 | 77644 | 188 | 413 | BY-S18-03 | Bayou | 2026-05-20 | 23 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002108 | 49896 | 81 | 616 | BY-S20-03 | Bayou | 2026-05-20 | 23 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002109 | 15895 | 55 | 289 | BY-S22-02 | Bayou | 2026-05-20 | 23 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002110 | 9805 | 53 | 185 | CR-S12-02 | Crossroads | 2026-05-20 | 23 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002111 | 21996 | 36 | 611 | BY-S19-04 | Bayou | 2026-05-20 | 23 | Vegetation | Lateral fuse | Major event | May 2026 wind event
OE-26-002112 | 87058 | 158 | 551 | BY-S17-01 | Bayou | 2026-05-20 | 23 | Weather - wind | Lateral fuse | Major event | May 2026 wind event
OE-26-002113 | 2088 | 24 | 87 | BY-S10-05 | Bayou | 2026-05-21 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002114 | 6816 | 48 | 142 | CR-S02-05 | Crossroads | 2026-05-21 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002115 | 2704 | 13 | 208 | BY-S30-01 | Bayou | 2026-05-21 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-002116 | 6572 | 62 | 106 | PR-S16-05 | Prairie | 2026-05-21 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002117 | 5474 | 34 | 161 | BY-S18-03 | Bayou | 2026-05-21 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002118 | 27537 | 201 | 137 | CR-S20-02 | Crossroads | 2026-05-21 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002119 | 15120 | 72 | 210 | BY-S16-04 | Bayou | 2026-05-21 | 18 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002120 | 1199 | 11 | 109 | CR-S22-03 | Crossroads | 2026-05-21 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002121 | 280 | 4 | 70 | CR-S09-03 | Crossroads | 2026-05-21 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002122 | 31457 | 379 | 83 | BY-S23-02 | Bayou | 2026-05-22 | 0 | Vegetation | Lateral fuse | Forced | None
OE-26-002123 | 760 | 10 | 76 | BY-S21-03 | Bayou | 2026-05-22 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-002124 | 1960 | 14 | 140 | CR-S28-04 | Crossroads | 2026-05-22 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002125 | 3120 | 10 | 312 | BY-S19-02 | Bayou | 2026-05-22 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002126 | 752 | 8 | 94 | PR-S01-04 | Prairie | 2026-05-22 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-26-002127 | 1953 | 9 | 217 | PR-S11-03 | Prairie | 2026-05-22 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-002128 | 10780 | 70 | 154 | BY-S12-02 | Bayou | 2026-05-22 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002129 | 630 | 6 | 105 | CR-S24-01 | Crossroads | 2026-05-22 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002130 | 215 | 1 | 215 | CR-S26-02 | Crossroads | 2026-05-22 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002131 | 2439 | 9 | 271 | PR-S20-03 | Prairie | 2026-05-22 | 16 | Animal | Transformer fuse | Forced | None
OE-26-002132 | 1620 | 18 | 90 | CR-S29-03 | Crossroads | 2026-05-22 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002133 | 2475 | 11 | 225 | CR-S32-04 | Crossroads | 2026-05-22 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-002134 | 38582 | 191 | 202 | BY-S18-03 | Bayou | 2026-05-22 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-26-002135 | 2352 | 12 | 196 | BY-S27-03 | Bayou | 2026-05-22 | 20 | Animal | Transformer fuse | Forced | None
OE-26-002136 | 19440 | 180 | 108 | PR-S13-05 | Prairie | 2026-05-22 | 21 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002137 | 56980 | 770 | 74 | HB-S07-04 | Harbor | 2026-05-22 | 22 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002138 | 16605 | 135 | 123 | PR-S13-03 | Prairie | 2026-05-22 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002139 | 23250 | 375 | 62 | CR-S16-06 | Crossroads | 2026-05-23 | 0 | Weather - lightning | Feeder recloser | Forced | None
OE-26-002140 | 480 | 4 | 120 | BY-S26-03 | Bayou | 2026-05-23 | 4 | Vegetation | Transformer fuse | Forced | None
OE-26-002141 | 241560 | 3960 | 61 | CR-S21-03 | Crossroads | 2026-05-23 | 7 | Unknown | Substation breaker | Outside cause | None
OE-26-002142 | 22712 | 68 | 334 | HB-S16-03 | Harbor | 2026-05-23 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002143 | 34076 | 1217 | 28 | BY-S14-02 | Bayou | 2026-05-23 | 10 | Vegetation | Substation breaker | Forced | None
OE-26-002144 | 70967 | 1339 | 53 | CR-S26-06 | Crossroads | 2026-05-23 | 11 | Equipment - underground | Substation breaker | Forced | None
OE-26-002145 | 666 | 3 | 222 | BY-S28-03 | Bayou | 2026-05-23 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-002146 | 22134 | 217 | 102 | CR-S11-02 | Crossroads | 2026-05-23 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002147 | 1980 | 6 | 330 | PR-S07-04 | Prairie | 2026-05-23 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-002148 | 660 | 3 | 220 | CR-S26-04 | Crossroads | 2026-05-23 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002149 | 1638 | 14 | 117 | PR-S09-04 | Prairie | 2026-05-23 | 13 | Animal | Transformer fuse | Forced | None
OE-26-002150 | 1155 | 7 | 165 | BY-S20-03 | Bayou | 2026-05-23 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002151 | 1222 | 13 | 94 | PR-S03-05 | Prairie | 2026-05-23 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002152 | 95 | 1 | 95 | BY-S04-03 | Bayou | 2026-05-23 | 15 | Animal | Transformer fuse | Forced | None
OE-26-002153 | 642 | 3 | 214 | BY-S16-06 | Bayou | 2026-05-23 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-002154 | 712 | 8 | 89 | BY-S08-02 | Bayou | 2026-05-23 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002155 | 411 | 3 | 137 | BY-S22-03 | Bayou | 2026-05-23 | 20 | Animal | Transformer fuse | Forced | None
OE-26-002156 | 158 | 2 | 79 | CR-S18-01 | Crossroads | 2026-05-24 | 1 | Weather - wind | Transformer fuse | Forced | None
OE-26-002157 | 1245 | 5 | 249 | CR-S22-04 | Crossroads | 2026-05-24 | 6 | Animal | Transformer fuse | Forced | None
OE-26-002158 | 30535 | 197 | 155 | PR-S02-02 | Prairie | 2026-05-24 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002159 | 54280 | 590 | 92 | CR-S30-06 | Crossroads | 2026-05-24 | 11 | Weather - wind | Feeder recloser | Forced | None
OE-26-002160 | 92736 | 1449 | 64 | CR-S19-02 | Crossroads | 2026-05-24 | 12 | Equipment - underground | Substation breaker | Forced | None
OE-26-002161 | 280 | 2 | 140 | HB-S07-05 | Harbor | 2026-05-24 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002162 | 266 | 2 | 133 | PR-S02-02 | Prairie | 2026-05-24 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002163 | 9108 | 132 | 69 | CR-S02-03 | Crossroads | 2026-05-24 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002164 | 522 | 9 | 58 | HB-S08-01 | Harbor | 2026-05-24 | 16 | Unknown | Transformer fuse | Forced | None
OE-26-002165 | 4635 | 45 | 103 | CR-S26-02 | Crossroads | 2026-05-24 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002166 | 65280 | 1088 | 60 | HB-S05-01 | Harbor | 2026-05-24 | 17 | Weather - lightning | Feeder recloser | Forced | None
OE-26-002167 | 552 | 12 | 46 | HB-S17-01 | Harbor | 2026-05-24 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-002168 | 21243 | 219 | 97 | CR-S16-05 | Crossroads | 2026-05-24 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002169 | 5824 | 14 | 416 | CR-S25-01 | Crossroads | 2026-05-24 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002170 | 23478 | 602 | 39 | HB-S18-02 | Harbor | 2026-05-24 | 18 | Weather - wind | Feeder recloser | Forced | None
OE-26-002171 | 14105 | 91 | 155 | BY-S15-01 | Bayou | 2026-05-24 | 21 | Weather - wind | Lateral fuse | Forced | None
OE-26-002172 | 223 | 1 | 223 | PR-S03-06 | Prairie | 2026-05-24 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002173 | 2928 | 12 | 244 | BY-S13-02 | Bayou | 2026-05-25 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-002174 | 860 | 4 | 215 | HB-S14-01 | Harbor | 2026-05-25 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002175 | 10890 | 363 | 30 | CR-S18-02 | Crossroads | 2026-05-25 | 7 | Vegetation | IGSD-isolated section | Forced | None
OE-26-002176 | 8930 | 95 | 94 | HB-S15-01 | Harbor | 2026-05-25 | 7 | Animal | Lateral fuse | Forced | None
OE-26-002177 | 4424 | 14 | 316 | BY-S26-04 | Bayou | 2026-05-25 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002178 | 3510 | 27 | 130 | CR-S04-05 | Crossroads | 2026-05-25 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002179 | 2698 | 38 | 71 | BY-S13-03 | Bayou | 2026-05-25 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002180 | 45416 | 811 | 56 | CR-S08-02 | Crossroads | 2026-05-25 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002181 | 3800 | 40 | 95 | PR-S01-03 | Prairie | 2026-05-25 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-26-002182 | 1584 | 11 | 144 | CR-S31-01 | Crossroads | 2026-05-25 | 15 | Unknown | Transformer fuse | Forced | None
OE-26-002183 | 632 | 4 | 158 | PR-S18-04 | Prairie | 2026-05-25 | 18 | Animal | Transformer fuse | Forced | None
OE-26-002184 | 846 | 6 | 141 | CR-S02-05 | Crossroads | 2026-05-26 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002185 | 22800 | 285 | 80 | BY-S03-03 | Bayou | 2026-05-26 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-26-002186 | 3108 | 21 | 148 | HB-S06-05 | Harbor | 2026-05-26 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002187 | 549 | 9 | 61 | CR-S18-01 | Crossroads | 2026-05-26 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002188 | 1312 | 8 | 164 | BY-S15-06 | Bayou | 2026-05-26 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002189 | 20099 | 199 | 101 | HB-S03-02 | Harbor | 2026-05-26 | 11 | Animal | Lateral fuse | Forced | None
OE-26-002190 | 8949 | 57 | 157 | BY-S13-04 | Bayou | 2026-05-26 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-002191 | 816 | 8 | 102 | BY-S24-04 | Bayou | 2026-05-26 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002192 | 840 | 28 | 30 | HB-S07-02 | Harbor | 2026-05-26 | 13 | Animal | Lateral fuse | Forced | None
OE-26-002193 | 1932 | 14 | 138 | BY-S01-02 | Bayou | 2026-05-26 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002194 | 5795 | 61 | 95 | CR-S26-01 | Crossroads | 2026-05-26 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002195 | 2702 | 14 | 193 | HB-S02-01 | Harbor | 2026-05-26 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-26-002196 | 1780 | 5 | 356 | PR-S15-06 | Prairie | 2026-05-26 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002197 | 32387 | 233 | 139 | PR-S07-01 | Prairie | 2026-05-26 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-002198 | 125851 | 673 | 187 | PR-S02-02 | Prairie | 2026-05-26 | 18 | Animal | Feeder recloser | Forced | None
OE-26-002199 | 1788 | 12 | 149 | BY-S23-03 | Bayou | 2026-05-26 | 19 | Animal | Transformer fuse | Forced | None
OE-26-002200 | 1952 | 8 | 244 | BY-S11-01 | Bayou | 2026-05-26 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-002201 | 4920 | 30 | 164 | CR-S30-05 | Crossroads | 2026-05-27 | 5 | Animal | Lateral fuse | Forced | None
OE-26-002202 | 217500 | 1250 | 174 | PR-S01-03 | Prairie | 2026-05-27 | 5 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002203 | 1595 | 29 | 55 | BY-S05-01 | Bayou | 2026-05-27 | 6 | Animal | Lateral fuse | Forced | None
OE-26-002204 | 5632 | 44 | 128 | BY-S25-03 | Bayou | 2026-05-27 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002205 | 7956 | 36 | 221 | CR-S17-02 | Crossroads | 2026-05-27 | 7 | Animal | Lateral fuse | Forced | None
OE-26-002206 | 205 | 1 | 205 | PR-S03-01 | Prairie | 2026-05-27 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002207 | 938 | 7 | 134 | CR-S09-04 | Crossroads | 2026-05-27 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002208 | 2736 | 19 | 144 | CR-S07-03 | Crossroads | 2026-05-27 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002209 | 2587 | 13 | 199 | BY-S18-01 | Bayou | 2026-05-27 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002210 | 664 | 4 | 166 | CR-S10-01 | Crossroads | 2026-05-27 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-002211 | 1778 | 7 | 254 | HB-S14-01 | Harbor | 2026-05-27 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002212 | 42642 | 309 | 138 | BY-S10-05 | Bayou | 2026-05-27 | 19 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-002213 | 1040 | 13 | 80 | CR-S16-01 | Crossroads | 2026-05-27 | 21 | Animal | Transformer fuse | Forced | None
OE-26-002214 | 816 | 8 | 102 | CR-S21-02 | Crossroads | 2026-05-28 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002215 | 41624 | 968 | 43 | PR-S11-01 | Prairie | 2026-05-28 | 1 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-002216 | 12900 | 75 | 172 | CR-S23-01 | Crossroads | 2026-05-28 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002217 | 6525 | 45 | 145 | BY-S18-05 | Bayou | 2026-05-28 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002218 | 16224 | 104 | 156 | CR-S02-01 | Crossroads | 2026-05-28 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002219 | 1485 | 11 | 135 | CR-S22-02 | Crossroads | 2026-05-28 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002220 | 732 | 6 | 122 | CR-S26-05 | Crossroads | 2026-05-28 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002221 | 150024 | 1128 | 133 | HB-S16-01 | Harbor | 2026-05-28 | 9 | Unknown | Feeder recloser | Forced | None
OE-26-002222 | 44872 | 568 | 79 | BY-S09-02 | Bayou | 2026-05-28 | 13 | Weather - wind | Feeder recloser | Forced | None
OE-26-002223 | 2670 | 10 | 267 | PR-S03-06 | Prairie | 2026-05-28 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002224 | 155540 | 2222 | 70 | PR-S17-01 | Prairie | 2026-05-28 | 14 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002225 | 3060 | 10 | 306 | BY-S09-04 | Bayou | 2026-05-28 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002226 | 2850 | 30 | 95 | HB-S01-02 | Harbor | 2026-05-28 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002227 | 1278 | 9 | 142 | CR-S12-01 | Crossroads | 2026-05-28 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002228 | 954 | 9 | 106 | PR-S19-02 | Prairie | 2026-05-28 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002229 | 8281 | 49 | 169 | PR-S18-01 | Prairie | 2026-05-29 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002230 | 9504 | 132 | 72 | CR-S08-04 | Crossroads | 2026-05-29 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002231 | 40439 | 763 | 53 | CR-S10-03 | Crossroads | 2026-05-29 | 10 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002232 | 20970 | 90 | 233 | HB-S20-05 | Harbor | 2026-05-29 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002233 | 21700 | 62 | 350 | CR-S30-04 | Crossroads | 2026-05-29 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002234 | 2132 | 13 | 164 | HB-S04-02 | Harbor | 2026-05-29 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002235 | 35931 | 609 | 59 | HB-S11-01 | Harbor | 2026-05-29 | 17 | Vegetation | Feeder recloser | Forced | None
OE-26-002236 | 272 | 1 | 272 | PR-S14-04 | Prairie | 2026-05-29 | 18 | Animal | Transformer fuse | Forced | None
OE-26-002237 | 1131 | 13 | 87 | CR-S20-03 | Crossroads | 2026-05-29 | 22 | Vegetation | Transformer fuse | Forced | None
OE-26-002238 | 1860 | 12 | 155 | BY-S03-02 | Bayou | 2026-05-30 | 4 | Unknown | Transformer fuse | Forced | None
OE-26-002239 | 33950 | 175 | 194 | PR-S01-01 | Prairie | 2026-05-30 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002240 | 7210 | 35 | 206 | CR-S02-03 | Crossroads | 2026-05-30 | 11 | Weather - wind | Lateral fuse | Forced | None
OE-26-002241 | 20536 | 136 | 151 | CR-S04-03 | Crossroads | 2026-05-30 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002242 | 12649 | 139 | 91 | CR-S22-01 | Crossroads | 2026-05-30 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002243 | 226055 | 1559 | 145 | BY-S26-03 | Bayou | 2026-05-30 | 13 | Vegetation | Substation breaker | Forced | None
OE-26-002244 | 2727 | 9 | 303 | HB-S10-03 | Harbor | 2026-05-30 | 13 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002245 | 825 | 5 | 165 | PR-S09-03 | Prairie | 2026-05-30 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002246 | 6732 | 68 | 99 | CR-S28-02 | Crossroads | 2026-05-30 | 15 | Unknown | Lateral fuse | Forced | None
OE-26-002247 | 1053 | 13 | 81 | HB-S20-02 | Harbor | 2026-05-30 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-002248 | 1140 | 10 | 114 | PR-S13-03 | Prairie | 2026-05-30 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002249 | 2482 | 34 | 73 | PR-S14-02 | Prairie | 2026-05-30 | 15 | Animal | Lateral fuse | Forced | None
OE-26-002250 | 68442 | 671 | 102 | BY-S25-04 | Bayou | 2026-05-30 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002251 | 1330 | 10 | 133 | CR-S26-05 | Crossroads | 2026-05-30 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002252 | 3311 | 7 | 473 | CR-S31-01 | Crossroads | 2026-05-30 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002253 | 930 | 6 | 155 | BY-S07-01 | Bayou | 2026-05-30 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002254 | 171288 | 549 | 312 | HB-S03-03 | Harbor | 2026-05-30 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002255 | 29735 | 313 | 95 | CR-S09-04 | Crossroads | 2026-05-30 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-26-002256 | 17526 | 127 | 138 | BY-S27-04 | Bayou | 2026-05-30 | 22 | Unknown | Lateral fuse | Forced | None
OE-26-002257 | 2176 | 8 | 272 | HB-S20-04 | Harbor | 2026-05-30 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002258 | 1572 | 6 | 262 | PR-S08-02 | Prairie | 2026-05-31 | 6 | Animal | Transformer fuse | Forced | None
OE-26-002259 | 16564 | 101 | 164 | PR-S01-02 | Prairie | 2026-05-31 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002260 | 3782 | 61 | 62 | PR-S04-01 | Prairie | 2026-05-31 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-002261 | 1310 | 10 | 131 | PR-S15-06 | Prairie | 2026-05-31 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002262 | 1456 | 7 | 208 | PR-S16-05 | Prairie | 2026-05-31 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002263 | 2982 | 14 | 213 | BY-S22-03 | Bayou | 2026-05-31 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002264 | 5184 | 64 | 81 | CR-S01-04 | Crossroads | 2026-05-31 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002265 | 1692 | 9 | 188 | BY-S04-01 | Bayou | 2026-05-31 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-002266 | 93649 | 1319 | 71 | PR-S17-01 | Prairie | 2026-05-31 | 22 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002267 | 3206 | 14 | 229 | PR-S17-02 | Prairie | 2026-05-31 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002268 | 1312 | 8 | 164 | BY-S12-01 | Bayou | 2026-05-31 | 23 | Animal | Transformer fuse | Forced | None
OE-26-002269 | 2534 | 14 | 181 | BY-S19-04 | Bayou | 2026-05-31 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-002270 | 2544 | 24 | 106 | PR-S03-06 | Prairie | 2026-06-01 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002271 | 15012 | 54 | 278 | CR-S29-02 | Crossroads | 2026-06-01 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002272 | 7920 | 36 | 220 | CR-S09-05 | Crossroads | 2026-06-01 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002273 | 19159 | 161 | 119 | CR-S14-01 | Crossroads | 2026-06-01 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-002274 | 3315 | 13 | 255 | HB-S08-05 | Harbor | 2026-06-01 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002275 | 46500 | 372 | 125 | BY-S24-04 | Bayou | 2026-06-01 | 16 | Vegetation | IGSD-isolated section | Forced | None
OE-26-002276 | 3042 | 18 | 169 | PR-S06-02 | Prairie | 2026-06-01 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002277 | 1915 | 5 | 383 | HB-S17-02 | Harbor | 2026-06-01 | 17 | Animal | Transformer fuse | Forced | None
OE-26-002278 | 1704 | 12 | 142 | BY-S03-03 | Bayou | 2026-06-01 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-002279 | 462 | 2 | 231 | PR-S02-02 | Prairie | 2026-06-01 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-002280 | 10106 | 163 | 62 | BY-S23-01 | Bayou | 2026-06-01 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002281 | 32508 | 126 | 258 | BY-S06-02 | Bayou | 2026-06-02 | 5 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002282 | 4320 | 54 | 80 | CR-S22-04 | Crossroads | 2026-06-02 | 6 | Weather - wind | Lateral fuse | Forced | None
OE-26-002283 | 12376 | 91 | 136 | BY-S20-01 | Bayou | 2026-06-02 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-002284 | 3813 | 41 | 93 | BY-S15-05 | Bayou | 2026-06-02 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002285 | 13912 | 74 | 188 | CR-S30-07 | Crossroads | 2026-06-02 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002286 | 31447 | 767 | 41 | BY-S11-03 | Bayou | 2026-06-02 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002287 | 294 | 2 | 147 | PR-S14-04 | Prairie | 2026-06-02 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-002288 | 2580 | 12 | 215 | HB-S02-03 | Harbor | 2026-06-02 | 14 | Animal | Transformer fuse | Forced | None
OE-26-002289 | 708 | 4 | 177 | PR-S20-01 | Prairie | 2026-06-02 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002290 | 1155 | 7 | 165 | CR-S05-06 | Crossroads | 2026-06-03 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002291 | 38190 | 201 | 190 | HB-S10-03 | Harbor | 2026-06-03 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002292 | 39680 | 620 | 64 | CR-S10-03 | Crossroads | 2026-06-03 | 3 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002293 | 42160 | 620 | 68 | PR-S15-06 | Prairie | 2026-06-03 | 5 | Animal | Lateral fuse | Forced | None
OE-26-002294 | 2061 | 9 | 229 | BY-S30-02 | Bayou | 2026-06-03 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-002295 | 6705 | 45 | 149 | PR-S06-01 | Prairie | 2026-06-03 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002296 | 218 | 2 | 109 | CR-S21-03 | Crossroads | 2026-06-03 | 10 | Animal | Transformer fuse | Forced | None
OE-26-002297 | 117952 | 1216 | 97 | HB-S02-01 | Harbor | 2026-06-03 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-002298 | 332 | 1 | 332 | CR-S12-02 | Crossroads | 2026-06-03 | 13 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002299 | 43439 | 359 | 121 | BY-S09-05 | Bayou | 2026-06-03 | 14 | Vegetation | Feeder recloser | Forced | None
OE-26-002300 | 53682 | 1167 | 46 | BY-S17-04 | Bayou | 2026-06-03 | 14 | Weather - lightning | Feeder recloser | Forced | None
OE-26-002301 | 2400 | 15 | 160 | BY-S18-06 | Bayou | 2026-06-03 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002302 | 935 | 11 | 85 | HB-S07-05 | Harbor | 2026-06-03 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-002303 | 808 | 8 | 101 | PR-S10-03 | Prairie | 2026-06-03 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002304 | 2162 | 23 | 94 | BY-S17-02 | Bayou | 2026-06-03 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-26-002305 | 4800 | 40 | 120 | HB-S09-03 | Harbor | 2026-06-03 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002306 | 792 | 11 | 72 | PR-S14-04 | Prairie | 2026-06-03 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002307 | 124488 | 504 | 247 | CR-S04-05 | Crossroads | 2026-06-03 | 20 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002308 | 109626 | 906 | 121 | HB-S20-04 | Harbor | 2026-06-03 | 20 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002309 | 1572 | 12 | 131 | CR-S20-02 | Crossroads | 2026-06-03 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-002310 | 10965 | 215 | 51 | CR-S05-02 | Crossroads | 2026-06-04 | 2 | Animal | Lateral fuse | Forced | None
OE-26-002311 | 13950 | 50 | 279 | CR-S29-01 | Crossroads | 2026-06-04 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002312 | 21180 | 353 | 60 | CR-S04-05 | Crossroads | 2026-06-04 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002313 | 1152 | 9 | 128 | CR-S30-07 | Crossroads | 2026-06-04 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002314 | 5586 | 57 | 98 | HB-S08-01 | Harbor | 2026-06-04 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002315 | 3216 | 8 | 402 | BY-S16-02 | Bayou | 2026-06-04 | 10 | Animal | Transformer fuse | Forced | None
OE-26-002316 | 1848 | 33 | 56 | CR-S31-01 | Crossroads | 2026-06-04 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002317 | 6424 | 73 | 88 | CR-S03-03 | Crossroads | 2026-06-04 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002318 | 6966 | 54 | 129 | CR-S30-03 | Crossroads | 2026-06-04 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002319 | 13440 | 105 | 128 | HB-S02-03 | Harbor | 2026-06-04 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-002320 | 2128 | 28 | 76 | HB-S07-02 | Harbor | 2026-06-04 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002321 | 2990 | 46 | 65 | CR-S04-06 | Crossroads | 2026-06-04 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-002322 | 19434 | 123 | 158 | BY-S13-01 | Bayou | 2026-06-04 | 18 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002323 | 441 | 3 | 147 | HB-S11-03 | Harbor | 2026-06-04 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-002324 | 50856 | 652 | 78 | BY-S16-04 | Bayou | 2026-06-04 | 23 | Vegetation | Feeder recloser | Forced | None
OE-26-002325 | 890 | 10 | 89 | BY-S21-05 | Bayou | 2026-06-05 | 5 | Vegetation | Transformer fuse | Forced | None
OE-26-002326 | 90145 | 1639 | 55 | PR-S07-03 | Prairie | 2026-06-05 | 6 | Vegetation | Substation breaker | Forced | None
OE-26-002327 | 366 | 6 | 61 | HB-S20-04 | Harbor | 2026-06-05 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002328 | 8440 | 20 | 422 | PR-S08-02 | Prairie | 2026-06-05 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002329 | 2960 | 20 | 148 | PR-S19-03 | Prairie | 2026-06-05 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002330 | 2363 | 17 | 139 | CR-S12-03 | Crossroads | 2026-06-05 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002331 | 1752 | 8 | 219 | HB-S15-01 | Harbor | 2026-06-05 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002332 | 18126 | 114 | 159 | BY-S17-03 | Bayou | 2026-06-05 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-002333 | 13983 | 79 | 177 | HB-S06-01 | Harbor | 2026-06-05 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002334 | 756 | 3 | 252 | BY-S12-02 | Bayou | 2026-06-05 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-002335 | 1295 | 7 | 185 | CR-S14-04 | Crossroads | 2026-06-05 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-002336 | 102085 | 1201 | 85 | BY-S09-03 | Bayou | 2026-06-05 | 20 | Vehicle or public | Substation breaker | Forced | None
OE-26-002337 | 17856 | 124 | 144 | CR-S29-02 | Crossroads | 2026-06-05 | 22 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002338 | 988 | 13 | 76 | BY-S27-03 | Bayou | 2026-06-06 | 2 | Weather - wind | Transformer fuse | Forced | None
OE-26-002339 | 19158 | 206 | 93 | PR-S01-01 | Prairie | 2026-06-06 | 4 | Vegetation | Lateral fuse | Forced | None
OE-26-002340 | 936 | 4 | 234 | PR-S11-02 | Prairie | 2026-06-06 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002341 | 1028 | 4 | 257 | PR-S17-01 | Prairie | 2026-06-06 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-002342 | 718 | 2 | 359 | HB-S09-03 | Harbor | 2026-06-06 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002343 | 43512 | 588 | 74 | PR-S11-01 | Prairie | 2026-06-06 | 12 | Vehicle or public | Feeder recloser | Forced | None
OE-26-002344 | 16896 | 192 | 88 | BY-S06-01 | Bayou | 2026-06-06 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002345 | 11655 | 111 | 105 | CR-S18-04 | Crossroads | 2026-06-06 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002346 | 1915 | 5 | 383 | BY-S02-01 | Bayou | 2026-06-06 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-002347 | 700 | 5 | 140 | PR-S08-03 | Prairie | 2026-06-06 | 18 | Animal | Transformer fuse | Forced | None
OE-26-002348 | 2665 | 13 | 205 | CR-S19-02 | Crossroads | 2026-06-07 | 12 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002349 | 193 | 1 | 193 | BY-S09-05 | Bayou | 2026-06-07 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002350 | 790 | 10 | 79 | BY-S14-03 | Bayou | 2026-06-07 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002351 | 4000 | 20 | 200 | BY-S23-02 | Bayou | 2026-06-07 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-002352 | 78750 | 2250 | 35 | HB-S07-02 | Harbor | 2026-06-07 | 15 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002353 | 23490 | 405 | 58 | PR-S03-06 | Prairie | 2026-06-07 | 15 | Vehicle or public | Feeder recloser | Forced | None
OE-26-002354 | 980 | 10 | 98 | BY-S20-01 | Bayou | 2026-06-07 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002355 | 2480 | 10 | 248 | BY-S21-04 | Bayou | 2026-06-07 | 16 | Animal | Transformer fuse | Forced | None
OE-26-002356 | 945 | 9 | 105 | CR-S02-03 | Crossroads | 2026-06-07 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002357 | 2219 | 7 | 317 | CR-S15-03 | Crossroads | 2026-06-07 | 17 | Unknown | Transformer fuse | Forced | None
OE-26-002358 | 1780 | 5 | 356 | PR-S01-06 | Prairie | 2026-06-07 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002359 | 8379 | 63 | 133 | PR-S07-03 | Prairie | 2026-06-07 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002360 | 1190 | 5 | 238 | BY-S12-02 | Bayou | 2026-06-07 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002361 | 30080 | 470 | 64 | PR-S07-01 | Prairie | 2026-06-07 | 19 | Weather - lightning | Feeder recloser | Forced | None
OE-26-002362 | 31064 | 353 | 88 | BY-S18-07 | Bayou | 2026-06-07 | 20 | Vegetation | Feeder recloser | Forced | None
OE-26-002363 | 31320 | 360 | 87 | BY-S15-06 | Bayou | 2026-06-07 | 21 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002364 | 1267 | 7 | 181 | PR-S07-03 | Prairie | 2026-06-08 | 0 | Animal | Transformer fuse | Forced | None
OE-26-002365 | 814 | 11 | 74 | BY-S17-01 | Bayou | 2026-06-08 | 1 | Vegetation | Transformer fuse | Forced | None
OE-26-002366 | 11528 | 44 | 262 | HB-S01-03 | Harbor | 2026-06-08 | 1 | Vegetation | Lateral fuse | Forced | None
OE-26-002367 | 4992 | 13 | 384 | CR-S04-03 | Crossroads | 2026-06-08 | 2 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002368 | 15800 | 79 | 200 | BY-S16-03 | Bayou | 2026-06-08 | 5 | Vegetation | Lateral fuse | Forced | None
OE-26-002369 | 2538 | 94 | 27 | CR-S01-03 | Crossroads | 2026-06-08 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002370 | 2912 | 13 | 224 | BY-S22-03 | Bayou | 2026-06-08 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002371 | 869 | 11 | 79 | CR-S23-02 | Crossroads | 2026-06-08 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002372 | 122 | 1 | 122 | BY-S08-03 | Bayou | 2026-06-08 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-002373 | 9163 | 187 | 49 | CR-S08-02 | Crossroads | 2026-06-08 | 11 | Animal | Lateral fuse | Forced | None
OE-26-002374 | 992 | 8 | 124 | CR-S04-03 | Crossroads | 2026-06-08 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002375 | 126120 | 1051 | 120 | PR-S12-01 | Prairie | 2026-06-08 | 13 | Vegetation | Feeder recloser | Forced | None
OE-26-002376 | 558 | 6 | 93 | PR-S17-02 | Prairie | 2026-06-08 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002377 | 5124 | 14 | 366 | CR-S14-01 | Crossroads | 2026-06-08 | 15 | Animal | Transformer fuse | Forced | None
OE-26-002378 | 1000 | 5 | 200 | PR-S07-01 | Prairie | 2026-06-08 | 15 | Unknown | Transformer fuse | Forced | None
OE-26-002379 | 7896 | 84 | 94 | CR-S09-05 | Crossroads | 2026-06-08 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002380 | 970 | 5 | 194 | PR-S04-01 | Prairie | 2026-06-08 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002381 | 28222 | 206 | 137 | BY-S23-02 | Bayou | 2026-06-09 | 4 | Vegetation | Lateral fuse | Forced | None
OE-26-002382 | 63547 | 1199 | 53 | BY-S18-07 | Bayou | 2026-06-09 | 5 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-002383 | 22355 | 85 | 263 | BY-S27-04 | Bayou | 2026-06-09 | 7 | Vegetation | Lateral fuse | Forced | None
OE-26-002384 | 1998 | 18 | 111 | CR-S17-01 | Crossroads | 2026-06-09 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002385 | 202488 | 858 | 236 | PR-S04-01 | Prairie | 2026-06-09 | 8 | Weather - wind | Feeder recloser | Forced | None
OE-26-002386 | 2944 | 32 | 92 | PR-S18-05 | Prairie | 2026-06-09 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002387 | 8855 | 77 | 115 | CR-S30-03 | Crossroads | 2026-06-09 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002388 | 306 | 1 | 306 | BY-S27-05 | Bayou | 2026-06-09 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002389 | 9095 | 85 | 107 | CR-S13-02 | Crossroads | 2026-06-09 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002390 | 25917 | 163 | 159 | PR-S04-03 | Prairie | 2026-06-09 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002391 | 3024 | 14 | 216 | HB-S05-02 | Harbor | 2026-06-09 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002392 | 183700 | 3674 | 50 | HB-S09-02 | Harbor | 2026-06-09 | 13 | Animal | Substation breaker | Forced | None
OE-26-002393 | 2196 | 12 | 183 | PR-S15-02 | Prairie | 2026-06-09 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-002394 | 384 | 8 | 48 | CR-S07-04 | Crossroads | 2026-06-09 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002395 | 1176 | 7 | 168 | PR-S15-05 | Prairie | 2026-06-09 | 14 | Animal | Transformer fuse | Forced | None
OE-26-002396 | 2032 | 8 | 254 | CR-S15-03 | Crossroads | 2026-06-09 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002397 | 3596 | 58 | 62 | CR-S16-04 | Crossroads | 2026-06-09 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002398 | 106878 | 1137 | 94 | PR-S08-01 | Prairie | 2026-06-09 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-002399 | 71967 | 1043 | 69 | BY-S26-03 | Bayou | 2026-06-09 | 17 | Vegetation | Feeder recloser | Forced | None
OE-26-002400 | 5474 | 46 | 119 | PR-S08-02 | Prairie | 2026-06-09 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-002401 | 2899 | 13 | 223 | BY-S19-01 | Bayou | 2026-06-09 | 22 | Vegetation | Transformer fuse | Forced | None
OE-26-002402 | 15589 | 131 | 119 | HB-S01-01 | Harbor | 2026-06-10 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002403 | 2508 | 11 | 228 | PR-S12-02 | Prairie | 2026-06-10 | 2 | Vegetation | Transformer fuse | Forced | None
OE-26-002404 | 793 | 13 | 61 | CR-S06-02 | Crossroads | 2026-06-10 | 5 | Vegetation | Transformer fuse | Forced | None
OE-26-002405 | 50421 | 147 | 343 | PR-S17-02 | Prairie | 2026-06-10 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002406 | 1241 | 17 | 73 | CR-S12-03 | Crossroads | 2026-06-10 | 9 | Animal | Lateral fuse | Forced | None
OE-26-002407 | 1620 | 12 | 135 | CR-S25-01 | Crossroads | 2026-06-10 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-26-002408 | 3059 | 23 | 133 | HB-S13-01 | Harbor | 2026-06-10 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002409 | 20468 | 68 | 301 | BY-S05-01 | Bayou | 2026-06-10 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002410 | 696 | 12 | 58 | BY-S06-02 | Bayou | 2026-06-10 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002411 | 8721 | 51 | 171 | HB-S06-01 | Harbor | 2026-06-10 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002412 | 12675 | 65 | 195 | PR-S16-03 | Prairie | 2026-06-10 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002413 | 35000 | 175 | 200 | BY-S18-06 | Bayou | 2026-06-11 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002414 | 1485 | 5 | 297 | CR-S31-02 | Crossroads | 2026-06-11 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002415 | 6142 | 37 | 166 | PR-S09-02 | Prairie | 2026-06-11 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002416 | 2784 | 29 | 96 | PR-S11-01 | Prairie | 2026-06-11 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002417 | 420 | 2 | 210 | BY-S26-02 | Bayou | 2026-06-11 | 11 | Animal | Transformer fuse | Forced | None
OE-26-002418 | 129056 | 592 | 218 | HB-S04-02 | Harbor | 2026-06-11 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002419 | 16660 | 238 | 70 | PR-S03-04 | Prairie | 2026-06-11 | 12 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002420 | 3033 | 9 | 337 | HB-S20-03 | Harbor | 2026-06-11 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002421 | 6384 | 56 | 114 | BY-S05-03 | Bayou | 2026-06-11 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002422 | 812 | 7 | 116 | HB-S19-01 | Harbor | 2026-06-11 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-002423 | 65800 | 1175 | 56 | BY-S19-03 | Bayou | 2026-06-11 | 16 | Animal | Feeder recloser | Forced | None
OE-26-002424 | 2880 | 12 | 240 | CR-S30-01 | Crossroads | 2026-06-11 | 19 | Animal | Transformer fuse | Forced | None
OE-26-002425 | 22748 | 188 | 121 | HB-S02-02 | Harbor | 2026-06-11 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-002426 | 1640 | 8 | 205 | HB-S10-03 | Harbor | 2026-06-11 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-002427 | 29088 | 909 | 32 | BY-S10-02 | Bayou | 2026-06-12 | 4 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-002428 | 5796 | 14 | 414 | PR-S18-06 | Prairie | 2026-06-12 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002429 | 60300 | 1675 | 36 | CR-S20-02 | Crossroads | 2026-06-12 | 9 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002430 | 35358 | 142 | 249 | BY-S07-05 | Bayou | 2026-06-12 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-002431 | 4117 | 23 | 179 | PR-S02-02 | Prairie | 2026-06-12 | 12 | Animal | Lateral fuse | Forced | None
OE-26-002432 | 490 | 5 | 98 | BY-S29-01 | Bayou | 2026-06-12 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-002433 | 565 | 5 | 113 | PR-S04-02 | Prairie | 2026-06-12 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-002434 | 1640 | 10 | 164 | CR-S17-02 | Crossroads | 2026-06-12 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002435 | 12127 | 67 | 181 | PR-S07-03 | Prairie | 2026-06-12 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002436 | 1008 | 9 | 112 | BY-S13-01 | Bayou | 2026-06-12 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-002437 | 1496 | 11 | 136 | CR-S18-05 | Crossroads | 2026-06-12 | 16 | Animal | Transformer fuse | Forced | None
OE-26-002438 | 1053 | 9 | 117 | CR-S21-03 | Crossroads | 2026-06-12 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-002439 | 4020 | 134 | 30 | BY-S26-03 | Bayou | 2026-06-12 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-002440 | 2332 | 11 | 212 | PR-S09-01 | Prairie | 2026-06-12 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002441 | 70308 | 837 | 84 | PR-S20-02 | Prairie | 2026-06-12 | 18 | Weather - wind | Substation breaker | Forced | None
OE-26-002442 | 1750 | 10 | 175 | CR-S32-03 | Crossroads | 2026-06-12 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-26-002443 | 1554 | 14 | 111 | BY-S02-02 | Bayou | 2026-06-12 | 21 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002444 | 910 | 10 | 91 | CR-S27-03 | Crossroads | 2026-06-12 | 22 | Weather - wind | Lateral fuse | Forced | None
OE-26-002445 | 66220 | 308 | 215 | PR-S14-04 | Prairie | 2026-06-13 | 2 | Vegetation | Lateral fuse | Forced | None
OE-26-002446 | 1701 | 9 | 189 | PR-S19-01 | Prairie | 2026-06-13 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002447 | 3237 | 13 | 249 | PR-S20-03 | Prairie | 2026-06-13 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002448 | 35360 | 221 | 160 | HB-S17-01 | Harbor | 2026-06-13 | 8 | Weather - wind | Lateral fuse | Forced | None
OE-26-002449 | 14091 | 231 | 61 | CR-S05-05 | Crossroads | 2026-06-13 | 9 | Vegetation | Feeder recloser | Forced | None
OE-26-002450 | 20536 | 302 | 68 | PR-S16-01 | Prairie | 2026-06-13 | 9 | Weather - wind | Feeder recloser | Forced | None
OE-26-002451 | 436 | 2 | 218 | PR-S18-03 | Prairie | 2026-06-13 | 9 | Animal | Transformer fuse | Forced | None
OE-26-002452 | 245376 | 1728 | 142 | CR-S28-03 | Crossroads | 2026-06-13 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002453 | 954 | 6 | 159 | CR-S05-01 | Crossroads | 2026-06-13 | 12 | Animal | Transformer fuse | Forced | None
OE-26-002454 | 194 | 2 | 97 | BY-S07-03 | Bayou | 2026-06-13 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002455 | 3429 | 9 | 381 | HB-S06-04 | Harbor | 2026-06-13 | 14 | Unknown | Transformer fuse | Forced | None
OE-26-002456 | 33069 | 73 | 453 | HB-S05-05 | Harbor | 2026-06-13 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002457 | 194400 | 1440 | 135 | BY-S30-01 | Bayou | 2026-06-13 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002458 | 62510 | 658 | 95 | BY-S18-05 | Bayou | 2026-06-13 | 18 | Vegetation | Feeder recloser | Forced | None
OE-26-002459 | 93 | 1 | 93 | HB-S17-02 | Harbor | 2026-06-13 | 19 | Animal | Transformer fuse | Forced | None
OE-26-002460 | 12675 | 169 | 75 | PR-S16-05 | Prairie | 2026-06-14 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002461 | 1480 | 10 | 148 | HB-S12-02 | Harbor | 2026-06-14 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002462 | 610 | 5 | 122 | BY-S13-02 | Bayou | 2026-06-14 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-002463 | 496 | 2 | 248 | CR-S21-03 | Crossroads | 2026-06-14 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002464 | 616 | 2 | 308 | PR-S03-01 | Prairie | 2026-06-14 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002465 | 6018 | 59 | 102 | BY-S07-02 | Bayou | 2026-06-14 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-002466 | 1050 | 6 | 175 | BY-S29-03 | Bayou | 2026-06-14 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002467 | 56202 | 493 | 114 | HB-S07-04 | Harbor | 2026-06-14 | 10 | Vehicle or public | Feeder recloser | Forced | None
OE-26-002468 | 37526 | 647 | 58 | PR-S03-05 | Prairie | 2026-06-14 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002469 | 105846 | 1534 | 69 | BY-S25-04 | Bayou | 2026-06-14 | 11 | Vegetation | Substation breaker | Forced | None
OE-26-002470 | 67614 | 382 | 177 | CR-S18-01 | Crossroads | 2026-06-14 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002471 | 5655 | 65 | 87 | CR-S20-02 | Crossroads | 2026-06-14 | 14 | Animal | Lateral fuse | Forced | None
OE-26-002472 | 4760 | 40 | 119 | CR-S28-02 | Crossroads | 2026-06-14 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002473 | 13248 | 288 | 46 | CR-S04-04 | Crossroads | 2026-06-14 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002474 | 927 | 9 | 103 | CR-S07-07 | Crossroads | 2026-06-14 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002475 | 6664 | 136 | 49 | CR-S19-04 | Crossroads | 2026-06-14 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002476 | 104256 | 362 | 288 | PR-S12-02 | Prairie | 2026-06-14 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002477 | 1470 | 14 | 105 | CR-S04-03 | Crossroads | 2026-06-14 | 18 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002478 | 8008 | 44 | 182 | BY-S07-01 | Bayou | 2026-06-14 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002479 | 1980 | 9 | 220 | CR-S02-05 | Crossroads | 2026-06-14 | 20 | Unknown | Transformer fuse | Forced | None
OE-26-002480 | 2760 | 12 | 230 | CR-S08-01 | Crossroads | 2026-06-14 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-002481 | 101250 | 675 | 150 | PR-S07-02 | Prairie | 2026-06-14 | 21 | Vegetation | Feeder recloser | Forced | None
OE-26-002482 | 10000 | 100 | 100 | BY-S30-01 | Bayou | 2026-06-14 | 22 | Vegetation | Lateral fuse | Forced | None
OE-26-002483 | 630 | 6 | 105 | CR-S23-03 | Crossroads | 2026-06-14 | 23 | Animal | Transformer fuse | Forced | None
OE-26-002484 | 1690 | 5 | 338 | PR-S02-03 | Prairie | 2026-06-15 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002485 | 1708 | 14 | 122 | BY-S24-05 | Bayou | 2026-06-15 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-002486 | 2110 | 10 | 211 | BY-S16-05 | Bayou | 2026-06-15 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002487 | 2132 | 41 | 52 | PR-S02-02 | Prairie | 2026-06-15 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002488 | 3504 | 24 | 146 | PR-S06-01 | Prairie | 2026-06-15 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-002489 | 264 | 8 | 33 | CR-S26-03 | Crossroads | 2026-06-15 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002490 | 6517 | 49 | 133 | CR-S09-01 | Crossroads | 2026-06-15 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-002491 | 3924 | 12 | 327 | HB-S12-02 | Harbor | 2026-06-15 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-002492 | 24336 | 144 | 169 | PR-S19-01 | Prairie | 2026-06-15 | 18 | Weather - wind | Lateral fuse | Forced | None
OE-26-002493 | 32121 | 387 | 83 | CR-S25-05 | Crossroads | 2026-06-15 | 19 | Animal | Feeder recloser | Forced | None
OE-26-002494 | 34944 | 312 | 112 | PR-S18-06 | Prairie | 2026-06-15 | 19 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-002495 | 1635 | 15 | 109 | PR-S19-03 | Prairie | 2026-06-15 | 19 | Unknown | Lateral fuse | Forced | None
OE-26-002496 | 7676 | 76 | 101 | CR-S14-03 | Crossroads | 2026-06-15 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-26-002497 | 39491 | 101 | 391 | PR-S08-01 | Prairie | 2026-06-15 | 21 | Animal | Lateral fuse | Forced | None
OE-26-002498 | 98400 | 820 | 120 | BY-S03-02 | Bayou | 2026-06-16 | 1 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002499 | 12324 | 158 | 78 | HB-S20-04 | Harbor | 2026-06-16 | 1 | Vegetation | Lateral fuse | Forced | None
OE-26-002500 | 1496 | 11 | 136 | HB-S08-01 | Harbor | 2026-06-16 | 4 | Vegetation | Transformer fuse | Forced | None
OE-26-002501 | 5088 | 32 | 159 | CR-S14-05 | Crossroads | 2026-06-16 | 7 | Animal | Lateral fuse | Forced | None
OE-26-002502 | 34858 | 601 | 58 | BY-S18-05 | Bayou | 2026-06-16 | 10 | Weather - wind | Feeder recloser | Forced | None
OE-26-002503 | 8313 | 51 | 163 | CR-S07-06 | Crossroads | 2026-06-16 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002504 | 1547 | 7 | 221 | PR-S18-04 | Prairie | 2026-06-16 | 11 | Animal | Transformer fuse | Forced | None
OE-26-002505 | 2929 | 29 | 101 | CR-S16-03 | Crossroads | 2026-06-16 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002506 | 29029 | 203 | 143 | BY-S13-02 | Bayou | 2026-06-16 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-002507 | 102 | 1 | 102 | BY-S26-04 | Bayou | 2026-06-16 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-002508 | 464 | 8 | 58 | CR-S30-02 | Crossroads | 2026-06-16 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-26-002509 | 24589 | 67 | 367 | BY-S29-05 | Bayou | 2026-06-16 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-26-002510 | 253 | 1 | 253 | BY-S07-04 | Bayou | 2026-06-16 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002511 | 2013 | 11 | 183 | CR-S31-03 | Crossroads | 2026-06-17 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002512 | 1494 | 9 | 166 | BY-S16-01 | Bayou | 2026-06-17 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002513 | 7668 | 71 | 108 | HB-S19-01 | Harbor | 2026-06-17 | 7 | Vegetation | Lateral fuse | Forced | None
OE-26-002514 | 1807 | 13 | 139 | CR-S24-04 | Crossroads | 2026-06-17 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002515 | 7644 | 91 | 84 | CR-S10-03 | Crossroads | 2026-06-17 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-002516 | 15336 | 71 | 216 | PR-S18-01 | Prairie | 2026-06-17 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-002517 | 6141 | 69 | 89 | CR-S08-06 | Crossroads | 2026-06-17 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002518 | 3129 | 7 | 447 | PR-S01-02 | Prairie | 2026-06-17 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002519 | 2665 | 41 | 65 | PR-S13-03 | Prairie | 2026-06-17 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-002520 | 27156 | 372 | 73 | BY-S05-03 | Bayou | 2026-06-17 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-002521 | 16530 | 95 | 174 | BY-S03-01 | Bayou | 2026-06-17 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002522 | 15795 | 117 | 135 | PR-S10-03 | Prairie | 2026-06-17 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002523 | 3333 | 11 | 303 | HB-S09-04 | Harbor | 2026-06-17 | 16 | Animal | Transformer fuse | Forced | None
OE-26-002524 | 13916 | 284 | 49 | PR-S15-02 | Prairie | 2026-06-17 | 17 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-002525 | 123308 | 1063 | 116 | CR-S13-05 | Crossroads | 2026-06-17 | 19 | Vehicle or public | Feeder recloser | Forced | None
OE-26-002526 | 24304 | 196 | 124 | HB-S19-01 | Harbor | 2026-06-18 | 0 | Animal | IGSD-isolated section | Forced | None
OE-26-002527 | 1012 | 11 | 92 | HB-S14-02 | Harbor | 2026-06-18 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002528 | 1064 | 8 | 133 | BY-S15-06 | Bayou | 2026-06-18 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002529 | 2016 | 12 | 168 | BY-S29-05 | Bayou | 2026-06-18 | 7 | Weather - wind | Lateral fuse | Forced | None
OE-26-002530 | 2668 | 23 | 116 | BY-S07-02 | Bayou | 2026-06-18 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002531 | 5084 | 31 | 164 | HB-S18-01 | Harbor | 2026-06-18 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002532 | 1518 | 11 | 138 | PR-S01-01 | Prairie | 2026-06-18 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-002533 | 3618 | 54 | 67 | CR-S15-03 | Crossroads | 2026-06-18 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002534 | 7641 | 27 | 283 | HB-S18-02 | Harbor | 2026-06-18 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002535 | 84372 | 316 | 267 | BY-S29-05 | Bayou | 2026-06-18 | 11 | Animal | Lateral fuse | Forced | None
OE-26-002536 | 7904 | 52 | 152 | BY-S30-02 | Bayou | 2026-06-18 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-002537 | 5796 | 23 | 252 | BY-S11-02 | Bayou | 2026-06-18 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002538 | 19866 | 77 | 258 | BY-S26-01 | Bayou | 2026-06-18 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-002539 | 11972 | 82 | 146 | CR-S30-03 | Crossroads | 2026-06-18 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-002540 | 71820 | 684 | 105 | PR-S03-03 | Prairie | 2026-06-18 | 13 | Animal | Substation breaker | Forced | None
OE-26-002541 | 1260 | 10 | 126 | CR-S26-02 | Crossroads | 2026-06-18 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-26-002542 | 16758 | 126 | 133 | PR-S18-02 | Prairie | 2026-06-19 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002543 | 18145 | 95 | 191 | PR-S18-03 | Prairie | 2026-06-19 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002544 | 20276 | 74 | 274 | BY-S20-02 | Bayou | 2026-06-19 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-002545 | 4278 | 62 | 69 | CR-S06-01 | Crossroads | 2026-06-19 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002546 | 30411 | 279 | 109 | BY-S10-01 | Bayou | 2026-06-19 | 13 | Weather - wind | IGSD-isolated section | Forced | None
OE-26-002547 | 10368 | 64 | 162 | HB-S01-01 | Harbor | 2026-06-19 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002548 | 606 | 6 | 101 | BY-S28-02 | Bayou | 2026-06-19 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002549 | 4066 | 107 | 38 | BY-S07-02 | Bayou | 2026-06-19 | 22 | Vegetation | Lateral fuse | Forced | None
OE-26-002550 | 3816 | 12 | 318 | BY-S23-02 | Bayou | 2026-06-20 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002551 | 5100 | 12 | 425 | BY-S01-01 | Bayou | 2026-06-20 | 7 | Animal | Transformer fuse | Forced | None
OE-26-002552 | 17869 | 167 | 107 | BY-S17-01 | Bayou | 2026-06-20 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002553 | 45500 | 364 | 125 | PR-S11-03 | Prairie | 2026-06-20 | 9 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-002554 | 7957 | 109 | 73 | CR-S16-06 | Crossroads | 2026-06-20 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002555 | 1730 | 5 | 346 | BY-S15-02 | Bayou | 2026-06-20 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002556 | 252 | 3 | 84 | CR-S10-02 | Crossroads | 2026-06-20 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-002557 | 128555 | 3673 | 35 | CR-S27-04 | Crossroads | 2026-06-20 | 11 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002558 | 4214 | 14 | 301 | CR-S31-02 | Crossroads | 2026-06-20 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-002559 | 1190 | 14 | 85 | CR-S23-01 | Crossroads | 2026-06-20 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-26-002560 | 11300 | 100 | 113 | BY-S13-02 | Bayou | 2026-06-20 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-002561 | 14504 | 148 | 98 | HB-S02-01 | Harbor | 2026-06-20 | 17 | Unknown | Lateral fuse | Forced | None
OE-26-002562 | 5478 | 33 | 166 | BY-S27-01 | Bayou | 2026-06-20 | 19 | Animal | Lateral fuse | Forced | None
OE-26-002563 | 17005 | 95 | 179 | PR-S01-06 | Prairie | 2026-06-20 | 19 | Animal | Lateral fuse | Forced | None
OE-26-002564 | 28413 | 231 | 123 | BY-S13-06 | Bayou | 2026-06-20 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002565 | 9313 | 67 | 139 | CR-S28-01 | Crossroads | 2026-06-20 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-002566 | 656 | 4 | 164 | HB-S16-03 | Harbor | 2026-06-20 | 22 | Weather - wind | Transformer fuse | Forced | None
OE-26-002567 | 930 | 5 | 186 | BY-S10-04 | Bayou | 2026-06-20 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-002568 | 21483 | 693 | 31 | PR-S16-03 | Prairie | 2026-06-21 | 5 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-002569 | 2184 | 12 | 182 | BY-S29-02 | Bayou | 2026-06-21 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002570 | 504 | 7 | 72 | BY-S07-06 | Bayou | 2026-06-21 | 8 | Animal | Transformer fuse | Forced | None
OE-26-002571 | 12104 | 178 | 68 | HB-S09-02 | Harbor | 2026-06-21 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-002572 | 2088 | 8 | 261 | BY-S16-06 | Bayou | 2026-06-21 | 11 | Animal | Transformer fuse | Forced | None
OE-26-002573 | 66800 | 668 | 100 | CR-S11-02 | Crossroads | 2026-06-21 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002574 | 67728 | 1328 | 51 | CR-S29-03 | Crossroads | 2026-06-21 | 11 | Weather - wind | Substation breaker | Forced | None
OE-26-002575 | 222585 | 2343 | 95 | CR-S21-03 | Crossroads | 2026-06-21 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-002576 | 21060 | 65 | 324 | CR-S16-04 | Crossroads | 2026-06-21 | 18 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002577 | 1885 | 13 | 145 | CR-S27-03 | Crossroads | 2026-06-22 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002578 | 1700 | 10 | 170 | BY-S08-03 | Bayou | 2026-06-22 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-002579 | 72498 | 258 | 281 | HB-S16-03 | Harbor | 2026-06-22 | 8 | Vegetation | IGSD-isolated section | Forced | None
OE-26-002580 | 246 | 1 | 246 | BY-S18-04 | Bayou | 2026-06-22 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002581 | 47191 | 1151 | 41 | BY-S21-01 | Bayou | 2026-06-22 | 9 | Weather - lightning | Feeder recloser | Forced | None
OE-26-002582 | 6480 | 108 | 60 | BY-S22-03 | Bayou | 2026-06-22 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002583 | 7059 | 39 | 181 | PR-S06-03 | Prairie | 2026-06-22 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002584 | 13335 | 127 | 105 | HB-S15-03 | Harbor | 2026-06-22 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-002585 | 536 | 4 | 134 | BY-S11-03 | Bayou | 2026-06-22 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002586 | 610 | 10 | 61 | CR-S13-06 | Crossroads | 2026-06-22 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002587 | 2016 | 14 | 144 | HB-S12-03 | Harbor | 2026-06-22 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002588 | 14694 | 93 | 158 | BY-S04-03 | Bayou | 2026-06-22 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-002589 | 21240 | 120 | 177 | BY-S23-03 | Bayou | 2026-06-22 | 14 | Unknown | Lateral fuse | Forced | None
OE-26-002590 | 1812 | 6 | 302 | PR-S16-05 | Prairie | 2026-06-22 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-002591 | 306 | 3 | 102 | PR-S16-01 | Prairie | 2026-06-22 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002592 | 75710 | 335 | 226 | HB-S02-02 | Harbor | 2026-06-22 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002593 | 36292 | 422 | 86 | PR-S06-02 | Prairie | 2026-06-22 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-002594 | 17686 | 74 | 239 | BY-S30-01 | Bayou | 2026-06-22 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-002595 | 790 | 5 | 158 | PR-S02-02 | Prairie | 2026-06-23 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-26-002596 | 38369 | 1037 | 37 | CR-S12-03 | Crossroads | 2026-06-23 | 6 | Unknown | Substation breaker | Forced | None
OE-26-002597 | 180728 | 2378 | 76 | CR-S27-04 | Crossroads | 2026-06-23 | 8 | Unknown | Feeder recloser | Forced | None
OE-26-002598 | 11610 | 90 | 129 | PR-S19-02 | Prairie | 2026-06-23 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002599 | 81426 | 1986 | 41 | BY-S22-04 | Bayou | 2026-06-23 | 12 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002600 | 654 | 6 | 109 | HB-S12-01 | Harbor | 2026-06-23 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002601 | 220 | 2 | 110 | HB-S12-02 | Harbor | 2026-06-23 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-002602 | 8695 | 47 | 185 | BY-S29-02 | Bayou | 2026-06-23 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-002603 | 4667 | 13 | 359 | BY-S11-02 | Bayou | 2026-06-23 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-002604 | 23086 | 238 | 97 | BY-S24-01 | Bayou | 2026-06-24 | 0 | Vegetation | Lateral fuse | Forced | None
OE-26-002605 | 475 | 1 | 475 | PR-S01-06 | Prairie | 2026-06-24 | 4 | Weather - wind | Transformer fuse | Forced | None
OE-26-002606 | 648 | 9 | 72 | BY-S20-02 | Bayou | 2026-06-24 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002607 | 36984 | 276 | 134 | HB-S07-03 | Harbor | 2026-06-24 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002608 | 213622 | 1037 | 206 | BY-S10-01 | Bayou | 2026-06-24 | 14 | Unknown | Feeder recloser | Forced | None
OE-26-002609 | 1494 | 9 | 166 | PR-S16-05 | Prairie | 2026-06-24 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-002610 | 834 | 6 | 139 | BY-S18-03 | Bayou | 2026-06-24 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002611 | 1010 | 10 | 101 | CR-S15-02 | Crossroads | 2026-06-24 | 21 | Unknown | Transformer fuse | Forced | None
OE-26-002612 | 20888 | 746 | 28 | CR-S03-01 | Crossroads | 2026-06-24 | 23 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002613 | 3861 | 11 | 351 | PR-S13-03 | Prairie | 2026-06-25 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002614 | 2506 | 14 | 179 | PR-S08-03 | Prairie | 2026-06-25 | 6 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002615 | 1261 | 13 | 97 | PR-S03-06 | Prairie | 2026-06-25 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002616 | 2365 | 43 | 55 | HB-S20-02 | Harbor | 2026-06-25 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-002617 | 16744 | 92 | 182 | PR-S01-06 | Prairie | 2026-06-25 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002618 | 1169 | 7 | 167 | BY-S01-02 | Bayou | 2026-06-25 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-002619 | 89600 | 1120 | 80 | BY-S09-03 | Bayou | 2026-06-25 | 16 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002620 | 12052 | 92 | 131 | PR-S12-02 | Prairie | 2026-06-25 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-26-002621 | 1778 | 14 | 127 | BY-S20-03 | Bayou | 2026-06-25 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-002622 | 3525 | 25 | 141 | PR-S07-02 | Prairie | 2026-06-25 | 23 | Animal | Lateral fuse | Forced | None
OE-26-002623 | 822 | 3 | 274 | BY-S23-02 | Bayou | 2026-06-26 | 2 | Animal | Transformer fuse | Forced | None
OE-26-002624 | 2316 | 12 | 193 | PR-S13-01 | Prairie | 2026-06-26 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002625 | 1064 | 8 | 133 | BY-S23-04 | Bayou | 2026-06-26 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002626 | 2538 | 27 | 94 | PR-S11-03 | Prairie | 2026-06-26 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002627 | 153882 | 1494 | 103 | BY-S21-04 | Bayou | 2026-06-26 | 9 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002628 | 1080 | 9 | 120 | CR-S07-03 | Crossroads | 2026-06-26 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002629 | 4706 | 26 | 181 | BY-S13-04 | Bayou | 2026-06-26 | 13 | Animal | Lateral fuse | Forced | None
OE-26-002630 | 8277 | 89 | 93 | PR-S04-03 | Prairie | 2026-06-26 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002631 | 2982 | 14 | 213 | PR-S07-06 | Prairie | 2026-06-26 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-002632 | 4260 | 12 | 355 | PR-S11-03 | Prairie | 2026-06-26 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002633 | 6080 | 40 | 152 | HB-S15-03 | Harbor | 2026-06-26 | 16 | Unknown | Lateral fuse | Forced | None
OE-26-002634 | 801 | 9 | 89 | PR-S15-03 | Prairie | 2026-06-26 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002635 | 1016 | 8 | 127 | HB-S01-03 | Harbor | 2026-06-27 | 4 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002636 | 6882 | 74 | 93 | HB-S06-02 | Harbor | 2026-06-27 | 6 | Animal | Lateral fuse | Forced | None
OE-26-002637 | 356 | 4 | 89 | BY-S23-01 | Bayou | 2026-06-27 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002638 | 642 | 6 | 107 | PR-S12-01 | Prairie | 2026-06-27 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002639 | 78624 | 1456 | 54 | BY-S14-01 | Bayou | 2026-06-27 | 10 | Vegetation | Feeder recloser | Forced | None
OE-26-002640 | 22356 | 243 | 92 | BY-S17-03 | Bayou | 2026-06-27 | 10 | Vegetation | Feeder recloser | Forced | None
OE-26-002641 | 5041 | 71 | 71 | CR-S24-04 | Crossroads | 2026-06-27 | 11 | Animal | Lateral fuse | Forced | None
OE-26-002642 | 1694 | 11 | 154 | PR-S03-05 | Prairie | 2026-06-27 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002643 | 27864 | 216 | 129 | CR-S14-02 | Crossroads | 2026-06-27 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002644 | 790 | 10 | 79 | HB-S10-03 | Harbor | 2026-06-27 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002645 | 891 | 11 | 81 | BY-S09-03 | Bayou | 2026-06-27 | 15 | Animal | Transformer fuse | Forced | None
OE-26-002646 | 212 | 1 | 212 | CR-S04-06 | Crossroads | 2026-06-27 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-002647 | 897 | 13 | 69 | BY-S29-01 | Bayou | 2026-06-27 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-002648 | 38522 | 187 | 206 | PR-S20-01 | Prairie | 2026-06-27 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002649 | 2388 | 4 | 597 | BY-S20-03 | Bayou | 2026-06-27 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-002650 | 242 | 1 | 242 | CR-S05-02 | Crossroads | 2026-06-27 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002651 | 15720 | 131 | 120 | BY-S10-03 | Bayou | 2026-06-27 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002652 | 612 | 4 | 153 | PR-S10-03 | Prairie | 2026-06-27 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002653 | 88618 | 751 | 118 | BY-S09-03 | Bayou | 2026-06-27 | 22 | Vegetation | Feeder recloser | Forced | None
OE-26-002654 | 8906 | 61 | 146 | PR-S13-01 | Prairie | 2026-06-28 | 5 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002655 | 61300 | 613 | 100 | CR-S25-05 | Crossroads | 2026-06-28 | 6 | Vegetation | Feeder recloser | Forced | None
OE-26-002656 | 9570 | 58 | 165 | BY-S23-02 | Bayou | 2026-06-28 | 7 | Vegetation | Lateral fuse | Forced | None
OE-26-002657 | 439 | 1 | 439 | HB-S14-01 | Harbor | 2026-06-28 | 10 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002658 | 2892 | 12 | 241 | PR-S19-05 | Prairie | 2026-06-28 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002659 | 3198 | 13 | 246 | BY-S25-04 | Bayou | 2026-06-28 | 15 | Animal | Transformer fuse | Forced | None
OE-26-002660 | 90207 | 351 | 257 | HB-S11-01 | Harbor | 2026-06-28 | 17 | Animal | Feeder recloser | Forced | None
OE-26-002661 | 54288 | 348 | 156 | PR-S01-05 | Prairie | 2026-06-28 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002662 | 190399 | 911 | 209 | HB-S07-02 | Harbor | 2026-06-28 | 20 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002663 | 11745 | 81 | 145 | BY-S25-02 | Bayou | 2026-06-28 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-002664 | 16632 | 216 | 77 | BY-S09-05 | Bayou | 2026-06-29 | 6 | Animal | Lateral fuse | Forced | None
OE-26-002665 | 888 | 12 | 74 | PR-S13-04 | Prairie | 2026-06-29 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-002666 | 1218 | 7 | 174 | PR-S03-04 | Prairie | 2026-06-29 | 8 | Animal | Transformer fuse | Forced | None
OE-26-002667 | 60400 | 1208 | 50 | BY-S26-05 | Bayou | 2026-06-29 | 10 | Weather - lightning | Substation breaker | Forced | None
OE-26-002668 | 752 | 8 | 94 | BY-S08-01 | Bayou | 2026-06-29 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-002669 | 1989 | 51 | 39 | HB-S15-01 | Harbor | 2026-06-29 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-002670 | 15158 | 106 | 143 | BY-S04-02 | Bayou | 2026-06-29 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002671 | 4978 | 38 | 131 | BY-S18-03 | Bayou | 2026-06-29 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002672 | 1036 | 7 | 148 | BY-S23-05 | Bayou | 2026-06-29 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-002673 | 2604 | 14 | 186 | PR-S02-02 | Prairie | 2026-06-29 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-002674 | 1995 | 19 | 105 | BY-S18-04 | Bayou | 2026-06-29 | 17 | Animal | Lateral fuse | Forced | None
OE-26-002675 | 805 | 7 | 115 | CR-S15-01 | Crossroads | 2026-06-29 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-002676 | 226 | 1 | 226 | PR-S07-05 | Prairie | 2026-06-29 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002677 | 1608 | 12 | 134 | CR-S10-03 | Crossroads | 2026-06-29 | 20 | Animal | Transformer fuse | Forced | None
OE-26-002678 | 8850 | 59 | 150 | PR-S05-02 | Prairie | 2026-06-30 | 4 | Weather - wind | Lateral fuse | Forced | None
OE-26-002679 | 9720 | 162 | 60 | BY-S17-02 | Bayou | 2026-06-30 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002680 | 12852 | 126 | 102 | PR-S03-06 | Prairie | 2026-06-30 | 9 | Animal | Lateral fuse | Forced | None
OE-26-002681 | 1218 | 14 | 87 | CR-S07-06 | Crossroads | 2026-06-30 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002682 | 63612 | 372 | 171 | PR-S07-02 | Prairie | 2026-06-30 | 12 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002683 | 975 | 3 | 325 | BY-S17-02 | Bayou | 2026-06-30 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002684 | 1494 | 9 | 166 | HB-S02-01 | Harbor | 2026-06-30 | 14 | Animal | Transformer fuse | Forced | None
OE-26-002685 | 131138 | 646 | 203 | BY-S29-05 | Bayou | 2026-06-30 | 15 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002686 | 40788 | 618 | 66 | CR-S28-04 | Crossroads | 2026-06-30 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-26-002687 | 21675 | 425 | 51 | HB-S06-05 | Harbor | 2026-06-30 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002688 | 10752 | 56 | 192 | HB-S19-02 | Harbor | 2026-06-30 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-002689 | 285 | 1 | 285 | BY-S08-02 | Bayou | 2026-06-30 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-26-002690 | 1869 | 21 | 89 | HB-S04-01 | Harbor | 2026-06-30 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002691 | 1224 | 6 | 204 | PR-S20-04 | Prairie | 2026-06-30 | 23 | Vegetation | Transformer fuse | Forced | None
OE-26-002692 | 1400 | 8 | 175 | CR-S23-02 | Crossroads | 2026-07-01 | 8 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002693 | 27494 | 233 | 118 | CR-S27-04 | Crossroads | 2026-07-01 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002694 | 2784 | 29 | 96 | CR-S10-01 | Crossroads | 2026-07-01 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-26-002695 | 18330 | 94 | 195 | CR-S13-05 | Crossroads | 2026-07-01 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002696 | 5206 | 38 | 137 | HB-S12-03 | Harbor | 2026-07-01 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002697 | 8760 | 60 | 146 | PR-S19-03 | Prairie | 2026-07-01 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002698 | 1496 | 4 | 374 | PR-S06-01 | Prairie | 2026-07-01 | 12 | Animal | Transformer fuse | Forced | None
OE-26-002699 | 2025 | 9 | 225 | PR-S14-04 | Prairie | 2026-07-01 | 12 | Animal | Transformer fuse | Forced | None
OE-26-002700 | 47880 | 399 | 120 | PR-S06-03 | Prairie | 2026-07-01 | 13 | Vegetation | IGSD-isolated section | Forced | None
OE-26-002701 | 11100 | 60 | 185 | BY-S21-03 | Bayou | 2026-07-01 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002702 | 16200 | 60 | 270 | BY-S20-02 | Bayou | 2026-07-01 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-002703 | 1490 | 10 | 149 | HB-S19-02 | Harbor | 2026-07-01 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-002704 | 2761 | 11 | 251 | BY-S27-02 | Bayou | 2026-07-01 | 23 | Weather - wind | Transformer fuse | Forced | None
OE-26-002705 | 25664 | 401 | 64 | PR-S01-05 | Prairie | 2026-07-01 | 23 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002706 | 11395 | 215 | 53 | HB-S07-03 | Harbor | 2026-07-02 | 5 | Unknown | Lateral fuse | Forced | None
OE-26-002707 | 125732 | 1849 | 68 | HB-S10-03 | Harbor | 2026-07-02 | 8 | Vegetation | Feeder recloser | Forced | None
OE-26-002708 | 11591 | 173 | 67 | BY-S15-05 | Bayou | 2026-07-02 | 9 | Animal | Lateral fuse | Forced | None
OE-26-002709 | 4466 | 29 | 154 | CR-S20-02 | Crossroads | 2026-07-02 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-002710 | 24026 | 586 | 41 | BY-S07-01 | Bayou | 2026-07-02 | 11 | Vegetation | Feeder recloser | Forced | None
OE-26-002711 | 3248 | 14 | 232 | BY-S27-03 | Bayou | 2026-07-02 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002712 | 1495 | 13 | 115 | PR-S09-03 | Prairie | 2026-07-02 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-002713 | 1092 | 6 | 182 | BY-S28-02 | Bayou | 2026-07-02 | 14 | Animal | Transformer fuse | Forced | None
OE-26-002714 | 1586 | 13 | 122 | HB-S19-02 | Harbor | 2026-07-02 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002715 | 5698 | 77 | 74 | BY-S18-03 | Bayou | 2026-07-02 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-002716 | 390 | 3 | 130 | HB-S15-02 | Harbor | 2026-07-02 | 17 | Animal | Transformer fuse | Forced | None
OE-26-002717 | 6324 | 68 | 93 | CR-S22-01 | Crossroads | 2026-07-02 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002718 | 387 | 3 | 129 | CR-S08-02 | Crossroads | 2026-07-02 | 22 | Animal | Transformer fuse | Forced | None
OE-26-002719 | 25239 | 179 | 141 | CR-S25-05 | Crossroads | 2026-07-03 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002720 | 1974 | 14 | 141 | HB-S08-02 | Harbor | 2026-07-03 | 0 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002721 | 2145 | 11 | 195 | HB-S04-01 | Harbor | 2026-07-03 | 3 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002722 | 1220 | 10 | 122 | BY-S21-04 | Bayou | 2026-07-03 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002723 | 18210 | 607 | 30 | BY-S14-02 | Bayou | 2026-07-03 | 8 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002724 | 6534 | 66 | 99 | CR-S08-01 | Crossroads | 2026-07-03 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002725 | 816 | 6 | 136 | HB-S12-02 | Harbor | 2026-07-03 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002726 | 8001 | 21 | 381 | PR-S02-01 | Prairie | 2026-07-03 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002727 | 1503 | 9 | 167 | PR-S15-02 | Prairie | 2026-07-03 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-26-002728 | 18330 | 78 | 235 | PR-S20-03 | Prairie | 2026-07-03 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002729 | 49140 | 260 | 189 | CR-S29-03 | Crossroads | 2026-07-03 | 11 | Weather - wind | IGSD-isolated section | Forced | None
OE-26-002730 | 1507 | 11 | 137 | BY-S21-05 | Bayou | 2026-07-03 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-002731 | 374 | 2 | 187 | PR-S09-03 | Prairie | 2026-07-03 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002732 | 1156 | 4 | 289 | BY-S18-03 | Bayou | 2026-07-03 | 22 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002733 | 18509 | 83 | 223 | CR-S02-03 | Crossroads | 2026-07-03 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002734 | 119 | 1 | 119 | CR-S25-05 | Crossroads | 2026-07-04 | 0 | Vegetation | Transformer fuse | Forced | None
OE-26-002735 | 41915 | 505 | 83 | HB-S15-03 | Harbor | 2026-07-04 | 9 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-002736 | 900 | 2 | 450 | BY-S09-02 | Bayou | 2026-07-04 | 10 | Animal | Transformer fuse | Forced | None
OE-26-002737 | 60690 | 255 | 238 | BY-S18-04 | Bayou | 2026-07-04 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002738 | 27140 | 460 | 59 | BY-S21-04 | Bayou | 2026-07-04 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-002739 | 75516 | 609 | 124 | CR-S28-01 | Crossroads | 2026-07-04 | 16 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-002740 | 720 | 6 | 120 | BY-S26-03 | Bayou | 2026-07-04 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-002741 | 280 | 2 | 140 | BY-S09-03 | Bayou | 2026-07-04 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002742 | 3198 | 82 | 39 | CR-S19-02 | Crossroads | 2026-07-04 | 21 | Weather - wind | Lateral fuse | Forced | None
OE-26-002743 | 38 | 1 | 38 | BY-S10-03 | Bayou | 2026-07-04 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002744 | 15190 | 155 | 98 | BY-S12-03 | Bayou | 2026-07-05 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002745 | 104715 | 1611 | 65 | PR-S06-01 | Prairie | 2026-07-05 | 7 | Weather - lightning | Substation breaker | Forced | None
OE-26-002746 | 10829 | 49 | 221 | BY-S02-02 | Bayou | 2026-07-05 | 9 | Weather - wind | Lateral fuse | Forced | None
OE-26-002747 | 240 | 3 | 80 | CR-S19-04 | Crossroads | 2026-07-05 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-002748 | 1748 | 23 | 76 | HB-S19-04 | Harbor | 2026-07-05 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002749 | 9856 | 112 | 88 | HB-S20-05 | Harbor | 2026-07-05 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002750 | 8924 | 194 | 46 | BY-S19-01 | Bayou | 2026-07-05 | 17 | Animal | Lateral fuse | Forced | None
OE-26-002751 | 104598 | 894 | 117 | CR-S13-05 | Crossroads | 2026-07-05 | 20 | Vehicle or public | Feeder recloser | Forced | None
OE-26-002752 | 7182 | 114 | 63 | CR-S05-04 | Crossroads | 2026-07-06 | 3 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002753 | 700 | 5 | 140 | BY-S18-05 | Bayou | 2026-07-06 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002754 | 1000 | 4 | 250 | BY-S16-01 | Bayou | 2026-07-06 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002755 | 6435 | 65 | 99 | HB-S12-02 | Harbor | 2026-07-06 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002756 | 1316 | 7 | 188 | PR-S13-04 | Prairie | 2026-07-06 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002757 | 352 | 4 | 88 | CR-S13-02 | Crossroads | 2026-07-06 | 9 | Weather - wind | Transformer fuse | Forced | None
OE-26-002758 | 2346 | 17 | 138 | BY-S10-01 | Bayou | 2026-07-06 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-002759 | 11850 | 158 | 75 | BY-S15-01 | Bayou | 2026-07-06 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002760 | 696 | 4 | 174 | BY-S15-03 | Bayou | 2026-07-06 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002761 | 4956 | 59 | 84 | CR-S13-01 | Crossroads | 2026-07-06 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-002762 | 1374 | 6 | 229 | PR-S07-05 | Prairie | 2026-07-06 | 10 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002763 | 132987 | 1371 | 97 | PR-S18-03 | Prairie | 2026-07-06 | 10 | Weather - lightning | Substation breaker | Forced | None
OE-26-002764 | 1378 | 13 | 106 | BY-S23-03 | Bayou | 2026-07-06 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-002765 | 963 | 9 | 107 | BY-S27-04 | Bayou | 2026-07-06 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002766 | 88 | 1 | 88 | CR-S31-03 | Crossroads | 2026-07-06 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002767 | 7912 | 92 | 86 | BY-S18-04 | Bayou | 2026-07-06 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002768 | 1188 | 11 | 108 | BY-S23-05 | Bayou | 2026-07-06 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002769 | 56712 | 408 | 139 | BY-S27-02 | Bayou | 2026-07-06 | 17 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002770 | 1188 | 9 | 132 | CR-S22-01 | Crossroads | 2026-07-06 | 17 | Unknown | Transformer fuse | Forced | None
OE-26-002771 | 20750 | 125 | 166 | BY-S22-01 | Bayou | 2026-07-06 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-002772 | 1350 | 9 | 150 | BY-S11-03 | Bayou | 2026-07-06 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-002773 | 159373 | 809 | 197 | PR-S18-05 | Prairie | 2026-07-06 | 21 | Vegetation | Feeder recloser | Forced | None
OE-26-002774 | 2760 | 10 | 276 | CR-S02-01 | Crossroads | 2026-07-06 | 23 | Unknown | Transformer fuse | Forced | None
OE-26-002775 | 450 | 6 | 75 | BY-S23-01 | Bayou | 2026-07-07 | 2 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002776 | 37410 | 290 | 129 | CR-S30-04 | Crossroads | 2026-07-07 | 7 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002777 | 101528 | 686 | 148 | BY-S13-06 | Bayou | 2026-07-07 | 8 | Animal | IGSD-isolated section | Forced | None
OE-26-002778 | 3808 | 14 | 272 | BY-S15-04 | Bayou | 2026-07-07 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002779 | 35500 | 125 | 284 | PR-S09-03 | Prairie | 2026-07-07 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-002780 | 1720 | 10 | 172 | PR-S18-01 | Prairie | 2026-07-07 | 10 | Animal | Transformer fuse | Forced | None
OE-26-002781 | 2048 | 16 | 128 | CR-S29-03 | Crossroads | 2026-07-07 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002782 | 3612 | 14 | 258 | HB-S06-05 | Harbor | 2026-07-07 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-002783 | 5500 | 22 | 250 | CR-S28-01 | Crossroads | 2026-07-07 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002784 | 1400 | 10 | 140 | CR-S26-03 | Crossroads | 2026-07-07 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002785 | 1476 | 12 | 123 | CR-S19-02 | Crossroads | 2026-07-07 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002786 | 2016 | 36 | 56 | CR-S23-04 | Crossroads | 2026-07-07 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002787 | 605 | 5 | 121 | HB-S10-03 | Harbor | 2026-07-07 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002788 | 13050 | 174 | 75 | BY-S02-01 | Bayou | 2026-07-07 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002789 | 24523 | 179 | 137 | HB-S03-03 | Harbor | 2026-07-07 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-002790 | 1365 | 3 | 455 | HB-S13-02 | Harbor | 2026-07-08 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002791 | 2264 | 8 | 283 | CR-S25-02 | Crossroads | 2026-07-08 | 5 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002792 | 2821 | 13 | 217 | BY-S12-02 | Bayou | 2026-07-08 | 6 | Weather - wind | Transformer fuse | Forced | None
OE-26-002793 | 644 | 7 | 92 | PR-S02-02 | Prairie | 2026-07-08 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-002794 | 4664 | 44 | 106 | CR-S07-01 | Crossroads | 2026-07-08 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002795 | 12213 | 59 | 207 | HB-S02-03 | Harbor | 2026-07-08 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002796 | 19398 | 159 | 122 | BY-S14-02 | Bayou | 2026-07-08 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002797 | 4375 | 25 | 175 | BY-S28-03 | Bayou | 2026-07-08 | 13 | Unknown | Lateral fuse | Forced | None
OE-26-002798 | 3588 | 26 | 138 | HB-S20-04 | Harbor | 2026-07-08 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002799 | 47188 | 502 | 94 | PR-S13-04 | Prairie | 2026-07-08 | 13 | Vegetation | Feeder recloser | Forced | None
OE-26-002800 | 116790 | 1374 | 85 | HB-S06-01 | Harbor | 2026-07-08 | 15 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-002801 | 7728 | 56 | 138 | BY-S07-05 | Bayou | 2026-07-08 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-002802 | 1208 | 4 | 302 | BY-S21-01 | Bayou | 2026-07-08 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002803 | 149 | 1 | 149 | BY-S23-02 | Bayou | 2026-07-08 | 17 | Animal | Transformer fuse | Forced | None
OE-26-002804 | 1400 | 5 | 280 | PR-S20-04 | Prairie | 2026-07-08 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002805 | 6765 | 123 | 55 | BY-S13-03 | Bayou | 2026-07-09 | 0 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002806 | 82770 | 310 | 267 | BY-S03-03 | Bayou | 2026-07-09 | 5 | Vegetation | Feeder recloser | Forced | None
OE-26-002807 | 4180 | 55 | 76 | PR-S15-03 | Prairie | 2026-07-09 | 5 | Vegetation | Lateral fuse | Forced | None
OE-26-002808 | 452 | 4 | 113 | BY-S26-05 | Bayou | 2026-07-09 | 6 | Vegetation | Transformer fuse | Forced | None
OE-26-002809 | 66452 | 1796 | 37 | BY-S19-03 | Bayou | 2026-07-09 | 7 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002810 | 4655 | 35 | 133 | CR-S25-04 | Crossroads | 2026-07-09 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002811 | 2304 | 12 | 192 | CR-S16-06 | Crossroads | 2026-07-09 | 11 | Animal | Transformer fuse | Forced | None
OE-26-002812 | 11700 | 60 | 195 | CR-S07-05 | Crossroads | 2026-07-09 | 12 | Animal | Lateral fuse | Forced | None
OE-26-002813 | 1804 | 11 | 164 | CR-S32-05 | Crossroads | 2026-07-09 | 13 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002814 | 7548 | 102 | 74 | PR-S03-04 | Prairie | 2026-07-09 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-002815 | 54675 | 729 | 75 | BY-S23-05 | Bayou | 2026-07-09 | 14 | Unknown | Feeder recloser | Forced | None
OE-26-002816 | 861 | 3 | 287 | CR-S04-06 | Crossroads | 2026-07-09 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-002817 | 1113 | 7 | 159 | CR-S22-01 | Crossroads | 2026-07-09 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002818 | 4731 | 57 | 83 | BY-S18-05 | Bayou | 2026-07-09 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-002819 | 19966 | 149 | 134 | HB-S20-03 | Harbor | 2026-07-09 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002820 | 54500 | 545 | 100 | BY-S09-05 | Bayou | 2026-07-09 | 17 | Vegetation | Feeder recloser | Forced | None
OE-26-002821 | 10302 | 51 | 202 | HB-S08-05 | Harbor | 2026-07-09 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002822 | 5180 | 70 | 74 | CR-S29-01 | Crossroads | 2026-07-09 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002823 | 988 | 4 | 247 | PR-S10-01 | Prairie | 2026-07-09 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002824 | 528 | 6 | 88 | BY-S10-02 | Bayou | 2026-07-09 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002825 | 10269 | 163 | 63 | PR-S13-06 | Prairie | 2026-07-10 | 1 | Vegetation | Lateral fuse | Forced | None
OE-26-002826 | 16910 | 95 | 178 | CR-S23-02 | Crossroads | 2026-07-10 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-26-002827 | 11554 | 109 | 106 | HB-S10-03 | Harbor | 2026-07-10 | 5 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002828 | 1655 | 5 | 331 | BY-S20-03 | Bayou | 2026-07-10 | 7 | Animal | Transformer fuse | Forced | None
OE-26-002829 | 210 | 1 | 210 | BY-S18-07 | Bayou | 2026-07-10 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002830 | 3625 | 29 | 125 | PR-S11-03 | Prairie | 2026-07-10 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002831 | 870 | 6 | 145 | HB-S01-03 | Harbor | 2026-07-10 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002832 | 234 | 2 | 117 | BY-S23-03 | Bayou | 2026-07-10 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-002833 | 9263 | 157 | 59 | CR-S05-01 | Crossroads | 2026-07-10 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-002834 | 2412 | 12 | 201 | CR-S15-03 | Crossroads | 2026-07-10 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002835 | 1254 | 6 | 209 | PR-S04-03 | Prairie | 2026-07-10 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-002836 | 3591 | 19 | 189 | PR-S18-04 | Prairie | 2026-07-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002837 | 163 | 1 | 163 | BY-S14-01 | Bayou | 2026-07-10 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002838 | 740 | 4 | 185 | BY-S19-03 | Bayou | 2026-07-10 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-002839 | 2408 | 43 | 56 | BY-S21-05 | Bayou | 2026-07-10 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002840 | 2040 | 15 | 136 | CR-S12-02 | Crossroads | 2026-07-10 | 14 | Animal | Lateral fuse | Forced | None
OE-26-002841 | 426 | 2 | 213 | PR-S18-01 | Prairie | 2026-07-10 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002842 | 732 | 6 | 122 | PR-S01-01 | Prairie | 2026-07-10 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002843 | 1100 | 4 | 275 | HB-S05-01 | Harbor | 2026-07-10 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002844 | 1920 | 12 | 160 | BY-S18-04 | Bayou | 2026-07-10 | 18 | Animal | Transformer fuse | Forced | None
OE-26-002845 | 82820 | 1010 | 82 | BY-S20-01 | Bayou | 2026-07-10 | 19 | Animal | Feeder recloser | Forced | None
OE-26-002846 | 1500 | 10 | 150 | BY-S20-01 | Bayou | 2026-07-10 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002847 | 8624 | 77 | 112 | BY-S27-05 | Bayou | 2026-07-10 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-002848 | 1326 | 13 | 102 | PR-S15-06 | Prairie | 2026-07-10 | 20 | Animal | Transformer fuse | Forced | None
OE-26-002849 | 111 | 1 | 111 | HB-S17-01 | Harbor | 2026-07-10 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-002850 | 73901 | 1103 | 67 | PR-S06-01 | Prairie | 2026-07-10 | 22 | Animal | Feeder recloser | Forced | None
OE-26-002851 | 1014 | 13 | 78 | CR-S18-01 | Crossroads | 2026-07-10 | 23 | Unknown | Transformer fuse | Forced | None
OE-26-002852 | 2664 | 24 | 111 | CR-S04-03 | Crossroads | 2026-07-11 | 2 | Vegetation | Lateral fuse | Forced | None
OE-26-002853 | 254 | 2 | 127 | BY-S05-02 | Bayou | 2026-07-11 | 4 | Vegetation | Transformer fuse | Forced | None
OE-26-002854 | 6776 | 14 | 484 | BY-S27-03 | Bayou | 2026-07-11 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002855 | 79940 | 1142 | 70 | PR-S09-01 | Prairie | 2026-07-11 | 8 | Vegetation | Feeder recloser | Forced | None
OE-26-002856 | 20933 | 121 | 173 | PR-S12-01 | Prairie | 2026-07-11 | 8 | Unknown | Lateral fuse | Forced | None
OE-26-002857 | 27675 | 123 | 225 | PR-S18-01 | Prairie | 2026-07-11 | 8 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002858 | 7568 | 88 | 86 | BY-S10-03 | Bayou | 2026-07-11 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002859 | 1288 | 8 | 161 | PR-S03-05 | Prairie | 2026-07-11 | 11 | Animal | Transformer fuse | Forced | None
OE-26-002860 | 11413 | 101 | 113 | CR-S32-03 | Crossroads | 2026-07-11 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002861 | 7290 | 90 | 81 | HB-S14-01 | Harbor | 2026-07-11 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002862 | 615 | 3 | 205 | PR-S10-01 | Prairie | 2026-07-11 | 14 | Animal | Transformer fuse | Forced | None
OE-26-002863 | 3560 | 40 | 89 | PR-S13-04 | Prairie | 2026-07-11 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002864 | 38808 | 98 | 396 | PR-S15-05 | Prairie | 2026-07-11 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002865 | 8908 | 68 | 131 | BY-S22-03 | Bayou | 2026-07-11 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002866 | 1358 | 14 | 97 | BY-S21-02 | Bayou | 2026-07-11 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-002867 | 3421 | 11 | 311 | PR-S16-05 | Prairie | 2026-07-11 | 16 | Animal | Transformer fuse | Forced | None
OE-26-002868 | 405 | 3 | 135 | BY-S05-02 | Bayou | 2026-07-11 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-002869 | 2982 | 42 | 71 | CR-S09-04 | Crossroads | 2026-07-11 | 17 | Animal | Lateral fuse | Forced | None
OE-26-002870 | 1020 | 10 | 102 | BY-S18-05 | Bayou | 2026-07-11 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-002871 | 284 | 4 | 71 | HB-S12-01 | Harbor | 2026-07-11 | 22 | Weather - wind | Transformer fuse | Forced | None
OE-26-002872 | 2400 | 32 | 75 | PR-S10-01 | Prairie | 2026-07-11 | 22 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002873 | 675 | 3 | 225 | HB-S10-03 | Harbor | 2026-07-12 | 3 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002874 | 535 | 5 | 107 | BY-S09-01 | Bayou | 2026-07-12 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-002875 | 33496 | 316 | 106 | CR-S02-01 | Crossroads | 2026-07-12 | 7 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-002876 | 97008 | 2021 | 48 | BY-S19-01 | Bayou | 2026-07-12 | 8 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002877 | 4214 | 49 | 86 | PR-S03-04 | Prairie | 2026-07-12 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-002878 | 1560 | 6 | 260 | BY-S18-05 | Bayou | 2026-07-12 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002879 | 11252 | 97 | 116 | BY-S18-07 | Bayou | 2026-07-12 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002880 | 3710 | 70 | 53 | BY-S29-02 | Bayou | 2026-07-12 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-002881 | 550 | 5 | 110 | CR-S03-01 | Crossroads | 2026-07-12 | 10 | Weather - wind | Transformer fuse | Forced | None
OE-26-002882 | 154350 | 1029 | 150 | PR-S13-01 | Prairie | 2026-07-12 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002883 | 5589 | 81 | 69 | BY-S07-03 | Bayou | 2026-07-12 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002884 | 49880 | 1247 | 40 | BY-S09-01 | Bayou | 2026-07-12 | 13 | Equipment - overhead | Substation breaker | Forced | None
OE-26-002885 | 1050 | 6 | 175 | BY-S14-03 | Bayou | 2026-07-12 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002886 | 612 | 9 | 68 | CR-S18-01 | Crossroads | 2026-07-12 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002887 | 6975 | 75 | 93 | CR-S26-06 | Crossroads | 2026-07-12 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002888 | 3864 | 14 | 276 | HB-S01-05 | Harbor | 2026-07-12 | 16 | Unknown | Transformer fuse | Forced | None
OE-26-002889 | 1157 | 13 | 89 | PR-S19-05 | Prairie | 2026-07-12 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-002890 | 1400 | 14 | 100 | BY-S16-05 | Bayou | 2026-07-12 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002891 | 6123 | 39 | 157 | BY-S30-02 | Bayou | 2026-07-13 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002892 | 6496 | 58 | 112 | CR-S26-05 | Crossroads | 2026-07-13 | 5 | Vegetation | Lateral fuse | Forced | None
OE-26-002893 | 59236 | 236 | 251 | BY-S18-06 | Bayou | 2026-07-13 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002894 | 11455 | 79 | 145 | HB-S05-01 | Harbor | 2026-07-13 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002895 | 11920 | 149 | 80 | HB-S17-02 | Harbor | 2026-07-13 | 10 | Animal | Lateral fuse | Forced | None
OE-26-002896 | 1990 | 10 | 199 | PR-S15-05 | Prairie | 2026-07-13 | 10 | Animal | Transformer fuse | Forced | None
OE-26-002897 | 2054 | 13 | 158 | BY-S18-01 | Bayou | 2026-07-13 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002898 | 404 | 4 | 101 | BY-S20-02 | Bayou | 2026-07-13 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002899 | 504 | 6 | 84 | BY-S23-04 | Bayou | 2026-07-13 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-002900 | 1792 | 14 | 128 | BY-S26-05 | Bayou | 2026-07-13 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002901 | 1830 | 10 | 183 | PR-S18-01 | Prairie | 2026-07-13 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-002902 | 16900 | 325 | 52 | BY-S03-01 | Bayou | 2026-07-13 | 13 | Vegetation | IGSD-isolated section | Forced | None
OE-26-002903 | 5660 | 20 | 283 | CR-S07-01 | Crossroads | 2026-07-13 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002904 | 1240 | 10 | 124 | CR-S08-05 | Crossroads | 2026-07-13 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002905 | 616 | 2 | 308 | PR-S01-05 | Prairie | 2026-07-13 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002906 | 372 | 4 | 93 | PR-S10-01 | Prairie | 2026-07-13 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-002907 | 8536 | 44 | 194 | BY-S15-06 | Bayou | 2026-07-13 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-26-002908 | 522 | 18 | 29 | HB-S01-05 | Harbor | 2026-07-13 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-26-002909 | 6162 | 158 | 39 | CR-S26-05 | Crossroads | 2026-07-13 | 17 | Weather - lightning | IGSD-isolated section | Forced | None
OE-26-002910 | 2526 | 6 | 421 | BY-S02-01 | Bayou | 2026-07-13 | 18 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002911 | 6943 | 53 | 131 | PR-S01-05 | Prairie | 2026-07-13 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002912 | 534 | 3 | 178 | BY-S16-03 | Bayou | 2026-07-13 | 20 | Animal | Transformer fuse | Forced | None
OE-26-002913 | 131 | 1 | 131 | BY-S17-04 | Bayou | 2026-07-13 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-002914 | 8949 | 57 | 157 | CR-S02-05 | Crossroads | 2026-07-13 | 21 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002915 | 1218 | 14 | 87 | CR-S13-05 | Crossroads | 2026-07-13 | 21 | Animal | Transformer fuse | Forced | None
OE-26-002916 | 515 | 5 | 103 | PR-S15-03 | Prairie | 2026-07-13 | 22 | Vegetation | Lateral fuse | Forced | None
OE-26-002917 | 5928 | 39 | 152 | BY-S21-01 | Bayou | 2026-07-14 | 0 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002918 | 208 | 2 | 104 | BY-S29-01 | Bayou | 2026-07-14 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002919 | 1638 | 18 | 91 | CR-S05-05 | Crossroads | 2026-07-14 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002920 | 1764 | 12 | 147 | CR-S15-02 | Crossroads | 2026-07-14 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002921 | 756 | 4 | 189 | PR-S01-06 | Prairie | 2026-07-14 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002922 | 2327 | 13 | 179 | CR-S32-01 | Crossroads | 2026-07-14 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002923 | 60119 | 761 | 79 | CR-S09-01 | Crossroads | 2026-07-14 | 17 | Weather - lightning | IGSD-isolated section | Forced | None
OE-26-002924 | 1680 | 12 | 140 | HB-S01-02 | Harbor | 2026-07-14 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002925 | 2968 | 14 | 212 | PR-S03-05 | Prairie | 2026-07-14 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002926 | 1188 | 22 | 54 | CR-S25-05 | Crossroads | 2026-07-14 | 20 | Weather - wind | Lateral fuse | Forced | None
OE-26-002927 | 11615 | 101 | 115 | BY-S07-02 | Bayou | 2026-07-14 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-002928 | 11750 | 94 | 125 | CR-S11-01 | Crossroads | 2026-07-14 | 21 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002929 | 17901 | 81 | 221 | PR-S14-04 | Prairie | 2026-07-14 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002930 | 717 | 3 | 239 | CR-S14-05 | Crossroads | 2026-07-14 | 23 | Weather - wind | Transformer fuse | Forced | None
OE-26-002931 | 10528 | 94 | 112 | PR-S01-01 | Prairie | 2026-07-15 | 1 | Vegetation | Lateral fuse | Forced | None
OE-26-002932 | 3408 | 12 | 284 | BY-S07-04 | Bayou | 2026-07-15 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-26-002933 | 380 | 4 | 95 | PR-S04-01 | Prairie | 2026-07-15 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002934 | 77050 | 575 | 134 | BY-S15-03 | Bayou | 2026-07-15 | 12 | Weather - lightning | IGSD-isolated section | Forced | None
OE-26-002935 | 40248 | 936 | 43 | HB-S10-01 | Harbor | 2026-07-15 | 13 | Vegetation | Feeder recloser | Forced | None
OE-26-002936 | 1863 | 23 | 81 | BY-S19-02 | Bayou | 2026-07-15 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002937 | 5032 | 37 | 136 | HB-S14-01 | Harbor | 2026-07-15 | 15 | Unknown | Lateral fuse | Forced | None
OE-26-002938 | 20880 | 174 | 120 | CR-S15-03 | Crossroads | 2026-07-15 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002939 | 516 | 3 | 172 | BY-S26-02 | Bayou | 2026-07-15 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-002940 | 312 | 8 | 39 | HB-S10-03 | Harbor | 2026-07-15 | 17 | Animal | Transformer fuse | Forced | None
OE-26-002941 | 54230 | 935 | 58 | CR-S20-03 | Crossroads | 2026-07-15 | 18 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-002942 | 1808 | 8 | 226 | BY-S06-02 | Bayou | 2026-07-15 | 20 | Animal | Transformer fuse | Forced | None
OE-26-002943 | 343 | 7 | 49 | BY-S25-01 | Bayou | 2026-07-15 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-002944 | 1484 | 14 | 106 | PR-S13-01 | Prairie | 2026-07-15 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-002945 | 1176 | 7 | 168 | PR-S19-02 | Prairie | 2026-07-16 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002946 | 1421 | 7 | 203 | BY-S13-04 | Bayou | 2026-07-16 | 4 | Animal | Transformer fuse | Forced | None
OE-26-002947 | 3234 | 7 | 462 | PR-S03-04 | Prairie | 2026-07-16 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002948 | 2444 | 13 | 188 | HB-S09-01 | Harbor | 2026-07-16 | 7 | Animal | Transformer fuse | Forced | None
OE-26-002949 | 1650 | 11 | 150 | BY-S05-03 | Bayou | 2026-07-16 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-002950 | 38998 | 1147 | 34 | CR-S23-03 | Crossroads | 2026-07-16 | 8 | Vehicle or public | Substation breaker | Forced | None
OE-26-002951 | 1248 | 13 | 96 | HB-S07-03 | Harbor | 2026-07-16 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002952 | 9620 | 37 | 260 | HB-S03-01 | Harbor | 2026-07-16 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002953 | 814 | 11 | 74 | PR-S03-03 | Prairie | 2026-07-16 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002954 | 96558 | 627 | 154 | PR-S08-03 | Prairie | 2026-07-16 | 9 | Weather - lightning | Feeder recloser | Forced | None
OE-26-002955 | 2592 | 8 | 324 | PR-S18-03 | Prairie | 2026-07-16 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002956 | 11536 | 56 | 206 | PR-S15-06 | Prairie | 2026-07-16 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002957 | 66836 | 539 | 124 | BY-S18-03 | Bayou | 2026-07-16 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-002958 | 202 | 1 | 202 | PR-S20-01 | Prairie | 2026-07-16 | 13 | Animal | Transformer fuse | Forced | None
OE-26-002959 | 9476 | 92 | 103 | BY-S23-01 | Bayou | 2026-07-16 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002960 | 5040 | 40 | 126 | BY-S27-02 | Bayou | 2026-07-16 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-26-002961 | 23056 | 131 | 176 | PR-S18-04 | Prairie | 2026-07-16 | 15 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002962 | 1512 | 7 | 216 | PR-S05-01 | Prairie | 2026-07-16 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002963 | 18091 | 79 | 229 | PR-S16-02 | Prairie | 2026-07-16 | 19 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002964 | 18117 | 99 | 183 | PR-S12-03 | Prairie | 2026-07-16 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002965 | 49839 | 1347 | 37 | BY-S15-02 | Bayou | 2026-07-16 | 21 | Weather - wind | Feeder recloser | Forced | None
OE-26-002966 | 704 | 8 | 88 | CR-S01-03 | Crossroads | 2026-07-16 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002967 | 960 | 10 | 96 | PR-S08-02 | Prairie | 2026-07-17 | 0 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002968 | 2112 | 12 | 176 | CR-S23-01 | Crossroads | 2026-07-17 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002969 | 37327 | 229 | 163 | BY-S22-03 | Bayou | 2026-07-17 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-002970 | 12788 | 46 | 278 | PR-S08-02 | Prairie | 2026-07-17 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002971 | 13416 | 86 | 156 | CR-S07-03 | Crossroads | 2026-07-17 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002972 | 1872 | 13 | 144 | PR-S07-06 | Prairie | 2026-07-17 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002973 | 7070 | 70 | 101 | CR-S04-03 | Crossroads | 2026-07-17 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002974 | 6149 | 43 | 143 | CR-S18-06 | Crossroads | 2026-07-17 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002975 | 14784 | 84 | 176 | CR-S32-02 | Crossroads | 2026-07-17 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-002976 | 21360 | 267 | 80 | BY-S14-03 | Bayou | 2026-07-17 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-002977 | 10976 | 196 | 56 | BY-S26-01 | Bayou | 2026-07-17 | 15 | Unknown | Lateral fuse | Forced | None
OE-26-002978 | 649 | 11 | 59 | PR-S07-06 | Prairie | 2026-07-17 | 15 | Animal | Transformer fuse | Forced | None
OE-26-002979 | 17400 | 60 | 290 | CR-S07-07 | Crossroads | 2026-07-17 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-002980 | 8850 | 50 | 177 | PR-S05-02 | Prairie | 2026-07-17 | 18 | Animal | Lateral fuse | Forced | None
OE-26-002981 | 596 | 2 | 298 | CR-S28-02 | Crossroads | 2026-07-17 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-26-002982 | 675 | 9 | 75 | BY-S26-02 | Bayou | 2026-07-17 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-002983 | 82460 | 620 | 133 | HB-S01-01 | Harbor | 2026-07-17 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-002984 | 1666 | 14 | 119 | PR-S20-01 | Prairie | 2026-07-17 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-26-002985 | 12516 | 149 | 84 | PR-S03-01 | Prairie | 2026-07-18 | 2 | Vegetation | Lateral fuse | Forced | None
OE-26-002986 | 2656 | 32 | 83 | HB-S19-04 | Harbor | 2026-07-18 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-002987 | 45825 | 325 | 141 | CR-S02-02 | Crossroads | 2026-07-18 | 7 | Weather - lightning | Lateral fuse | Forced | None
OE-26-002988 | 1870 | 10 | 187 | HB-S14-03 | Harbor | 2026-07-18 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-002989 | 32736 | 176 | 186 | BY-S15-02 | Bayou | 2026-07-18 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-002990 | 31416 | 616 | 51 | PR-S16-05 | Prairie | 2026-07-18 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-26-002991 | 61134 | 1329 | 46 | PR-S18-05 | Prairie | 2026-07-18 | 12 | Animal | Feeder recloser | Forced | None
OE-26-002992 | 33908 | 196 | 173 | BY-S10-04 | Bayou | 2026-07-18 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-002993 | 10780 | 77 | 140 | HB-S19-04 | Harbor | 2026-07-18 | 13 | Animal | Lateral fuse | Forced | None
OE-26-002994 | 1768 | 13 | 136 | HB-S20-02 | Harbor | 2026-07-18 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-002995 | 105 | 1 | 105 | CR-S06-01 | Crossroads | 2026-07-18 | 15 | Animal | Transformer fuse | Forced | None
OE-26-002996 | 7865 | 55 | 143 | PR-S13-06 | Prairie | 2026-07-18 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-002997 | 2340 | 12 | 195 | BY-S26-04 | Bayou | 2026-07-18 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-002998 | 1800 | 10 | 180 | CR-S32-01 | Crossroads | 2026-07-19 | 5 | Vehicle or public | Transformer fuse | Forced | None
OE-26-002999 | 1584 | 12 | 132 | PR-S15-06 | Prairie | 2026-07-19 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003000 | 5185 | 61 | 85 | HB-S19-04 | Harbor | 2026-07-19 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003001 | 775 | 5 | 155 | BY-S21-05 | Bayou | 2026-07-19 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-003002 | 54825 | 255 | 215 | BY-S29-02 | Bayou | 2026-07-19 | 8 | Animal | Lateral fuse | Forced | None
OE-26-003003 | 141 | 1 | 141 | CR-S10-03 | Crossroads | 2026-07-19 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-003004 | 7614 | 54 | 141 | BY-S01-02 | Bayou | 2026-07-19 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003005 | 8030 | 73 | 110 | BY-S15-03 | Bayou | 2026-07-19 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-003006 | 31065 | 285 | 109 | PR-S19-03 | Prairie | 2026-07-19 | 10 | Weather - lightning | Feeder recloser | Forced | None
OE-26-003007 | 690 | 6 | 115 | CR-S01-01 | Crossroads | 2026-07-19 | 11 | Unknown | Transformer fuse | Forced | None
OE-26-003008 | 1144 | 8 | 143 | CR-S07-01 | Crossroads | 2026-07-19 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003009 | 1920 | 24 | 80 | HB-S01-05 | Harbor | 2026-07-19 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003010 | 198 | 1 | 198 | CR-S09-03 | Crossroads | 2026-07-19 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-003011 | 1125 | 9 | 125 | PR-S04-03 | Prairie | 2026-07-19 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-003012 | 780 | 5 | 156 | BY-S09-01 | Bayou | 2026-07-19 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-003013 | 3710 | 53 | 70 | BY-S29-01 | Bayou | 2026-07-19 | 15 | Animal | Lateral fuse | Forced | None
OE-26-003014 | 1940 | 10 | 194 | CR-S08-01 | Crossroads | 2026-07-19 | 15 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003015 | 951 | 3 | 317 | HB-S07-03 | Harbor | 2026-07-19 | 15 | Animal | Transformer fuse | Forced | None
OE-26-003016 | 57202 | 773 | 74 | HB-S15-03 | Harbor | 2026-07-19 | 15 | Vegetation | Feeder recloser | Forced | None
OE-26-003017 | 3276 | 14 | 234 | BY-S15-03 | Bayou | 2026-07-19 | 16 | Animal | Transformer fuse | Forced | None
OE-26-003018 | 58512 | 552 | 106 | CR-S07-01 | Crossroads | 2026-07-19 | 16 | Animal | Feeder recloser | Forced | None
OE-26-003019 | 146124 | 492 | 297 | PR-S19-03 | Prairie | 2026-07-19 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003020 | 1547 | 13 | 119 | CR-S20-05 | Crossroads | 2026-07-19 | 20 | Animal | Transformer fuse | Forced | None
OE-26-003021 | 1704 | 12 | 142 | PR-S15-01 | Prairie | 2026-07-20 | 3 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003022 | 74060 | 805 | 92 | BY-S16-04 | Bayou | 2026-07-20 | 8 | Vegetation | Feeder recloser | Forced | None
OE-26-003023 | 6235 | 43 | 145 | PR-S16-01 | Prairie | 2026-07-20 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003024 | 73 | 1 | 73 | BY-S23-04 | Bayou | 2026-07-20 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-003025 | 27125 | 217 | 125 | CR-S07-05 | Crossroads | 2026-07-20 | 9 | Animal | Lateral fuse | Forced | None
OE-26-003026 | 45136 | 728 | 62 | CR-S29-02 | Crossroads | 2026-07-20 | 9 | Vegetation | Feeder recloser | Forced | None
OE-26-003027 | 5425 | 31 | 175 | BY-S11-03 | Bayou | 2026-07-20 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003028 | 4059 | 33 | 123 | BY-S09-03 | Bayou | 2026-07-20 | 13 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003029 | 13452 | 76 | 177 | PR-S07-06 | Prairie | 2026-07-20 | 13 | Weather - wind | Lateral fuse | Forced | None
OE-26-003030 | 49306 | 178 | 277 | BY-S08-02 | Bayou | 2026-07-20 | 14 | Animal | Lateral fuse | Forced | None
OE-26-003031 | 3320 | 10 | 332 | BY-S28-03 | Bayou | 2026-07-20 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-003032 | 3970 | 10 | 397 | PR-S18-06 | Prairie | 2026-07-20 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-003033 | 2132 | 13 | 164 | PR-S07-02 | Prairie | 2026-07-20 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-003034 | 976 | 8 | 122 | CR-S07-07 | Crossroads | 2026-07-20 | 16 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003035 | 808 | 4 | 202 | CR-S27-04 | Crossroads | 2026-07-20 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003036 | 15566 | 86 | 181 | PR-S04-01 | Prairie | 2026-07-20 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003037 | 47092 | 386 | 122 | PR-S03-04 | Prairie | 2026-07-20 | 19 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003038 | 86940 | 945 | 92 | BY-S01-02 | Bayou | 2026-07-20 | 21 | Vegetation | Substation breaker | Forced | None
OE-26-003039 | 2058 | 7 | 294 | PR-S17-01 | Prairie | 2026-07-20 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003040 | 511 | 7 | 73 | BY-S27-06 | Bayou | 2026-07-20 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003041 | 6192 | 36 | 172 | CR-S26-01 | Crossroads | 2026-07-20 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003042 | 2008 | 8 | 251 | HB-S15-02 | Harbor | 2026-07-20 | 23 | Animal | Transformer fuse | Forced | None
OE-26-003043 | 3804 | 12 | 317 | PR-S03-04 | Prairie | 2026-07-21 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-26-003044 | 3872 | 8 | 484 | PR-S04-02 | Prairie | 2026-07-21 | 3 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003045 | 1240 | 10 | 124 | CR-S05-01 | Crossroads | 2026-07-21 | 8 | Animal | Transformer fuse | Forced | None
OE-26-003046 | 884 | 4 | 221 | BY-S30-03 | Bayou | 2026-07-21 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003047 | 1001 | 13 | 77 | CR-S05-03 | Crossroads | 2026-07-21 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003048 | 3640 | 40 | 91 | BY-S06-03 | Bayou | 2026-07-21 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003049 | 6765 | 55 | 123 | CR-S06-01 | Crossroads | 2026-07-21 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003050 | 33664 | 526 | 64 | PR-S14-01 | Prairie | 2026-07-21 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003051 | 26933 | 1171 | 23 | HB-S09-05 | Harbor | 2026-07-21 | 13 | Animal | Substation breaker | Forced | None
OE-26-003052 | 57938 | 491 | 118 | CR-S10-02 | Crossroads | 2026-07-21 | 14 | Animal | Feeder recloser | Forced | None
OE-26-003053 | 1305 | 9 | 145 | CR-S23-01 | Crossroads | 2026-07-21 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003054 | 412 | 4 | 103 | CR-S26-04 | Crossroads | 2026-07-21 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003055 | 185 | 1 | 185 | PR-S01-05 | Prairie | 2026-07-21 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003056 | 1127 | 7 | 161 | CR-S14-06 | Crossroads | 2026-07-21 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003057 | 3410 | 31 | 110 | CR-S10-01 | Crossroads | 2026-07-21 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003058 | 3576 | 12 | 298 | PR-S07-03 | Prairie | 2026-07-21 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-003059 | 19200 | 400 | 48 | BY-S11-03 | Bayou | 2026-07-21 | 18 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-003060 | 17466 | 123 | 142 | HB-S09-05 | Harbor | 2026-07-21 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003061 | 480 | 10 | 48 | HB-S08-04 | Harbor | 2026-07-21 | 21 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003062 | 16116 | 474 | 34 | CR-S27-01 | Crossroads | 2026-07-22 | 2 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003063 | 140304 | 1264 | 111 | BY-S09-03 | Bayou | 2026-07-22 | 5 | Animal | Substation breaker | Forced | None
OE-26-003064 | 3738 | 42 | 89 | HB-S09-02 | Harbor | 2026-07-22 | 6 | Weather - wind | Lateral fuse | Forced | None
OE-26-003065 | 2310 | 11 | 210 | BY-S23-03 | Bayou | 2026-07-22 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003066 | 790 | 5 | 158 | CR-S25-03 | Crossroads | 2026-07-22 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-003067 | 378 | 3 | 126 | CR-S14-01 | Crossroads | 2026-07-22 | 10 | Animal | Transformer fuse | Forced | None
OE-26-003068 | 52520 | 520 | 101 | HB-S10-02 | Harbor | 2026-07-22 | 11 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-003069 | 1408 | 8 | 176 | PR-S04-02 | Prairie | 2026-07-22 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-003070 | 500 | 10 | 50 | CR-S14-06 | Crossroads | 2026-07-22 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003071 | 19364 | 103 | 188 | PR-S08-03 | Prairie | 2026-07-22 | 14 | Animal | Lateral fuse | Forced | None
OE-26-003072 | 1134 | 9 | 126 | CR-S20-03 | Crossroads | 2026-07-22 | 16 | Weather - wind | Transformer fuse | Forced | None
OE-26-003073 | 346 | 2 | 173 | BY-S15-02 | Bayou | 2026-07-22 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003074 | 252315 | 1335 | 189 | CR-S07-03 | Crossroads | 2026-07-22 | 18 | Vegetation | Feeder recloser | Forced | None
OE-26-003075 | 1443 | 13 | 111 | CR-S09-03 | Crossroads | 2026-07-22 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003076 | 9520 | 28 | 340 | PR-S05-01 | Prairie | 2026-07-22 | 18 | Animal | Lateral fuse | Forced | None
OE-26-003077 | 2380 | 14 | 170 | BY-S15-05 | Bayou | 2026-07-22 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003078 | 2960 | 40 | 74 | HB-S10-01 | Harbor | 2026-07-22 | 23 | Animal | Lateral fuse | Forced | None
OE-26-003079 | 66708 | 306 | 218 | HB-S10-03 | Harbor | 2026-07-22 | 23 | Unknown | Lateral fuse | Forced | None
OE-26-003080 | 5760 | 480 | 12 | CR-S13-05 | Crossroads | 2026-07-23 | 5 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003081 | 1288 | 8 | 161 | CR-S23-01 | Crossroads | 2026-07-23 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003082 | 800 | 40 | 20 | BY-S24-02 | Bayou | 2026-07-23 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003083 | 522 | 3 | 174 | PR-S15-03 | Prairie | 2026-07-23 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003084 | 1652 | 14 | 118 | HB-S14-03 | Harbor | 2026-07-23 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003085 | 2002 | 14 | 143 | BY-S17-02 | Bayou | 2026-07-23 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-003086 | 11280 | 235 | 48 | CR-S02-01 | Crossroads | 2026-07-23 | 12 | Weather - lightning | IGSD-isolated section | Forced | None
OE-26-003087 | 8190 | 45 | 182 | BY-S06-03 | Bayou | 2026-07-23 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-003088 | 1040 | 10 | 104 | HB-S07-04 | Harbor | 2026-07-23 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-003089 | 12586 | 203 | 62 | PR-S13-03 | Prairie | 2026-07-23 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-26-003090 | 1580 | 4 | 395 | PR-S15-06 | Prairie | 2026-07-23 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003091 | 2114 | 14 | 151 | CR-S18-06 | Crossroads | 2026-07-23 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-003092 | 58905 | 1683 | 35 | BY-S29-01 | Bayou | 2026-07-23 | 20 | Vegetation | IGSD-isolated section | Forced | None
OE-26-003093 | 6688 | 11 | 608 | CR-S05-03 | Crossroads | 2026-07-23 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003094 | 9515 | 55 | 173 | BY-S23-01 | Bayou | 2026-07-23 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-003095 | 3850 | 11 | 350 | HB-S20-02 | Harbor | 2026-07-23 | 21 | Animal | Transformer fuse | Forced | None
OE-26-003096 | 39140 | 380 | 103 | PR-S18-06 | Prairie | 2026-07-24 | 0 | Unknown | Feeder recloser | Forced | None
OE-26-003097 | 79668 | 2213 | 36 | HB-S02-03 | Harbor | 2026-07-24 | 1 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-003098 | 1606 | 11 | 146 | BY-S10-01 | Bayou | 2026-07-24 | 2 | Vegetation | Transformer fuse | Forced | None
OE-26-003099 | 18816 | 112 | 168 | HB-S10-02 | Harbor | 2026-07-24 | 5 | Animal | Lateral fuse | Forced | None
OE-26-003100 | 32558 | 146 | 223 | BY-S25-05 | Bayou | 2026-07-24 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003101 | 33998 | 178 | 191 | CR-S09-01 | Crossroads | 2026-07-24 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-003102 | 104544 | 726 | 144 | CR-S06-03 | Crossroads | 2026-07-24 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003103 | 10919 | 61 | 179 | PR-S06-02 | Prairie | 2026-07-24 | 11 | Unknown | Lateral fuse | Forced | None
OE-26-003104 | 4579 | 19 | 241 | CR-S03-01 | Crossroads | 2026-07-24 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003105 | 157 | 1 | 157 | CR-S14-06 | Crossroads | 2026-07-24 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-003106 | 2112 | 12 | 176 | CR-S26-05 | Crossroads | 2026-07-24 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-003107 | 10140 | 39 | 260 | BY-S10-05 | Bayou | 2026-07-24 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003108 | 9344 | 128 | 73 | BY-S23-01 | Bayou | 2026-07-24 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003109 | 756 | 7 | 108 | CR-S32-04 | Crossroads | 2026-07-24 | 14 | Unknown | Transformer fuse | Forced | None
OE-26-003110 | 97008 | 1128 | 86 | CR-S18-04 | Crossroads | 2026-07-24 | 15 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003111 | 708 | 4 | 177 | CR-S05-01 | Crossroads | 2026-07-24 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003112 | 4556 | 34 | 134 | BY-S06-01 | Bayou | 2026-07-24 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003113 | 15400 | 154 | 100 | BY-S15-01 | Bayou | 2026-07-24 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003114 | 7052 | 86 | 82 | BY-S20-02 | Bayou | 2026-07-25 | 3 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003115 | 66397 | 991 | 67 | PR-S10-03 | Prairie | 2026-07-25 | 5 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003116 | 232 | 1 | 232 | BY-S23-03 | Bayou | 2026-07-25 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003117 | 33858 | 162 | 209 | BY-S12-02 | Bayou | 2026-07-25 | 8 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003118 | 42780 | 115 | 372 | PR-S18-03 | Prairie | 2026-07-25 | 8 | Animal | Lateral fuse | Forced | None
OE-26-003119 | 504 | 12 | 42 | BY-S03-01 | Bayou | 2026-07-25 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003120 | 3321 | 41 | 81 | CR-S04-01 | Crossroads | 2026-07-25 | 9 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003121 | 205233 | 1011 | 203 | BY-S06-02 | Bayou | 2026-07-25 | 10 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003122 | 2340 | 12 | 195 | CR-S09-01 | Crossroads | 2026-07-25 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003123 | 124 | 2 | 62 | BY-S22-01 | Bayou | 2026-07-25 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003124 | 3601 | 13 | 277 | PR-S15-01 | Prairie | 2026-07-25 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003125 | 1188 | 6 | 198 | BY-S19-02 | Bayou | 2026-07-25 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-003126 | 3519 | 23 | 153 | HB-S17-03 | Harbor | 2026-07-25 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003127 | 71514 | 522 | 137 | BY-S10-02 | Bayou | 2026-07-25 | 15 | Vegetation | Feeder recloser | Forced | None
OE-26-003128 | 159 | 3 | 53 | CR-S12-03 | Crossroads | 2026-07-25 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-003129 | 1735 | 5 | 347 | BY-S06-02 | Bayou | 2026-07-25 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003130 | 4292 | 74 | 58 | BY-S29-05 | Bayou | 2026-07-25 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003131 | 4940 | 52 | 95 | HB-S02-02 | Harbor | 2026-07-25 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003132 | 108576 | 624 | 174 | BY-S18-05 | Bayou | 2026-07-25 | 20 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-003133 | 188 | 2 | 94 | CR-S32-04 | Crossroads | 2026-07-25 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003134 | 95432 | 604 | 158 | HB-S15-03 | Harbor | 2026-07-25 | 23 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-003135 | 1350 | 9 | 150 | BY-S26-05 | Bayou | 2026-07-26 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003136 | 13446 | 81 | 166 | BY-S18-04 | Bayou | 2026-07-26 | 3 | Vegetation | Lateral fuse | Forced | None
OE-26-003137 | 1963 | 13 | 151 | BY-S19-02 | Bayou | 2026-07-26 | 12 | Animal | Transformer fuse | Forced | None
OE-26-003138 | 4394 | 13 | 338 | PR-S18-04 | Prairie | 2026-07-26 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003139 | 662 | 2 | 331 | PR-S19-05 | Prairie | 2026-07-26 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003140 | 5625 | 45 | 125 | CR-S16-06 | Crossroads | 2026-07-26 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003141 | 8804 | 124 | 71 | CR-S10-03 | Crossroads | 2026-07-26 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003142 | 53248 | 1024 | 52 | CR-S01-03 | Crossroads | 2026-07-26 | 18 | Animal | Feeder recloser | Forced | None
OE-26-003143 | 10710 | 126 | 85 | CR-S28-02 | Crossroads | 2026-07-26 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003144 | 318 | 2 | 159 | PR-S07-06 | Prairie | 2026-07-26 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-003145 | 25776 | 1074 | 24 | BY-S21-01 | Bayou | 2026-07-26 | 20 | Animal | Feeder recloser | Forced | None
OE-26-003146 | 1116 | 9 | 124 | CR-S20-05 | Crossroads | 2026-07-27 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003147 | 944 | 4 | 236 | BY-S02-01 | Bayou | 2026-07-27 | 2 | Vegetation | Transformer fuse | Forced | None
OE-26-003148 | 6000 | 75 | 80 | BY-S26-01 | Bayou | 2026-07-27 | 4 | Weather - wind | Lateral fuse | Forced | None
OE-26-003149 | 4680 | 26 | 180 | BY-S04-03 | Bayou | 2026-07-27 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003150 | 747 | 9 | 83 | BY-S19-01 | Bayou | 2026-07-27 | 8 | Unknown | Transformer fuse | Forced | None
OE-26-003151 | 1152 | 12 | 96 | CR-S18-04 | Crossroads | 2026-07-27 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003152 | 2784 | 12 | 232 | CR-S18-02 | Crossroads | 2026-07-27 | 9 | Animal | Transformer fuse | Forced | None
OE-26-003153 | 6708 | 39 | 172 | BY-S04-01 | Bayou | 2026-07-27 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003154 | 4920 | 60 | 82 | BY-S20-01 | Bayou | 2026-07-27 | 11 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003155 | 81575 | 325 | 251 | BY-S26-02 | Bayou | 2026-07-27 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003156 | 1360 | 8 | 170 | PR-S10-03 | Prairie | 2026-07-27 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003157 | 595 | 5 | 119 | BY-S10-05 | Bayou | 2026-07-27 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-003158 | 2511 | 9 | 279 | BY-S21-02 | Bayou | 2026-07-27 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003159 | 516 | 2 | 258 | PR-S03-05 | Prairie | 2026-07-27 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003160 | 2070 | 23 | 90 | CR-S05-01 | Crossroads | 2026-07-27 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003161 | 20670 | 530 | 39 | CR-S08-03 | Crossroads | 2026-07-27 | 16 | Weather - wind | Feeder recloser | Forced | None
OE-26-003162 | 1020 | 10 | 102 | BY-S21-04 | Bayou | 2026-07-27 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-003163 | 560 | 5 | 112 | CR-S07-05 | Crossroads | 2026-07-27 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003164 | 910 | 7 | 130 | CR-S05-03 | Crossroads | 2026-07-27 | 21 | Vegetation | Transformer fuse | Forced | None
OE-26-003165 | 462 | 3 | 154 | HB-S17-01 | Harbor | 2026-07-27 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-26-003166 | 1694 | 14 | 121 | CR-S22-03 | Crossroads | 2026-07-27 | 23 | Unknown | Transformer fuse | Forced | None
OE-26-003167 | 174 | 2 | 87 | BY-S04-01 | Bayou | 2026-07-28 | 7 | Animal | Transformer fuse | Forced | None
OE-26-003168 | 7020 | 26 | 270 | CR-S30-02 | Crossroads | 2026-07-28 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003169 | 4033 | 37 | 109 | BY-S29-04 | Bayou | 2026-07-28 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003170 | 11921 | 91 | 131 | PR-S19-03 | Prairie | 2026-07-28 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003171 | 9843 | 51 | 193 | PR-S14-04 | Prairie | 2026-07-28 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003172 | 6864 | 33 | 208 | CR-S10-03 | Crossroads | 2026-07-28 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003173 | 13206 | 71 | 186 | HB-S09-02 | Harbor | 2026-07-28 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-26-003174 | 1575 | 9 | 175 | CR-S14-06 | Crossroads | 2026-07-28 | 17 | Animal | Transformer fuse | Forced | None
OE-26-003175 | 1750 | 14 | 125 | BY-S18-02 | Bayou | 2026-07-28 | 18 | Animal | Transformer fuse | Forced | None
OE-26-003176 | 1270 | 5 | 254 | BY-S26-02 | Bayou | 2026-07-28 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003177 | 1352 | 13 | 104 | HB-S12-03 | Harbor | 2026-07-28 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-003178 | 546 | 6 | 91 | BY-S23-05 | Bayou | 2026-07-28 | 19 | Animal | Transformer fuse | Forced | None
OE-26-003179 | 9408 | 56 | 168 | BY-S27-03 | Bayou | 2026-07-28 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003180 | 287 | 1 | 287 | BY-S13-05 | Bayou | 2026-07-28 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003181 | 38180 | 166 | 230 | PR-S01-03 | Prairie | 2026-07-28 | 20 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003182 | 310 | 2 | 155 | HB-S14-01 | Harbor | 2026-07-28 | 21 | Animal | Transformer fuse | Forced | None
OE-26-003183 | 3922 | 106 | 37 | HB-S01-05 | Harbor | 2026-07-28 | 22 | Weather - wind | Lateral fuse | Forced | None
OE-26-003184 | 1339 | 13 | 103 | HB-S11-01 | Harbor | 2026-07-28 | 22 | Weather - wind | Transformer fuse | Forced | None
OE-26-003185 | 5859 | 31 | 189 | CR-S26-02 | Crossroads | 2026-07-29 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003186 | 27664 | 304 | 91 | PR-S13-05 | Prairie | 2026-07-29 | 4 | Weather - wind | Feeder recloser | Forced | None
OE-26-003187 | 30456 | 376 | 81 | BY-S11-03 | Bayou | 2026-07-29 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-003188 | 1742 | 13 | 134 | CR-S08-06 | Crossroads | 2026-07-29 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003189 | 227010 | 1974 | 115 | CR-S12-01 | Crossroads | 2026-07-29 | 9 | Equipment - underground | Substation breaker | Forced | None
OE-26-003190 | 6142 | 74 | 83 | BY-S19-01 | Bayou | 2026-07-29 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-003191 | 736 | 8 | 92 | BY-S23-02 | Bayou | 2026-07-29 | 11 | Unknown | Transformer fuse | Forced | None
OE-26-003192 | 309 | 3 | 103 | CR-S32-02 | Crossroads | 2026-07-29 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003193 | 314 | 2 | 157 | HB-S04-01 | Harbor | 2026-07-29 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003194 | 57769 | 1409 | 41 | BY-S09-04 | Bayou | 2026-07-29 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-003195 | 2398 | 22 | 109 | CR-S16-05 | Crossroads | 2026-07-29 | 14 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003196 | 1974 | 21 | 94 | HB-S07-02 | Harbor | 2026-07-29 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-003197 | 21948 | 372 | 59 | CR-S05-02 | Crossroads | 2026-07-29 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003198 | 125 | 1 | 125 | BY-S03-01 | Bayou | 2026-07-30 | 4 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003199 | 762 | 6 | 127 | CR-S09-03 | Crossroads | 2026-07-30 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003200 | 480 | 8 | 60 | CR-S04-01 | Crossroads | 2026-07-30 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003201 | 11925 | 75 | 159 | CR-S29-03 | Crossroads | 2026-07-30 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003202 | 2160 | 10 | 216 | BY-S29-03 | Bayou | 2026-07-30 | 12 | Vegetation | Transformer fuse | Forced | None
OE-26-003203 | 28767 | 223 | 129 | BY-S01-02 | Bayou | 2026-07-30 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003204 | 294998 | 1219 | 242 | HB-S06-01 | Harbor | 2026-07-30 | 15 | Animal | Substation breaker | Forced | None
OE-26-003205 | 90 | 1 | 90 | PR-S20-01 | Prairie | 2026-07-30 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003206 | 210 | 3 | 70 | HB-S20-03 | Harbor | 2026-07-30 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003207 | 132 | 1 | 132 | BY-S26-02 | Bayou | 2026-07-30 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003208 | 4716 | 18 | 262 | BY-S21-02 | Bayou | 2026-07-30 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-003209 | 2847 | 13 | 219 | HB-S03-03 | Harbor | 2026-07-30 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003210 | 91 | 1 | 91 | CR-S09-03 | Crossroads | 2026-07-31 | 3 | Animal | Transformer fuse | Forced | None
OE-26-003211 | 17145 | 135 | 127 | BY-S21-04 | Bayou | 2026-07-31 | 6 | Vegetation | Lateral fuse | Forced | None
OE-26-003212 | 2568 | 12 | 214 | CR-S27-03 | Crossroads | 2026-07-31 | 6 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003213 | 2296 | 8 | 287 | PR-S02-03 | Prairie | 2026-07-31 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003214 | 3332 | 34 | 98 | PR-S19-01 | Prairie | 2026-07-31 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003215 | 9100 | 52 | 175 | BY-S26-02 | Bayou | 2026-07-31 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003216 | 2976 | 16 | 186 | HB-S02-03 | Harbor | 2026-07-31 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003217 | 2808 | 9 | 312 | PR-S01-02 | Prairie | 2026-07-31 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-003218 | 2492 | 14 | 178 | CR-S19-04 | Crossroads | 2026-07-31 | 14 | Weather - wind | Transformer fuse | Forced | None
OE-26-003219 | 21952 | 98 | 224 | HB-S18-01 | Harbor | 2026-07-31 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003220 | 756 | 4 | 189 | CR-S30-07 | Crossroads | 2026-07-31 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003221 | 1269 | 9 | 141 | HB-S05-06 | Harbor | 2026-07-31 | 17 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003222 | 53701 | 647 | 83 | BY-S18-05 | Bayou | 2026-07-31 | 18 | Vegetation | IGSD-isolated section | Forced | None
OE-26-003223 | 1144 | 11 | 104 | BY-S15-03 | Bayou | 2026-07-31 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003224 | 1872 | 12 | 156 | PR-S11-01 | Prairie | 2026-07-31 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-003225 | 14948 | 148 | 101 | HB-S03-01 | Harbor | 2026-07-31 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003226 | 732 | 6 | 122 | HB-S06-02 | Harbor | 2026-08-01 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003227 | 2170 | 10 | 217 | PR-S08-02 | Prairie | 2026-08-01 | 0 | Animal | Transformer fuse | Forced | None
OE-26-003228 | 68834 | 542 | 127 | HB-S17-03 | Harbor | 2026-08-01 | 1 | Weather - wind | Feeder recloser | Forced | None
OE-26-003229 | 56949 | 123 | 463 | HB-S10-02 | Harbor | 2026-08-01 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003230 | 7448 | 56 | 133 | BY-S29-01 | Bayou | 2026-08-01 | 9 | Animal | Lateral fuse | Forced | None
OE-26-003231 | 4950 | 90 | 55 | CR-S09-01 | Crossroads | 2026-08-01 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003232 | 1314 | 9 | 146 | CR-S30-06 | Crossroads | 2026-08-01 | 10 | Unknown | Transformer fuse | Forced | None
OE-26-003233 | 671 | 11 | 61 | HB-S19-04 | Harbor | 2026-08-01 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-003234 | 8968 | 76 | 118 | BY-S03-01 | Bayou | 2026-08-01 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003235 | 28329 | 399 | 71 | CR-S11-01 | Crossroads | 2026-08-01 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003236 | 2320 | 8 | 290 | PR-S07-05 | Prairie | 2026-08-01 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003237 | 3956 | 46 | 86 | BY-S17-04 | Bayou | 2026-08-01 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-003238 | 1180 | 4 | 295 | CR-S14-05 | Crossroads | 2026-08-01 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003239 | 9632 | 32 | 301 | PR-S14-01 | Prairie | 2026-08-01 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003240 | 2004 | 12 | 167 | BY-S02-01 | Bayou | 2026-08-01 | 16 | Animal | Transformer fuse | Forced | None
OE-26-003241 | 9120 | 95 | 96 | PR-S18-02 | Prairie | 2026-08-01 | 16 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003242 | 6820 | 55 | 124 | BY-S08-03 | Bayou | 2026-08-01 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003243 | 2088 | 12 | 174 | BY-S15-02 | Bayou | 2026-08-01 | 17 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003244 | 105 | 1 | 105 | BY-S26-03 | Bayou | 2026-08-01 | 17 | Animal | Transformer fuse | Forced | None
OE-26-003245 | 550 | 2 | 275 | PR-S02-03 | Prairie | 2026-08-01 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003246 | 31737 | 149 | 213 | PR-S16-04 | Prairie | 2026-08-01 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-003247 | 1896 | 8 | 237 | CR-S27-01 | Crossroads | 2026-08-01 | 19 | Animal | Transformer fuse | Forced | None
OE-26-003248 | 492 | 12 | 41 | CR-S17-02 | Crossroads | 2026-08-01 | 20 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003249 | 10640 | 112 | 95 | HB-S15-03 | Harbor | 2026-08-01 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003250 | 13902 | 42 | 331 | CR-S25-03 | Crossroads | 2026-08-01 | 22 | Animal | Lateral fuse | Forced | None
OE-26-003251 | 4452 | 53 | 84 | CR-S06-02 | Crossroads | 2026-08-02 | 6 | Unknown | Lateral fuse | Forced | None
OE-26-003252 | 166 | 1 | 166 | HB-S17-01 | Harbor | 2026-08-02 | 6 | Unknown | Transformer fuse | Forced | None
OE-26-003253 | 800 | 8 | 100 | BY-S10-03 | Bayou | 2026-08-02 | 7 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003254 | 1536 | 12 | 128 | BY-S24-04 | Bayou | 2026-08-02 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-003255 | 1495 | 13 | 115 | BY-S08-01 | Bayou | 2026-08-02 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-003256 | 2964 | 12 | 247 | BY-S16-01 | Bayou | 2026-08-02 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003257 | 11248 | 592 | 19 | CR-S07-06 | Crossroads | 2026-08-02 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003258 | 256 | 2 | 128 | PR-S19-04 | Prairie | 2026-08-02 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003259 | 45253 | 767 | 59 | PR-S05-03 | Prairie | 2026-08-02 | 15 | Weather - lightning | Substation breaker | Forced | None
OE-26-003260 | 513 | 3 | 171 | PR-S08-02 | Prairie | 2026-08-02 | 15 | Animal | Transformer fuse | Forced | None
OE-26-003261 | 11295 | 45 | 251 | PR-S12-01 | Prairie | 2026-08-02 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-003262 | 48050 | 775 | 62 | BY-S03-02 | Bayou | 2026-08-02 | 18 | Vegetation | Feeder recloser | Forced | None
OE-26-003263 | 1660 | 4 | 415 | PR-S11-02 | Prairie | 2026-08-02 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-003264 | 63479 | 247 | 257 | CR-S04-03 | Crossroads | 2026-08-02 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003265 | 1443 | 13 | 111 | HB-S07-02 | Harbor | 2026-08-02 | 20 | Unknown | Transformer fuse | Forced | None
OE-26-003266 | 1824 | 38 | 48 | CR-S14-01 | Crossroads | 2026-08-02 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003267 | 1694 | 14 | 121 | HB-S09-02 | Harbor | 2026-08-03 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003268 | 18768 | 68 | 276 | BY-S20-01 | Bayou | 2026-08-03 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003269 | 4029 | 51 | 79 | CR-S20-02 | Crossroads | 2026-08-03 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-003270 | 36025 | 655 | 55 | BY-S20-02 | Bayou | 2026-08-03 | 11 | Animal | Feeder recloser | Forced | None
OE-26-003271 | 24543 | 101 | 243 | CR-S02-01 | Crossroads | 2026-08-03 | 11 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003272 | 26410 | 278 | 95 | CR-S03-02 | Crossroads | 2026-08-03 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003273 | 21681 | 219 | 99 | HB-S16-03 | Harbor | 2026-08-03 | 14 | Vegetation | IGSD-isolated section | Forced | None
OE-26-003274 | 3638 | 17 | 214 | PR-S19-02 | Prairie | 2026-08-03 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-26-003275 | 900 | 25 | 36 | CR-S22-01 | Crossroads | 2026-08-03 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003276 | 14137 | 67 | 211 | PR-S16-03 | Prairie | 2026-08-03 | 17 | Animal | Lateral fuse | Forced | None
OE-26-003277 | 15651 | 111 | 141 | PR-S03-02 | Prairie | 2026-08-03 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003278 | 1248 | 12 | 104 | HB-S14-01 | Harbor | 2026-08-04 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003279 | 56525 | 323 | 175 | BY-S01-02 | Bayou | 2026-08-04 | 8 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-003280 | 22701 | 161 | 141 | BY-S12-04 | Bayou | 2026-08-04 | 8 | Animal | Lateral fuse | Forced | None
OE-26-003281 | 984 | 8 | 123 | BY-S19-04 | Bayou | 2026-08-04 | 8 | Animal | Transformer fuse | Forced | None
OE-26-003282 | 7200 | 45 | 160 | CR-S12-03 | Crossroads | 2026-08-04 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003283 | 5408 | 52 | 104 | PR-S15-03 | Prairie | 2026-08-04 | 9 | Vegetation | Lateral fuse | Forced | None
OE-26-003284 | 6162 | 26 | 237 | CR-S04-03 | Crossroads | 2026-08-04 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003285 | 410 | 5 | 82 | BY-S20-01 | Bayou | 2026-08-04 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-003286 | 1269 | 9 | 141 | HB-S09-01 | Harbor | 2026-08-04 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-003287 | 26696 | 188 | 142 | PR-S11-02 | Prairie | 2026-08-04 | 13 | Animal | Lateral fuse | Forced | None
OE-26-003288 | 620 | 4 | 155 | PR-S03-03 | Prairie | 2026-08-04 | 16 | Unknown | Transformer fuse | Forced | None
OE-26-003289 | 6256 | 92 | 68 | PR-S07-04 | Prairie | 2026-08-04 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-003290 | 14674 | 58 | 253 | PR-S13-06 | Prairie | 2026-08-04 | 17 | Weather - wind | Lateral fuse | Forced | None
OE-26-003291 | 1802 | 34 | 53 | HB-S15-02 | Harbor | 2026-08-04 | 19 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003292 | 4680 | 156 | 30 | PR-S13-03 | Prairie | 2026-08-04 | 20 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003293 | 3225 | 25 | 129 | HB-S15-02 | Harbor | 2026-08-04 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-003294 | 477 | 3 | 159 | BY-S18-05 | Bayou | 2026-08-04 | 23 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003295 | 14363 | 53 | 271 | CR-S26-02 | Crossroads | 2026-08-04 | 23 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003296 | 1060 | 4 | 265 | HB-S06-01 | Harbor | 2026-08-05 | 7 | Animal | Transformer fuse | Forced | None
OE-26-003297 | 675 | 5 | 135 | HB-S20-01 | Harbor | 2026-08-05 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-003298 | 20043 | 153 | 131 | BY-S21-04 | Bayou | 2026-08-05 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003299 | 7956 | 26 | 306 | CR-S12-01 | Crossroads | 2026-08-05 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003300 | 17759 | 413 | 43 | CR-S05-03 | Crossroads | 2026-08-05 | 12 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003301 | 12090 | 30 | 403 | PR-S06-02 | Prairie | 2026-08-05 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-003302 | 894 | 6 | 149 | BY-S22-04 | Bayou | 2026-08-05 | 13 | Animal | Transformer fuse | Forced | None
OE-26-003303 | 452 | 4 | 113 | PR-S10-03 | Prairie | 2026-08-05 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003304 | 3680 | 23 | 160 | BY-S29-05 | Bayou | 2026-08-05 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-003305 | 1386 | 14 | 99 | CR-S16-02 | Crossroads | 2026-08-05 | 15 | Animal | Transformer fuse | Forced | None
OE-26-003306 | 1580 | 4 | 395 | HB-S05-01 | Harbor | 2026-08-05 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003307 | 4150 | 83 | 50 | PR-S01-02 | Prairie | 2026-08-05 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-003308 | 448 | 8 | 56 | BY-S06-03 | Bayou | 2026-08-05 | 16 | Animal | Transformer fuse | Forced | None
OE-26-003309 | 1860 | 12 | 155 | BY-S04-02 | Bayou | 2026-08-05 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-003310 | 700 | 10 | 70 | CR-S12-01 | Crossroads | 2026-08-05 | 18 | Animal | Transformer fuse | Forced | None
OE-26-003311 | 1750 | 10 | 175 | HB-S16-05 | Harbor | 2026-08-05 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-003312 | 9879 | 111 | 89 | PR-S15-04 | Prairie | 2026-08-05 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-003313 | 342 | 6 | 57 | CR-S16-01 | Crossroads | 2026-08-06 | 0 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003314 | 5474 | 14 | 391 | PR-S05-01 | Prairie | 2026-08-06 | 1 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003315 | 1862 | 14 | 133 | CR-S12-02 | Crossroads | 2026-08-06 | 2 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003316 | 37791 | 117 | 323 | BY-S22-03 | Bayou | 2026-08-06 | 6 | Animal | Lateral fuse | Forced | None
OE-26-003317 | 334 | 2 | 167 | PR-S12-01 | Prairie | 2026-08-06 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-003318 | 2048 | 8 | 256 | BY-S25-02 | Bayou | 2026-08-06 | 10 | Animal | Transformer fuse | Forced | None
OE-26-003319 | 5520 | 40 | 138 | CR-S22-01 | Crossroads | 2026-08-06 | 10 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003320 | 9676 | 41 | 236 | PR-S01-02 | Prairie | 2026-08-06 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003321 | 55960 | 1399 | 40 | CR-S19-04 | Crossroads | 2026-08-06 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003322 | 1280 | 8 | 160 | HB-S18-04 | Harbor | 2026-08-06 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-26-003323 | 1730 | 10 | 173 | BY-S10-03 | Bayou | 2026-08-06 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-003324 | 636 | 12 | 53 | CR-S04-05 | Crossroads | 2026-08-06 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003325 | 23595 | 165 | 143 | PR-S09-02 | Prairie | 2026-08-06 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-003326 | 3055 | 13 | 235 | BY-S09-03 | Bayou | 2026-08-06 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-003327 | 2232 | 9 | 248 | BY-S09-04 | Bayou | 2026-08-06 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003328 | 209380 | 1102 | 190 | CR-S04-06 | Crossroads | 2026-08-06 | 16 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003329 | 2530 | 23 | 110 | CR-S07-01 | Crossroads | 2026-08-06 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003330 | 62457 | 573 | 109 | HB-S01-05 | Harbor | 2026-08-06 | 17 | Vegetation | IGSD-isolated section | Forced | None
OE-26-003331 | 3752 | 67 | 56 | HB-S02-01 | Harbor | 2026-08-06 | 18 | Animal | Lateral fuse | Forced | None
OE-26-003332 | 2304 | 9 | 256 | HB-S18-03 | Harbor | 2026-08-06 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-003333 | 696 | 6 | 116 | BY-S01-02 | Bayou | 2026-08-06 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003334 | 333 | 3 | 111 | BY-S07-04 | Bayou | 2026-08-06 | 20 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003335 | 1380 | 10 | 138 | CR-S09-05 | Crossroads | 2026-08-06 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003336 | 48461 | 301 | 161 | PR-S14-01 | Prairie | 2026-08-06 | 22 | Weather - wind | IGSD-isolated section | Forced | None
OE-26-003337 | 4350 | 10 | 435 | PR-S08-02 | Prairie | 2026-08-07 | 8 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003338 | 9916 | 268 | 37 | HB-S13-01 | Harbor | 2026-08-07 | 9 | Vegetation | IGSD-isolated section | Forced | None
OE-26-003339 | 246 | 3 | 82 | HB-S05-03 | Harbor | 2026-08-07 | 10 | Animal | Transformer fuse | Forced | None
OE-26-003340 | 7150 | 26 | 275 | BY-S02-01 | Bayou | 2026-08-07 | 11 | Animal | Lateral fuse | Forced | None
OE-26-003341 | 948 | 6 | 158 | BY-S09-04 | Bayou | 2026-08-07 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003342 | 155213 | 577 | 269 | PR-S01-01 | Prairie | 2026-08-07 | 13 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003343 | 2959 | 11 | 269 | PR-S20-01 | Prairie | 2026-08-07 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003344 | 2793 | 7 | 399 | PR-S08-01 | Prairie | 2026-08-07 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003345 | 4148 | 61 | 68 | BY-S05-01 | Bayou | 2026-08-07 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-003346 | 15300 | 450 | 34 | BY-S17-03 | Bayou | 2026-08-07 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-003347 | 19470 | 110 | 177 | PR-S09-02 | Prairie | 2026-08-07 | 16 | Unknown | Lateral fuse | Forced | None
OE-26-003348 | 172 | 1 | 172 | BY-S26-01 | Bayou | 2026-08-07 | 19 | Vegetation | Transformer fuse | Forced | None
OE-26-003349 | 788 | 4 | 197 | PR-S18-04 | Prairie | 2026-08-07 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003350 | 396 | 4 | 99 | BY-S15-06 | Bayou | 2026-08-07 | 20 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003351 | 790 | 5 | 158 | BY-S30-02 | Bayou | 2026-08-07 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-003352 | 16236 | 66 | 246 | HB-S18-01 | Harbor | 2026-08-07 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003353 | 97370 | 910 | 107 | PR-S17-01 | Prairie | 2026-08-07 | 20 | Vegetation | Feeder recloser | Forced | None
OE-26-003354 | 3900 | 39 | 100 | BY-S23-03 | Bayou | 2026-08-07 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-003355 | 15570 | 173 | 90 | CR-S04-01 | Crossroads | 2026-08-08 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003356 | 120 | 1 | 120 | CR-S09-02 | Crossroads | 2026-08-08 | 5 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003357 | 1692 | 12 | 141 | BY-S15-06 | Bayou | 2026-08-08 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-003358 | 402 | 3 | 134 | BY-S25-04 | Bayou | 2026-08-08 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003359 | 1017 | 9 | 113 | CR-S30-03 | Crossroads | 2026-08-08 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003360 | 134900 | 355 | 380 | PR-S03-02 | Prairie | 2026-08-08 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003361 | 99288 | 1182 | 84 | BY-S12-03 | Bayou | 2026-08-08 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003362 | 30800 | 88 | 350 | BY-S12-02 | Bayou | 2026-08-08 | 13 | Animal | Lateral fuse | Forced | None
OE-26-003363 | 665 | 5 | 133 | BY-S23-01 | Bayou | 2026-08-08 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003364 | 420 | 4 | 105 | CR-S30-04 | Crossroads | 2026-08-08 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-003365 | 6716 | 73 | 92 | HB-S13-02 | Harbor | 2026-08-08 | 13 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003366 | 875 | 5 | 175 | BY-S14-02 | Bayou | 2026-08-08 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-003367 | 976 | 8 | 122 | CR-S24-01 | Crossroads | 2026-08-08 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003368 | 109 | 1 | 109 | HB-S10-01 | Harbor | 2026-08-08 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003369 | 915 | 5 | 183 | CR-S26-04 | Crossroads | 2026-08-08 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-003370 | 8056 | 38 | 212 | PR-S19-02 | Prairie | 2026-08-08 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-003371 | 114 | 1 | 114 | BY-S23-01 | Bayou | 2026-08-08 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003372 | 15640 | 115 | 136 | BY-S26-06 | Bayou | 2026-08-08 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003373 | 2880 | 10 | 288 | BY-S09-04 | Bayou | 2026-08-08 | 20 | Weather - wind | Transformer fuse | Forced | None
OE-26-003374 | 1580 | 5 | 316 | PR-S11-01 | Prairie | 2026-08-08 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003375 | 16432 | 316 | 52 | CR-S13-04 | Crossroads | 2026-08-09 | 0 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003376 | 10750 | 50 | 215 | CR-S28-04 | Crossroads | 2026-08-09 | 1 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003377 | 13800 | 46 | 300 | CR-S07-02 | Crossroads | 2026-08-09 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-26-003378 | 875 | 7 | 125 | CR-S27-04 | Crossroads | 2026-08-09 | 5 | Vegetation | Transformer fuse | Forced | None
OE-26-003379 | 1798 | 58 | 31 | HB-S01-05 | Harbor | 2026-08-09 | 6 | Animal | Lateral fuse | Forced | None
OE-26-003380 | 585 | 3 | 195 | HB-S19-04 | Harbor | 2026-08-09 | 6 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003381 | 2656 | 32 | 83 | HB-S18-01 | Harbor | 2026-08-09 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003382 | 1773 | 9 | 197 | PR-S08-03 | Prairie | 2026-08-09 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-003383 | 9858 | 106 | 93 | CR-S09-03 | Crossroads | 2026-08-09 | 9 | Animal | Lateral fuse | Forced | None
OE-26-003384 | 10788 | 124 | 87 | BY-S15-02 | Bayou | 2026-08-09 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003385 | 390 | 2 | 195 | PR-S10-03 | Prairie | 2026-08-09 | 10 | Animal | Transformer fuse | Forced | None
OE-26-003386 | 1943 | 29 | 67 | CR-S32-04 | Crossroads | 2026-08-09 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003387 | 48621 | 853 | 57 | BY-S19-02 | Bayou | 2026-08-09 | 12 | Animal | Feeder recloser | Forced | None
OE-26-003388 | 10584 | 108 | 98 | HB-S08-01 | Harbor | 2026-08-09 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-003389 | 749 | 7 | 107 | BY-S15-06 | Bayou | 2026-08-09 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-003390 | 4977 | 79 | 63 | CR-S07-03 | Crossroads | 2026-08-09 | 13 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003391 | 242004 | 938 | 258 | CR-S08-06 | Crossroads | 2026-08-09 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003392 | 26080 | 160 | 163 | PR-S12-01 | Prairie | 2026-08-09 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003393 | 149632 | 1336 | 112 | BY-S04-01 | Bayou | 2026-08-09 | 15 | Animal | Substation breaker | Forced | None
OE-26-003394 | 1809 | 9 | 201 | BY-S18-05 | Bayou | 2026-08-09 | 16 | Vegetation | Transformer fuse | Forced | None
OE-26-003395 | 18699 | 271 | 69 | BY-S14-01 | Bayou | 2026-08-09 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003396 | 430 | 2 | 215 | BY-S10-01 | Bayou | 2026-08-09 | 18 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003397 | 852 | 4 | 213 | CR-S12-03 | Crossroads | 2026-08-09 | 18 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003398 | 14981 | 211 | 71 | BY-S26-02 | Bayou | 2026-08-09 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-003399 | 141 | 1 | 141 | CR-S32-03 | Crossroads | 2026-08-09 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003400 | 822 | 6 | 137 | CR-S12-02 | Crossroads | 2026-08-09 | 22 | Animal | Transformer fuse | Forced | None
OE-26-003401 | 53025 | 525 | 101 | CR-S04-01 | Crossroads | 2026-08-10 | 8 | Animal | Feeder recloser | Forced | None
OE-26-003402 | 295650 | 1825 | 162 | CR-S27-02 | Crossroads | 2026-08-10 | 9 | Unknown | Feeder recloser | Forced | None
OE-26-003403 | 1575 | 25 | 63 | HB-S14-01 | Harbor | 2026-08-10 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003404 | 2795 | 13 | 215 | BY-S12-04 | Bayou | 2026-08-10 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003405 | 4176 | 36 | 116 | PR-S09-01 | Prairie | 2026-08-10 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003406 | 425 | 5 | 85 | BY-S24-05 | Bayou | 2026-08-10 | 11 | Unknown | Transformer fuse | Forced | None
OE-26-003407 | 5586 | 98 | 57 | BY-S13-03 | Bayou | 2026-08-10 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-003408 | 165540 | 1068 | 155 | BY-S18-04 | Bayou | 2026-08-10 | 12 | Weather - lightning | Feeder recloser | Forced | None
OE-26-003409 | 5600 | 32 | 175 | BY-S07-05 | Bayou | 2026-08-10 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003410 | 66528 | 432 | 154 | CR-S26-04 | Crossroads | 2026-08-10 | 13 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003411 | 10584 | 63 | 168 | BY-S17-03 | Bayou | 2026-08-10 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003412 | 1152 | 9 | 128 | CR-S23-02 | Crossroads | 2026-08-10 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003413 | 67338 | 783 | 86 | PR-S03-05 | Prairie | 2026-08-10 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003414 | 2628 | 12 | 219 | BY-S05-03 | Bayou | 2026-08-10 | 17 | Weather - wind | Transformer fuse | Forced | None
OE-26-003415 | 1278 | 9 | 142 | CR-S07-01 | Crossroads | 2026-08-10 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003416 | 504 | 4 | 126 | HB-S08-05 | Harbor | 2026-08-10 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003417 | 92872 | 1786 | 52 | BY-S29-01 | Bayou | 2026-08-10 | 19 | Vegetation | Feeder recloser | Forced | None
OE-26-003418 | 700 | 5 | 140 | BY-S05-01 | Bayou | 2026-08-10 | 22 | Vegetation | Transformer fuse | Forced | None
OE-26-003419 | 3542 | 11 | 322 | BY-S29-05 | Bayou | 2026-08-10 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003420 | 850 | 10 | 85 | CR-S32-05 | Crossroads | 2026-08-11 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003421 | 41 | 1 | 41 | CR-S15-01 | Crossroads | 2026-08-11 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003422 | 8427 | 53 | 159 | CR-S16-05 | Crossroads | 2026-08-11 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003423 | 3690 | 45 | 82 | CR-S08-06 | Crossroads | 2026-08-11 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003424 | 64020 | 660 | 97 | BY-S28-03 | Bayou | 2026-08-11 | 11 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003425 | 1920 | 60 | 32 | BY-S10-04 | Bayou | 2026-08-11 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-003426 | 1824 | 12 | 152 | CR-S22-04 | Crossroads | 2026-08-11 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003427 | 4147 | 29 | 143 | BY-S24-05 | Bayou | 2026-08-11 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003428 | 352 | 4 | 88 | CR-S27-04 | Crossroads | 2026-08-11 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003429 | 366 | 1 | 366 | PR-S18-06 | Prairie | 2026-08-11 | 14 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003430 | 11650 | 50 | 233 | BY-S07-06 | Bayou | 2026-08-11 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-003431 | 22374 | 678 | 33 | HB-S08-05 | Harbor | 2026-08-11 | 15 | Weather - wind | Feeder recloser | Forced | None
OE-26-003432 | 670 | 5 | 134 | BY-S26-02 | Bayou | 2026-08-11 | 16 | Animal | Transformer fuse | Forced | None
OE-26-003433 | 107113 | 2021 | 53 | BY-S22-04 | Bayou | 2026-08-11 | 17 | Equipment - overhead | Substation breaker | Forced | None
OE-26-003434 | 228 | 2 | 114 | CR-S04-01 | Crossroads | 2026-08-11 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003435 | 2112 | 44 | 48 | CR-S08-05 | Crossroads | 2026-08-11 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-003436 | 624 | 8 | 78 | CR-S17-01 | Crossroads | 2026-08-11 | 21 | Animal | Transformer fuse | Forced | None
OE-26-003437 | 39151 | 833 | 47 | BY-S23-01 | Bayou | 2026-08-12 | 0 | Weather - wind | Feeder recloser | Forced | None
OE-26-003438 | 45396 | 194 | 234 | PR-S09-01 | Prairie | 2026-08-12 | 2 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003439 | 660 | 5 | 132 | CR-S18-05 | Crossroads | 2026-08-12 | 6 | Animal | Transformer fuse | Forced | None
OE-26-003440 | 5934 | 69 | 86 | CR-S23-02 | Crossroads | 2026-08-12 | 7 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003441 | 913 | 11 | 83 | CR-S27-02 | Crossroads | 2026-08-12 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003442 | 1133 | 11 | 103 | BY-S16-01 | Bayou | 2026-08-12 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-003443 | 13720 | 70 | 196 | BY-S16-05 | Bayou | 2026-08-12 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003444 | 6144 | 48 | 128 | CR-S03-02 | Crossroads | 2026-08-12 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003445 | 582 | 3 | 194 | HB-S14-02 | Harbor | 2026-08-12 | 13 | Animal | Transformer fuse | Forced | None
OE-26-003446 | 16539 | 447 | 37 | PR-S06-03 | Prairie | 2026-08-12 | 13 | Animal | Feeder recloser | Forced | None
OE-26-003447 | 14076 | 92 | 153 | HB-S07-03 | Harbor | 2026-08-12 | 15 | Vegetation | Lateral fuse | Forced | None
OE-26-003448 | 30525 | 185 | 165 | HB-S11-03 | Harbor | 2026-08-12 | 15 | Unknown | Lateral fuse | Forced | None
OE-26-003449 | 97650 | 1953 | 50 | HB-S17-03 | Harbor | 2026-08-12 | 16 | Equipment - overhead | Substation breaker | Forced | None
OE-26-003450 | 2212 | 14 | 158 | BY-S15-02 | Bayou | 2026-08-12 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003451 | 24360 | 174 | 140 | BY-S23-03 | Bayou | 2026-08-12 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003452 | 3744 | 78 | 48 | HB-S17-02 | Harbor | 2026-08-12 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003453 | 15326 | 158 | 97 | CR-S27-01 | Crossroads | 2026-08-12 | 18 | Vegetation | Lateral fuse | Forced | None
OE-26-003454 | 68472 | 1902 | 36 | HB-S17-03 | Harbor | 2026-08-12 | 18 | Animal | Substation breaker | Forced | None
OE-26-003455 | 745 | 5 | 149 | BY-S09-03 | Bayou | 2026-08-12 | 21 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003456 | 1323 | 27 | 49 | BY-S10-02 | Bayou | 2026-08-12 | 23 | Vegetation | Lateral fuse | Forced | None
OE-26-003457 | 58625 | 469 | 125 | PR-S06-03 | Prairie | 2026-08-13 | 5 | Vegetation | IGSD-isolated section | Forced | None
OE-26-003458 | 112310 | 1021 | 110 | BY-S11-01 | Bayou | 2026-08-13 | 7 | Weather - wind | Feeder recloser | Forced | None
OE-26-003459 | 2412 | 18 | 134 | BY-S24-03 | Bayou | 2026-08-13 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003460 | 26820 | 894 | 30 | HB-S10-02 | Harbor | 2026-08-13 | 8 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003461 | 1624 | 29 | 56 | PR-S18-05 | Prairie | 2026-08-13 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003462 | 3618 | 67 | 54 | PR-S03-01 | Prairie | 2026-08-13 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003463 | 3938 | 22 | 179 | CR-S17-02 | Crossroads | 2026-08-13 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003464 | 4370 | 38 | 115 | BY-S07-02 | Bayou | 2026-08-13 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003465 | 111723 | 669 | 167 | BY-S23-04 | Bayou | 2026-08-13 | 13 | Vegetation | Feeder recloser | Forced | None
OE-26-003466 | 2100 | 35 | 60 | BY-S21-01 | Bayou | 2026-08-13 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003467 | 237 | 1 | 237 | CR-S26-01 | Crossroads | 2026-08-13 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003468 | 950 | 5 | 190 | HB-S02-01 | Harbor | 2026-08-13 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003469 | 57660 | 620 | 93 | PR-S09-03 | Prairie | 2026-08-13 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-003470 | 1070 | 5 | 214 | PR-S16-02 | Prairie | 2026-08-13 | 14 | Animal | Transformer fuse | Forced | None
OE-26-003471 | 107484 | 2028 | 53 | CR-S21-01 | Crossroads | 2026-08-13 | 15 | Weather - wind | Substation breaker | Forced | None
OE-26-003472 | 972 | 9 | 108 | HB-S05-03 | Harbor | 2026-08-13 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003473 | 834 | 6 | 139 | CR-S03-02 | Crossroads | 2026-08-13 | 19 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003474 | 290 | 1 | 290 | PR-S07-01 | Prairie | 2026-08-13 | 20 | Vegetation | Transformer fuse | Forced | None
OE-26-003475 | 18619 | 433 | 43 | PR-S03-06 | Prairie | 2026-08-13 | 22 | Vehicle or public | Feeder recloser | Forced | None
OE-26-003476 | 5170 | 47 | 110 | BY-S21-05 | Bayou | 2026-08-14 | 0 | Vegetation | Lateral fuse | Forced | None
OE-26-003477 | 2673 | 33 | 81 | BY-S11-02 | Bayou | 2026-08-14 | 5 | Weather - wind | Lateral fuse | Forced | None
OE-26-003478 | 117 | 1 | 117 | CR-S25-03 | Crossroads | 2026-08-14 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003479 | 19240 | 520 | 37 | BY-S10-03 | Bayou | 2026-08-14 | 8 | Weather - wind | Feeder recloser | Forced | None
OE-26-003480 | 1344 | 12 | 112 | HB-S10-01 | Harbor | 2026-08-14 | 8 | Vegetation | Transformer fuse | Forced | None
OE-26-003481 | 3456 | 18 | 192 | BY-S17-04 | Bayou | 2026-08-14 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-003482 | 480 | 4 | 120 | BY-S23-01 | Bayou | 2026-08-14 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003483 | 7956 | 68 | 117 | HB-S07-05 | Harbor | 2026-08-14 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003484 | 1890 | 10 | 189 | PR-S08-02 | Prairie | 2026-08-14 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-003485 | 35980 | 1285 | 28 | BY-S07-02 | Bayou | 2026-08-14 | 13 | Weather - lightning | Feeder recloser | Forced | None
OE-26-003486 | 376 | 2 | 188 | CR-S05-04 | Crossroads | 2026-08-14 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-003487 | 480 | 5 | 96 | CR-S20-01 | Crossroads | 2026-08-14 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003488 | 882 | 7 | 126 | BY-S12-01 | Bayou | 2026-08-14 | 16 | Unknown | Transformer fuse | Forced | None
OE-26-003489 | 5460 | 91 | 60 | CR-S09-03 | Crossroads | 2026-08-14 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-003490 | 11210 | 59 | 190 | BY-S21-02 | Bayou | 2026-08-14 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-003491 | 13386 | 97 | 138 | HB-S01-05 | Harbor | 2026-08-14 | 17 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003492 | 3534 | 93 | 38 | BY-S16-01 | Bayou | 2026-08-14 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-003493 | 3861 | 13 | 297 | BY-S04-01 | Bayou | 2026-08-14 | 22 | Animal | Lateral fuse | Forced | None
OE-26-003494 | 2772 | 33 | 84 | BY-S08-02 | Bayou | 2026-08-15 | 5 | Vegetation | Lateral fuse | Forced | None
OE-26-003495 | 5642 | 62 | 91 | BY-S23-01 | Bayou | 2026-08-15 | 7 | Vegetation | Lateral fuse | Forced | None
OE-26-003496 | 20961 | 411 | 51 | BY-S30-02 | Bayou | 2026-08-15 | 8 | Vegetation | Feeder recloser | Forced | None
OE-26-003497 | 560 | 4 | 140 | CR-S03-03 | Crossroads | 2026-08-15 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003498 | 1134 | 7 | 162 | CR-S27-02 | Crossroads | 2026-08-15 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003499 | 6715 | 85 | 79 | CR-S31-01 | Crossroads | 2026-08-15 | 12 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003500 | 1710 | 9 | 190 | CR-S22-01 | Crossroads | 2026-08-15 | 13 | Weather - wind | Transformer fuse | Forced | None
OE-26-003501 | 1960 | 10 | 196 | BY-S03-03 | Bayou | 2026-08-15 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-003502 | 36448 | 536 | 68 | HB-S16-03 | Harbor | 2026-08-15 | 14 | Weather - wind | Feeder recloser | Forced | None
OE-26-003503 | 668 | 4 | 167 | PR-S18-02 | Prairie | 2026-08-15 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003504 | 22610 | 133 | 170 | HB-S06-02 | Harbor | 2026-08-15 | 16 | Weather - wind | Lateral fuse | Forced | None
OE-26-003505 | 3287 | 19 | 173 | HB-S04-01 | Harbor | 2026-08-15 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003506 | 3150 | 10 | 315 | CR-S27-04 | Crossroads | 2026-08-15 | 18 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003507 | 663 | 3 | 221 | CR-S20-02 | Crossroads | 2026-08-15 | 19 | Animal | Transformer fuse | Forced | None
OE-26-003508 | 1947 | 11 | 177 | BY-S16-01 | Bayou | 2026-08-15 | 20 | Unknown | Transformer fuse | Forced | None
OE-26-003509 | 3416 | 14 | 244 | PR-S02-02 | Prairie | 2026-08-15 | 22 | Vegetation | Transformer fuse | Forced | None
OE-26-003510 | 48776 | 938 | 52 | PR-S13-01 | Prairie | 2026-08-15 | 22 | Weather - lightning | Feeder recloser | Forced | None
OE-26-003511 | 35298 | 666 | 53 | CR-S17-02 | Crossroads | 2026-08-16 | 0 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-003512 | 3318 | 14 | 237 | PR-S10-01 | Prairie | 2026-08-16 | 2 | Vegetation | Transformer fuse | Forced | None
OE-26-003513 | 1790 | 10 | 179 | BY-S07-02 | Bayou | 2026-08-16 | 6 | Animal | Transformer fuse | Forced | None
OE-26-003514 | 44268 | 651 | 68 | BY-S21-05 | Bayou | 2026-08-16 | 8 | Weather - lightning | Feeder recloser | Forced | None
OE-26-003515 | 708 | 4 | 177 | BY-S28-03 | Bayou | 2026-08-16 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-003516 | 490 | 5 | 98 | BY-S15-06 | Bayou | 2026-08-16 | 11 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003517 | 602 | 7 | 86 | BY-S17-01 | Bayou | 2026-08-16 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003518 | 48174 | 518 | 93 | PR-S05-01 | Prairie | 2026-08-16 | 11 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003519 | 7160 | 40 | 179 | PR-S16-03 | Prairie | 2026-08-16 | 11 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003520 | 141459 | 773 | 183 | BY-S04-03 | Bayou | 2026-08-16 | 14 | Weather - wind | Feeder recloser | Forced | None
OE-26-003521 | 1773 | 9 | 197 | CR-S14-05 | Crossroads | 2026-08-16 | 15 | Animal | Transformer fuse | Forced | None
OE-26-003522 | 5460 | 14 | 390 | HB-S07-04 | Harbor | 2026-08-16 | 15 | Unknown | Transformer fuse | Forced | None
OE-26-003523 | 51359 | 203 | 253 | BY-S25-04 | Bayou | 2026-08-16 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003524 | 2088 | 12 | 174 | CR-S05-05 | Crossroads | 2026-08-16 | 16 | Animal | Transformer fuse | Forced | None
OE-26-003525 | 5046 | 58 | 87 | BY-S10-03 | Bayou | 2026-08-16 | 19 | Animal | Lateral fuse | Forced | None
OE-26-003526 | 80884 | 1108 | 73 | BY-S12-04 | Bayou | 2026-08-16 | 19 | Vegetation | Substation breaker | Forced | None
OE-26-003527 | 14527 | 73 | 199 | CR-S04-01 | Crossroads | 2026-08-16 | 19 | Animal | Lateral fuse | Forced | None
OE-26-003528 | 67122 | 226 | 297 | PR-S04-01 | Prairie | 2026-08-16 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003529 | 18170 | 230 | 79 | CR-S08-04 | Crossroads | 2026-08-16 | 23 | Vegetation | Feeder recloser | Forced | None
OE-26-003530 | 2431 | 13 | 187 | PR-S06-02 | Prairie | 2026-08-17 | 4 | Animal | Transformer fuse | Forced | None
OE-26-003531 | 2046 | 11 | 186 | PR-S18-01 | Prairie | 2026-08-17 | 5 | Animal | Transformer fuse | Forced | None
OE-26-003532 | 222 | 3 | 74 | PR-S16-02 | Prairie | 2026-08-17 | 6 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003533 | 20988 | 106 | 198 | PR-S18-05 | Prairie | 2026-08-17 | 7 | Unknown | Lateral fuse | Forced | None
OE-26-003534 | 5586 | 38 | 147 | CR-S24-01 | Crossroads | 2026-08-17 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003535 | 1199 | 11 | 109 | HB-S09-04 | Harbor | 2026-08-17 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003536 | 1056 | 11 | 96 | PR-S14-04 | Prairie | 2026-08-17 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003537 | 7626 | 82 | 93 | CR-S14-03 | Crossroads | 2026-08-17 | 11 | Vegetation | Lateral fuse | Forced | None
OE-26-003538 | 728 | 13 | 56 | PR-S05-01 | Prairie | 2026-08-17 | 11 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003539 | 99788 | 988 | 101 | PR-S11-03 | Prairie | 2026-08-17 | 12 | Animal | Feeder recloser | Forced | None
OE-26-003540 | 38485 | 215 | 179 | PR-S06-02 | Prairie | 2026-08-17 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003541 | 6060 | 12 | 505 | PR-S04-02 | Prairie | 2026-08-17 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003542 | 237 | 3 | 79 | BY-S29-01 | Bayou | 2026-08-17 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003543 | 273 | 3 | 91 | CR-S29-03 | Crossroads | 2026-08-17 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003544 | 11640 | 60 | 194 | CR-S26-06 | Crossroads | 2026-08-17 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003545 | 729 | 9 | 81 | HB-S03-03 | Harbor | 2026-08-17 | 19 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003546 | 1088 | 8 | 136 | CR-S29-03 | Crossroads | 2026-08-18 | 0 | Weather - wind | Transformer fuse | Forced | None
OE-26-003547 | 1044 | 9 | 116 | CR-S30-01 | Crossroads | 2026-08-18 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-003548 | 3650 | 50 | 73 | CR-S30-03 | Crossroads | 2026-08-18 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003549 | 10750 | 215 | 50 | HB-S01-02 | Harbor | 2026-08-18 | 9 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003550 | 1368 | 9 | 152 | PR-S03-03 | Prairie | 2026-08-18 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003551 | 1150 | 10 | 115 | CR-S19-03 | Crossroads | 2026-08-18 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003552 | 10080 | 60 | 168 | BY-S07-05 | Bayou | 2026-08-18 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003553 | 12426 | 218 | 57 | BY-S12-03 | Bayou | 2026-08-18 | 13 | Animal | Lateral fuse | Forced | None
OE-26-003554 | 44362 | 1082 | 41 | PR-S05-02 | Prairie | 2026-08-18 | 13 | Equipment - overhead | Substation breaker | Forced | None
OE-26-003555 | 10519 | 67 | 157 | PR-S20-02 | Prairie | 2026-08-18 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003556 | 21712 | 118 | 184 | BY-S08-01 | Bayou | 2026-08-18 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-003557 | 2380 | 34 | 70 | CR-S05-04 | Crossroads | 2026-08-18 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003558 | 5015 | 59 | 85 | CR-S30-06 | Crossroads | 2026-08-18 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003559 | 1425 | 5 | 285 | CR-S03-02 | Crossroads | 2026-08-18 | 17 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003560 | 762 | 6 | 127 | CR-S04-02 | Crossroads | 2026-08-18 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003561 | 1210 | 10 | 121 | CR-S22-01 | Crossroads | 2026-08-18 | 22 | Animal | Transformer fuse | Forced | None
OE-26-003562 | 36252 | 477 | 76 | BY-S13-02 | Bayou | 2026-08-18 | 23 | Vegetation | Feeder recloser | Forced | None
OE-26-003563 | 2300 | 10 | 230 | HB-S08-01 | Harbor | 2026-08-19 | 2 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003564 | 2652 | 13 | 204 | BY-S26-05 | Bayou | 2026-08-19 | 5 | Vegetation | Transformer fuse | Forced | None
OE-26-003565 | 6887 | 71 | 97 | HB-S01-03 | Harbor | 2026-08-19 | 5 | Animal | Lateral fuse | Forced | None
OE-26-003566 | 700 | 2 | 350 | PR-S05-02 | Prairie | 2026-08-19 | 6 | Weather - wind | Transformer fuse | Forced | None
OE-26-003567 | 951 | 3 | 317 | BY-S28-03 | Bayou | 2026-08-19 | 7 | Vegetation | Transformer fuse | Forced | None
OE-26-003568 | 6708 | 43 | 156 | BY-S16-02 | Bayou | 2026-08-19 | 8 | Vegetation | Lateral fuse | Forced | None
OE-26-003569 | 11008 | 64 | 172 | HB-S19-04 | Harbor | 2026-08-19 | 12 | Vegetation | Lateral fuse | Forced | None
OE-26-003570 | 695 | 5 | 139 | PR-S13-03 | Prairie | 2026-08-19 | 12 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003571 | 33012 | 262 | 126 | PR-S14-02 | Prairie | 2026-08-19 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003572 | 7050 | 47 | 150 | BY-S18-05 | Bayou | 2026-08-19 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003573 | 47810 | 683 | 70 | PR-S16-03 | Prairie | 2026-08-19 | 13 | Equipment - overhead | Substation breaker | Forced | None
OE-26-003574 | 86541 | 951 | 91 | PR-S06-02 | Prairie | 2026-08-19 | 14 | Equipment - underground | Substation breaker | Forced | None
OE-26-003575 | 22359 | 87 | 257 | CR-S06-02 | Crossroads | 2026-08-19 | 15 | Animal | Lateral fuse | Forced | None
OE-26-003576 | 742 | 7 | 106 | CR-S04-06 | Crossroads | 2026-08-19 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-003577 | 110526 | 507 | 218 | PR-S05-03 | Prairie | 2026-08-19 | 18 | Vegetation | Feeder recloser | Forced | None
OE-26-003578 | 168 | 1 | 168 | BY-S17-04 | Bayou | 2026-08-19 | 21 | Animal | Transformer fuse | Forced | None
OE-26-003579 | 20562 | 149 | 138 | HB-S03-02 | Harbor | 2026-08-19 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003580 | 38478 | 242 | 159 | PR-S01-05 | Prairie | 2026-08-19 | 22 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003581 | 4140 | 12 | 345 | BY-S19-02 | Bayou | 2026-08-19 | 23 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003582 | 21546 | 189 | 114 | CR-S09-05 | Crossroads | 2026-08-19 | 23 | Animal | Lateral fuse | Forced | None
OE-26-003583 | 42130 | 1915 | 22 | CR-S14-02 | Crossroads | 2026-08-19 | 23 | Weather - wind | Feeder recloser | Forced | None
OE-26-003584 | 1106 | 7 | 158 | BY-S15-05 | Bayou | 2026-08-20 | 0 | Vegetation | Transformer fuse | Forced | None
OE-26-003585 | 220 | 2 | 110 | CR-S19-04 | Crossroads | 2026-08-20 | 0 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003586 | 29964 | 908 | 33 | HB-S18-01 | Harbor | 2026-08-20 | 3 | Vegetation | Feeder recloser | Forced | None
OE-26-003587 | 1266 | 6 | 211 | CR-S14-02 | Crossroads | 2026-08-20 | 6 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003588 | 2048 | 8 | 256 | PR-S01-03 | Prairie | 2026-08-20 | 6 | Animal | Transformer fuse | Forced | None
OE-26-003589 | 28002 | 718 | 39 | BY-S27-04 | Bayou | 2026-08-20 | 9 | Weather - lightning | Substation breaker | Outside cause | None
OE-26-003590 | 356 | 4 | 89 | CR-S07-07 | Crossroads | 2026-08-20 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003591 | 3219 | 37 | 87 | BY-S02-01 | Bayou | 2026-08-20 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-003592 | 16440 | 60 | 274 | HB-S03-02 | Harbor | 2026-08-20 | 11 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003593 | 3538 | 58 | 61 | HB-S19-04 | Harbor | 2026-08-20 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003594 | 275022 | 1389 | 198 | PR-S04-01 | Prairie | 2026-08-20 | 12 | Vegetation | Substation breaker | Forced | None
OE-26-003595 | 179424 | 2016 | 89 | CR-S22-01 | Crossroads | 2026-08-20 | 13 | Equipment - underground | Substation breaker | Forced | None
OE-26-003596 | 6580 | 47 | 140 | HB-S06-02 | Harbor | 2026-08-20 | 13 | Vegetation | Lateral fuse | Forced | None
OE-26-003597 | 4980 | 60 | 83 | BY-S18-07 | Bayou | 2026-08-20 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-003598 | 153682 | 1787 | 86 | BY-S23-02 | Bayou | 2026-08-20 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003599 | 428 | 4 | 107 | HB-S15-02 | Harbor | 2026-08-20 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-003600 | 856 | 4 | 214 | CR-S16-04 | Crossroads | 2026-08-20 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003601 | 18040 | 88 | 205 | BY-S18-01 | Bayou | 2026-08-20 | 18 | Animal | Lateral fuse | Forced | None
OE-26-003602 | 3408 | 12 | 284 | CR-S26-04 | Crossroads | 2026-08-20 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003603 | 45353 | 341 | 133 | PR-S03-01 | Prairie | 2026-08-21 | 0 | Vehicle or public | Feeder recloser | Forced | None
OE-26-003604 | 2128 | 14 | 152 | CR-S08-05 | Crossroads | 2026-08-21 | 5 | Weather - wind | Transformer fuse | Forced | None
OE-26-003605 | 2562 | 14 | 183 | CR-S08-02 | Crossroads | 2026-08-21 | 7 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003606 | 462 | 3 | 154 | BY-S09-02 | Bayou | 2026-08-21 | 8 | Animal | Transformer fuse | Forced | None
OE-26-003607 | 1936 | 22 | 88 | BY-S26-06 | Bayou | 2026-08-21 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003608 | 1206 | 6 | 201 | BY-S25-04 | Bayou | 2026-08-21 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-003609 | 4655 | 35 | 133 | BY-S16-01 | Bayou | 2026-08-21 | 11 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003610 | 169 | 1 | 169 | BY-S03-01 | Bayou | 2026-08-21 | 12 | Unknown | Transformer fuse | Forced | None
OE-26-003611 | 938 | 7 | 134 | CR-S17-01 | Crossroads | 2026-08-21 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003612 | 990 | 9 | 110 | CR-S26-06 | Crossroads | 2026-08-21 | 12 | Animal | Transformer fuse | Forced | None
OE-26-003613 | 18600 | 155 | 120 | BY-S19-02 | Bayou | 2026-08-21 | 13 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003614 | 4992 | 52 | 96 | HB-S15-02 | Harbor | 2026-08-21 | 13 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003615 | 166 | 2 | 83 | CR-S28-03 | Crossroads | 2026-08-21 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003616 | 178 | 1 | 178 | BY-S20-03 | Bayou | 2026-08-21 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003617 | 17640 | 84 | 210 | CR-S01-02 | Crossroads | 2026-08-21 | 15 | Animal | Lateral fuse | Forced | None
OE-26-003618 | 700 | 10 | 70 | HB-S19-03 | Harbor | 2026-08-21 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-26-003619 | 2388 | 12 | 199 | PR-S01-06 | Prairie | 2026-08-21 | 15 | Weather - wind | Transformer fuse | Forced | None
OE-26-003620 | 9880 | 52 | 190 | BY-S09-02 | Bayou | 2026-08-21 | 16 | Vegetation | Lateral fuse | Forced | None
OE-26-003621 | 1164 | 4 | 291 | BY-S16-02 | Bayou | 2026-08-21 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003622 | 76923 | 1221 | 63 | BY-S23-02 | Bayou | 2026-08-21 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-003623 | 393 | 3 | 131 | HB-S13-02 | Harbor | 2026-08-21 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003624 | 406 | 7 | 58 | BY-S14-01 | Bayou | 2026-08-21 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-003625 | 1510 | 10 | 151 | CR-S18-02 | Crossroads | 2026-08-21 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003626 | 972 | 9 | 108 | HB-S10-03 | Harbor | 2026-08-21 | 21 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003627 | 484 | 2 | 242 | CR-S09-04 | Crossroads | 2026-08-22 | 0 | Animal | Transformer fuse | Forced | None
OE-26-003628 | 1336 | 8 | 167 | PR-S14-02 | Prairie | 2026-08-22 | 2 | Vegetation | Transformer fuse | Forced | None
OE-26-003629 | 2314 | 13 | 178 | CR-S23-05 | Crossroads | 2026-08-22 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003630 | 52080 | 1240 | 42 | CR-S14-03 | Crossroads | 2026-08-22 | 9 | Vegetation | Feeder recloser | Forced | None
OE-26-003631 | 1269 | 9 | 141 | CR-S27-01 | Crossroads | 2026-08-22 | 9 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003632 | 44528 | 506 | 88 | PR-S03-05 | Prairie | 2026-08-22 | 9 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003633 | 42714 | 678 | 63 | BY-S07-03 | Bayou | 2026-08-22 | 12 | Vegetation | Feeder recloser | Forced | None
OE-26-003634 | 59362 | 886 | 67 | BY-S13-02 | Bayou | 2026-08-22 | 12 | Vegetation | Substation breaker | Forced | None
OE-26-003635 | 1881 | 11 | 171 | HB-S05-03 | Harbor | 2026-08-22 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003636 | 560 | 10 | 56 | HB-S17-03 | Harbor | 2026-08-22 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-003637 | 822 | 6 | 137 | BY-S03-03 | Bayou | 2026-08-22 | 13 | Unknown | Transformer fuse | Forced | None
OE-26-003638 | 1350 | 10 | 135 | CR-S11-01 | Crossroads | 2026-08-22 | 13 | Vegetation | Transformer fuse | Forced | None
OE-26-003639 | 13020 | 310 | 42 | BY-S18-01 | Bayou | 2026-08-22 | 14 | Vegetation | Feeder recloser | Forced | None
OE-26-003640 | 756 | 9 | 84 | CR-S13-06 | Crossroads | 2026-08-22 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003641 | 1130 | 10 | 113 | CR-S32-03 | Crossroads | 2026-08-22 | 15 | Animal | Transformer fuse | Forced | None
OE-26-003642 | 308 | 2 | 154 | BY-S27-03 | Bayou | 2026-08-22 | 17 | Vegetation | Transformer fuse | Forced | None
OE-26-003643 | 6050 | 55 | 110 | CR-S14-01 | Crossroads | 2026-08-22 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003644 | 2780 | 10 | 278 | PR-S19-02 | Prairie | 2026-08-22 | 17 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003645 | 490 | 5 | 98 | CR-S25-05 | Crossroads | 2026-08-22 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003646 | 9135 | 87 | 105 | BY-S02-02 | Bayou | 2026-08-22 | 22 | Vegetation | Lateral fuse | Forced | None
OE-26-003647 | 7332 | 52 | 141 | BY-S07-04 | Bayou | 2026-08-23 | 1 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003648 | 616 | 8 | 77 | BY-S16-02 | Bayou | 2026-08-23 | 1 | Weather - wind | Transformer fuse | Forced | None
OE-26-003649 | 1344 | 12 | 112 | PR-S13-06 | Prairie | 2026-08-23 | 8 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003650 | 1116 | 6 | 186 | BY-S29-03 | Bayou | 2026-08-23 | 9 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003651 | 1484 | 53 | 28 | BY-S11-02 | Bayou | 2026-08-23 | 12 | Weather - wind | Lateral fuse | Forced | None
OE-26-003652 | 18590 | 169 | 110 | HB-S06-02 | Harbor | 2026-08-23 | 12 | Animal | Lateral fuse | Forced | None
OE-26-003653 | 50819 | 571 | 89 | CR-S04-05 | Crossroads | 2026-08-23 | 14 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003654 | 354 | 3 | 118 | CR-S27-02 | Crossroads | 2026-08-23 | 14 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003655 | 745 | 5 | 149 | CR-S17-03 | Crossroads | 2026-08-23 | 15 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003656 | 1206 | 6 | 201 | PR-S08-03 | Prairie | 2026-08-23 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-003657 | 2748 | 12 | 229 | BY-S21-01 | Bayou | 2026-08-23 | 17 | Animal | Transformer fuse | Forced | None
OE-26-003658 | 1564 | 34 | 46 | BY-S04-01 | Bayou | 2026-08-23 | 18 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003659 | 1834 | 14 | 131 | BY-S09-04 | Bayou | 2026-08-23 | 18 | Weather - wind | Transformer fuse | Forced | None
OE-26-003660 | 6272 | 56 | 112 | BY-S24-04 | Bayou | 2026-08-23 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003661 | 34629 | 679 | 51 | CR-S25-04 | Crossroads | 2026-08-23 | 21 | Vegetation | Feeder recloser | Forced | None
OE-26-003662 | 852 | 6 | 142 | HB-S07-03 | Harbor | 2026-08-23 | 22 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003663 | 1452 | 12 | 121 | PR-S08-03 | Prairie | 2026-08-23 | 23 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003664 | 81095 | 2317 | 35 | CR-S16-04 | Crossroads | 2026-08-24 | 0 | Unknown | Substation breaker | Outside cause | None
OE-26-003665 | 1719 | 9 | 191 | BY-S08-01 | Bayou | 2026-08-24 | 5 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003666 | 5356 | 52 | 103 | CR-S11-01 | Crossroads | 2026-08-24 | 6 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003667 | 884 | 13 | 68 | HB-S01-03 | Harbor | 2026-08-24 | 7 | Animal | Lateral fuse | Forced | None
OE-26-003668 | 23800 | 70 | 340 | BY-S04-03 | Bayou | 2026-08-24 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003669 | 1024 | 8 | 128 | BY-S19-04 | Bayou | 2026-08-24 | 9 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003670 | 9581 | 143 | 67 | CR-S20-03 | Crossroads | 2026-08-24 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003671 | 940 | 5 | 188 | BY-S23-02 | Bayou | 2026-08-24 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003672 | 360 | 6 | 60 | CR-S13-06 | Crossroads | 2026-08-24 | 10 | Animal | Transformer fuse | Forced | None
OE-26-003673 | 68628 | 903 | 76 | CR-S30-07 | Crossroads | 2026-08-24 | 10 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003674 | 40832 | 352 | 116 | HB-S07-05 | Harbor | 2026-08-24 | 10 | Weather - wind | IGSD-isolated section | Forced | None
OE-26-003675 | 2466 | 18 | 137 | CR-S02-03 | Crossroads | 2026-08-24 | 11 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003676 | 1326 | 6 | 221 | BY-S21-01 | Bayou | 2026-08-24 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003677 | 10528 | 56 | 188 | PR-S03-04 | Prairie | 2026-08-24 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-003678 | 5750 | 46 | 125 | BY-S08-02 | Bayou | 2026-08-24 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003679 | 3185 | 65 | 49 | CR-S09-01 | Crossroads | 2026-08-24 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003680 | 59616 | 368 | 162 | PR-S15-04 | Prairie | 2026-08-24 | 16 | Vegetation | Feeder recloser | Forced | None
OE-26-003681 | 35854 | 182 | 197 | PR-S19-05 | Prairie | 2026-08-24 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003682 | 7154 | 73 | 98 | PR-S16-01 | Prairie | 2026-08-24 | 17 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003683 | 179 | 1 | 179 | BY-S23-05 | Bayou | 2026-08-24 | 19 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003684 | 3842 | 34 | 113 | PR-S11-02 | Prairie | 2026-08-24 | 22 | Vegetation | Lateral fuse | Forced | None
OE-26-003685 | 1575 | 7 | 225 | CR-S15-01 | Crossroads | 2026-08-25 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003686 | 1400 | 14 | 100 | BY-S16-02 | Bayou | 2026-08-25 | 1 | Vegetation | Transformer fuse | Forced | None
OE-26-003687 | 396 | 2 | 198 | BY-S06-02 | Bayou | 2026-08-25 | 3 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003688 | 531 | 3 | 177 | CR-S21-02 | Crossroads | 2026-08-25 | 9 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003689 | 277732 | 1526 | 182 | BY-S23-02 | Bayou | 2026-08-25 | 10 | Vehicle or public | Feeder recloser | Forced | None
OE-26-003690 | 119805 | 815 | 147 | CR-S22-04 | Crossroads | 2026-08-25 | 10 | Vegetation | Feeder recloser | Forced | None
OE-26-003691 | 738 | 9 | 82 | BY-S14-02 | Bayou | 2026-08-25 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003692 | 29414 | 154 | 191 | PR-S14-01 | Prairie | 2026-08-25 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003693 | 1770 | 10 | 177 | HB-S14-01 | Harbor | 2026-08-25 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003694 | 6811 | 49 | 139 | PR-S18-06 | Prairie | 2026-08-25 | 13 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003695 | 4615 | 65 | 71 | CR-S16-04 | Crossroads | 2026-08-25 | 14 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003696 | 1599 | 13 | 123 | BY-S28-01 | Bayou | 2026-08-25 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003697 | 11730 | 51 | 230 | BY-S17-01 | Bayou | 2026-08-25 | 19 | Vegetation | Lateral fuse | Forced | None
OE-26-003698 | 837 | 9 | 93 | BY-S23-02 | Bayou | 2026-08-25 | 20 | Animal | Transformer fuse | Forced | None
OE-26-003699 | 4830 | 30 | 161 | CR-S03-01 | Crossroads | 2026-08-25 | 20 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003700 | 39468 | 299 | 132 | PR-S10-02 | Prairie | 2026-08-25 | 21 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003701 | 5074 | 43 | 118 | CR-S04-05 | Crossroads | 2026-08-26 | 7 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003702 | 163 | 1 | 163 | HB-S09-05 | Harbor | 2026-08-26 | 7 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003703 | 34221 | 187 | 183 | BY-S13-03 | Bayou | 2026-08-26 | 8 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003704 | 9660 | 42 | 230 | BY-S28-02 | Bayou | 2026-08-26 | 8 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003705 | 7812 | 62 | 126 | PR-S07-06 | Prairie | 2026-08-26 | 9 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003706 | 370 | 2 | 185 | PR-S18-06 | Prairie | 2026-08-26 | 9 | Vegetation | Transformer fuse | Forced | None
OE-26-003707 | 1356 | 12 | 113 | PR-S15-03 | Prairie | 2026-08-26 | 10 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003708 | 415 | 5 | 83 | HB-S01-02 | Harbor | 2026-08-26 | 11 | Animal | Transformer fuse | Forced | None
OE-26-003709 | 6895 | 35 | 197 | HB-S09-01 | Harbor | 2026-08-26 | 12 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003710 | 34048 | 224 | 152 | PR-S18-03 | Prairie | 2026-08-26 | 12 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003711 | 1974 | 14 | 141 | BY-S20-03 | Bayou | 2026-08-26 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003712 | 2052 | 12 | 171 | BY-S15-02 | Bayou | 2026-08-26 | 14 | Vegetation | Transformer fuse | Forced | None
OE-26-003713 | 8372 | 52 | 161 | BY-S15-02 | Bayou | 2026-08-26 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-003714 | 12095 | 59 | 205 | BY-S24-01 | Bayou | 2026-08-26 | 14 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003715 | 370104 | 4406 | 84 | HB-S10-03 | Harbor | 2026-08-26 | 14 | Unknown | Substation breaker | Forced | None
OE-26-003716 | 735 | 5 | 147 | HB-S01-02 | Harbor | 2026-08-26 | 15 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003717 | 3248 | 56 | 58 | BY-S29-02 | Bayou | 2026-08-26 | 17 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003718 | 8883 | 189 | 47 | HB-S09-03 | Harbor | 2026-08-26 | 18 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003719 | 1548 | 6 | 258 | BY-S01-01 | Bayou | 2026-08-26 | 20 | Animal | Transformer fuse | Forced | None
OE-26-003720 | 3638 | 34 | 107 | BY-S29-05 | Bayou | 2026-08-26 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-003721 | 357 | 3 | 119 | CR-S17-01 | Crossroads | 2026-08-26 | 21 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003722 | 35666 | 1049 | 34 | BY-S30-03 | Bayou | 2026-08-27 | 9 | Vegetation | Substation breaker | Forced | None
OE-26-003723 | 10285 | 85 | 121 | BY-S02-01 | Bayou | 2026-08-27 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003724 | 495 | 11 | 45 | BY-S26-01 | Bayou | 2026-08-27 | 10 | Vegetation | Transformer fuse | Forced | None
OE-26-003725 | 8352 | 96 | 87 | HB-S05-01 | Harbor | 2026-08-27 | 10 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003726 | 762 | 3 | 254 | BY-S29-02 | Bayou | 2026-08-27 | 12 | Unknown | Transformer fuse | Forced | None
OE-26-003727 | 485 | 5 | 97 | PR-S06-02 | Prairie | 2026-08-27 | 13 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003728 | 29799 | 77 | 387 | BY-S16-03 | Bayou | 2026-08-27 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-003729 | 3528 | 36 | 98 | CR-S04-02 | Crossroads | 2026-08-27 | 14 | Vegetation | Lateral fuse | Forced | None
OE-26-003730 | 1308 | 12 | 109 | HB-S11-01 | Harbor | 2026-08-27 | 14 | Weather - wind | Lateral fuse | Forced | None
OE-26-003731 | 24156 | 66 | 366 | CR-S13-03 | Crossroads | 2026-08-27 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003732 | 51367 | 1657 | 31 | CR-S13-03 | Crossroads | 2026-08-27 | 17 | Weather - lightning | Substation breaker | Forced | None
OE-26-003733 | 11400 | 95 | 120 | BY-S21-05 | Bayou | 2026-08-27 | 21 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003734 | 4769 | 19 | 251 | PR-S03-02 | Prairie | 2026-08-27 | 21 | Vegetation | Lateral fuse | Forced | None
OE-26-003735 | 316 | 2 | 158 | BY-S26-04 | Bayou | 2026-08-27 | 22 | Animal | Transformer fuse | Forced | None
OE-26-003736 | 1056 | 12 | 88 | HB-S03-03 | Harbor | 2026-08-27 | 22 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003737 | 1352 | 13 | 104 | HB-S12-01 | Harbor | 2026-08-27 | 22 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003738 | 1728 | 32 | 54 | HB-S15-02 | Harbor | 2026-08-27 | 23 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003739 | 15635 | 265 | 59 | CR-S27-01 | Crossroads | 2026-08-28 | 6 | Equipment - underground | Feeder recloser | Forced | None
OE-26-003740 | 11660 | 110 | 106 | HB-S09-02 | Harbor | 2026-08-28 | 6 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003741 | 1600 | 10 | 160 | HB-S14-04 | Harbor | 2026-08-28 | 7 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003742 | 4061 | 31 | 131 | HB-S09-02 | Harbor | 2026-08-28 | 8 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003743 | 4941 | 61 | 81 | CR-S04-06 | Crossroads | 2026-08-28 | 10 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003744 | 18601 | 89 | 209 | CR-S26-04 | Crossroads | 2026-08-28 | 10 | Animal | Lateral fuse | Forced | None
OE-26-003745 | 94000 | 235 | 400 | PR-S03-04 | Prairie | 2026-08-28 | 10 | Vehicle or public | Lateral fuse | Forced | None
OE-26-003746 | 1442 | 14 | 103 | CR-S19-04 | Crossroads | 2026-08-28 | 11 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003747 | 2324 | 14 | 166 | CR-S16-04 | Crossroads | 2026-08-28 | 12 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003748 | 167365 | 895 | 187 | PR-S10-03 | Prairie | 2026-08-28 | 14 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003749 | 318 | 3 | 106 | BY-S23-04 | Bayou | 2026-08-28 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003750 | 1420 | 10 | 142 | PR-S13-05 | Prairie | 2026-08-28 | 15 | Vegetation | Transformer fuse | Forced | None
OE-26-003751 | 11730 | 102 | 115 | BY-S17-01 | Bayou | 2026-08-28 | 17 | Vegetation | Lateral fuse | Forced | None
OE-26-003752 | 696 | 4 | 174 | BY-S15-06 | Bayou | 2026-08-28 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003753 | 4977 | 21 | 237 | PR-S13-04 | Prairie | 2026-08-28 | 19 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003754 | 12152 | 56 | 217 | CR-S22-03 | Crossroads | 2026-08-28 | 20 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003755 | 284 | 2 | 142 | PR-S12-01 | Prairie | 2026-08-28 | 21 | Weather - wind | Transformer fuse | Forced | None
OE-26-003756 | 100928 | 664 | 152 | CR-S14-01 | Crossroads | 2026-08-29 | 7 | Animal | Feeder recloser | Forced | None
OE-26-003757 | 322368 | 1168 | 276 | BY-S08-01 | Bayou | 2026-08-29 | 8 | Vegetation | Feeder recloser | Forced | None
OE-26-003758 | 134 | 2 | 67 | CR-S17-01 | Crossroads | 2026-08-29 | 9 | Animal | Transformer fuse | Forced | None
OE-26-003759 | 576 | 6 | 96 | PR-S08-01 | Prairie | 2026-08-29 | 10 | Animal | Lateral fuse | Forced | None
OE-26-003760 | 1125 | 9 | 125 | CR-S12-01 | Crossroads | 2026-08-29 | 11 | Vegetation | Transformer fuse | Forced | None
OE-26-003761 | 83367 | 1413 | 59 | CR-S17-01 | Crossroads | 2026-08-29 | 13 | Vehicle or public | Feeder recloser | Forced | None
OE-26-003762 | 1305 | 9 | 145 | CR-S15-02 | Crossroads | 2026-08-29 | 14 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003763 | 31306 | 1423 | 22 | CR-S31-02 | Crossroads | 2026-08-29 | 15 | Vegetation | Feeder recloser | Forced | None
OE-26-003764 | 43731 | 387 | 113 | CR-S32-03 | Crossroads | 2026-08-29 | 15 | Equipment - underground | IGSD-isolated section | Forced | None
OE-26-003765 | 3681 | 9 | 409 | PR-S20-02 | Prairie | 2026-08-29 | 15 | Animal | Lateral fuse | Forced | None
OE-26-003766 | 595 | 7 | 85 | CR-S02-03 | Crossroads | 2026-08-29 | 16 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003767 | 2052 | 12 | 171 | HB-S14-01 | Harbor | 2026-08-29 | 16 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003768 | 2232 | 12 | 186 | PR-S07-02 | Prairie | 2026-08-29 | 16 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003769 | 9828 | 84 | 117 | PR-S10-02 | Prairie | 2026-08-29 | 16 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003770 | 462 | 2 | 231 | BY-S19-03 | Bayou | 2026-08-29 | 17 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003771 | 1199 | 11 | 109 | BY-S19-04 | Bayou | 2026-08-29 | 18 | Vegetation | Transformer fuse | Forced | None
OE-26-003772 | 18584 | 101 | 184 | PR-S12-01 | Prairie | 2026-08-29 | 18 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003773 | 3216 | 12 | 268 | CR-S12-01 | Crossroads | 2026-08-29 | 19 | Vehicle or public | Transformer fuse | Forced | None
OE-26-003774 | 3591 | 57 | 63 | PR-S03-04 | Prairie | 2026-08-29 | 20 | Vegetation | Lateral fuse | Forced | None
OE-26-003775 | 236406 | 2883 | 82 | CR-S27-02 | Crossroads | 2026-08-30 | 0 | Equipment - underground | Substation breaker | Forced | None
OE-26-003776 | 37975 | 175 | 217 | BY-S22-01 | Bayou | 2026-08-30 | 2 | Vegetation | Lateral fuse | Forced | None
OE-26-003777 | 1152 | 12 | 96 | BY-S05-01 | Bayou | 2026-08-30 | 6 | Animal | Transformer fuse | Forced | None
OE-26-003778 | 1030 | 5 | 206 | BY-S27-03 | Bayou | 2026-08-30 | 7 | Animal | Transformer fuse | Forced | None
OE-26-003779 | 2002 | 11 | 182 | BY-S12-02 | Bayou | 2026-08-30 | 8 | Weather - wind | Transformer fuse | Forced | None
OE-26-003780 | 1988 | 14 | 142 | BY-S15-03 | Bayou | 2026-08-30 | 8 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003781 | 10368 | 54 | 192 | BY-S25-02 | Bayou | 2026-08-30 | 9 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003782 | 3122 | 14 | 223 | HB-S18-02 | Harbor | 2026-08-30 | 9 | Animal | Transformer fuse | Forced | None
OE-26-003783 | 1968 | 12 | 164 | BY-S06-01 | Bayou | 2026-08-30 | 10 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003784 | 2697 | 93 | 29 | CR-S28-02 | Crossroads | 2026-08-30 | 11 | Animal | Lateral fuse | Forced | None
OE-26-003785 | 3280 | 20 | 164 | BY-S05-01 | Bayou | 2026-08-30 | 12 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003786 | 488 | 4 | 122 | BY-S22-02 | Bayou | 2026-08-30 | 12 | Weather - wind | Transformer fuse | Forced | None
OE-26-003787 | 1582 | 14 | 113 | CR-S08-02 | Crossroads | 2026-08-30 | 12 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003788 | 765 | 5 | 153 | HB-S08-01 | Harbor | 2026-08-30 | 13 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003789 | 16340 | 215 | 76 | CR-S04-02 | Crossroads | 2026-08-30 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003790 | 143960 | 1180 | 122 | PR-S01-03 | Prairie | 2026-08-30 | 14 | Weather - wind | Substation breaker | Forced | None
OE-26-003791 | 3276 | 13 | 252 | PR-S01-03 | Prairie | 2026-08-30 | 14 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003792 | 6278 | 43 | 146 | BY-S15-04 | Bayou | 2026-08-30 | 15 | Equipment - underground | Lateral fuse | Forced | None
OE-26-003793 | 2800 | 14 | 200 | PR-S01-04 | Prairie | 2026-08-30 | 15 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003794 | 126540 | 1140 | 111 | BY-S22-03 | Bayou | 2026-08-30 | 16 | Equipment - overhead | Feeder recloser | Forced | None
OE-26-003795 | 2800 | 40 | 70 | CR-S20-02 | Crossroads | 2026-08-30 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003796 | 825 | 5 | 165 | CR-S32-02 | Crossroads | 2026-08-30 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003797 | 3146 | 26 | 121 | CR-S29-02 | Crossroads | 2026-08-30 | 17 | Unknown | Lateral fuse | Forced | None
OE-26-003798 | 606 | 3 | 202 | CR-S15-02 | Crossroads | 2026-08-30 | 18 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003799 | 39072 | 528 | 74 | CR-S20-05 | Crossroads | 2026-08-30 | 20 | Equipment - overhead | IGSD-isolated section | Forced | None
OE-26-003800 | 3570 | 14 | 255 | PR-S10-01 | Prairie | 2026-08-30 | 21 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003801 | 680 | 5 | 136 | HB-S03-01 | Harbor | 2026-08-30 | 22 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003802 | 6084 | 52 | 117 | HB-S18-01 | Harbor | 2026-08-30 | 22 | Vegetation | Lateral fuse | Forced | None
OE-26-003803 | 1875 | 5 | 375 | PR-S07-03 | Prairie | 2026-08-30 | 23 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003804 | 984 | 6 | 164 | CR-S14-01 | Crossroads | 2026-08-31 | 0 | Equipment - underground | Transformer fuse | Forced | None
OE-26-003805 | 1998 | 9 | 222 | BY-S16-06 | Bayou | 2026-08-31 | 4 | Equipment - overhead | Transformer fuse | Forced | None
OE-26-003806 | 5832 | 81 | 72 | PR-S01-03 | Prairie | 2026-08-31 | 9 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003807 | 73216 | 832 | 88 | PR-S17-01 | Prairie | 2026-08-31 | 9 | Weather - lightning | Feeder recloser | Forced | None
OE-26-003808 | 5576 | 41 | 136 | BY-S17-03 | Bayou | 2026-08-31 | 10 | Scheduled | Lateral fuse | Scheduled | None
OE-26-003809 | 5301 | 93 | 57 | HB-S09-04 | Harbor | 2026-08-31 | 10 | Vegetation | Lateral fuse | Forced | None
OE-26-003810 | 7215 | 111 | 65 | HB-S19-01 | Harbor | 2026-08-31 | 10 | Weather - wind | Lateral fuse | Forced | None
OE-26-003811 | 110800 | 1108 | 100 | BY-S26-06 | Bayou | 2026-08-31 | 14 | Weather - lightning | Substation breaker | Forced | None
OE-26-003812 | 3000 | 25 | 120 | CR-S20-02 | Crossroads | 2026-08-31 | 14 | Equipment - overhead | Lateral fuse | Forced | None
OE-26-003813 | 27507 | 519 | 53 | BY-S09-01 | Bayou | 2026-08-31 | 15 | Animal | Lateral fuse | Forced | None
OE-26-003814 | 45510 | 410 | 111 | CR-S09-02 | Crossroads | 2026-08-31 | 15 | Animal | Feeder recloser | Forced | None
OE-26-003815 | 8030 | 55 | 146 | PR-S01-05 | Prairie | 2026-08-31 | 15 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003816 | 952 | 28 | 34 | BY-S08-03 | Bayou | 2026-08-31 | 16 | Weather - lightning | Lateral fuse | Forced | None
OE-26-003817 | 23532 | 318 | 74 | CR-S07-03 | Crossroads | 2026-08-31 | 16 | Animal | IGSD-isolated section | Forced | None
OE-26-003818 | 720 | 3 | 240 | CR-S16-06 | Crossroads | 2026-08-31 | 16 | Weather - lightning | Transformer fuse | Forced | None
OE-26-003819 | 880 | 11 | 80 | CR-S28-03 | Crossroads | 2026-08-31 | 18 | Weather - wind | Transformer fuse | Forced | None