## Slide 1
Reliability Council: Worst-Feeder Review, August 2026
Reliability Council, September 16, 2026. Worst-feeder review with January-August 2026 results. Presented by Reliability Engineering.
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 1

## Slide 2
Year to date: on track
January-August 2026 SAIDI excluding major events: 84.0 minutes (83.3 same period 2025). SAIFI 0.830 (0.850). Full-year standards are 124 minutes and 1.28.
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 2
Notes: Indices exclude the May 19-22 major event, planned interruptions and outside causes.

## Slide 3
By district
SAIDI / SAIFI, January-August 2026:
Harbor 71.3 / 0.713
Crossroads 63.4 / 0.724
Bayou 88.5 / 0.896
Prairie 139.3 / 1.092
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 3
Notes: Prairie remains the outlier; long rural overhead feeders.

## Slide 4
Customer minutes by month
All sustained interruptions in the 2026 extract, all classes. May is dominated by the wind event (463 interruptions, 132,152 customers, 116.6 million customer minutes).
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 4

## Slide 5
Customer minutes by month · customer-minutes
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 5
Chart: 
| 2026-01 | 2026-02 | 2026-03 | 2026-04 | 2026-05 | 2026-06 | 2026-07 | 2026-08
customer_minutes | 7616053 | 5410316 | 6195923 | 5699150 | 124623700 | 8488567 | 8472099 | 11033189

## Slide 6
2025 worst-feeder list recap
32 feeders: top 22 by SAIDI and top 22 by SAIFI (5% each, with overlap). 18 feeders were more than 200% above the feeder average in 2025. We screen against both the 300% rule text and the 200% statutory threshold.
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 6

## Slide 7
Repeat worst feeders in 2026
3 feeders on the 2025 list are again among the 22 highest-SAIDI feeders for January-August 2026 (excluding the May event):
BY-S29-05
PR-S02-02
PR-S03-04
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 7
Notes: All three already have remediation plans; see next slide.

## Slide 8
Remediation status
Each listed feeder gets a plan within 90 days: patrol and infrared scan, vegetation hot spots, fuse coordination, and reclosers or IGSD automation where needed. Prairie actions: owner shown as the Prairie district engineer in the tracker.
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 8
Notes: Ownership of the Prairie actions moved to Reliability Engineering in August; tracker update pending.

## Slide 9
Automation coverage
At August 31: 162 feeders with reclosers only, 134 with none, 102 with IGSD loops and 38 with full automation.
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 9

## Slide 10
Asks of the Council
Confirm IGSD automation for PR-S02-02 and PR-S03-04 in the 2027 plan.
Confirm the tracker owner for Prairie actions.
Sedgewater Energy Holdings | Reliability Engineering and Performance | 2026-09-16 | 10