## Slide 1
Bare Steel and Steel Service Replacement Program Review
Unprotected steel and steel service replacement program review, September 12, 2026. Targets, progress at August 31, leak performance and risks. Presented by Gas Compliance.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 1

## Slide 2
Program target
84 miles of unprotected steel main at the end of 2025, to be removed by the end of 2029. 2026 target: 22 miles of main and 2,400 steel services.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 2

## Slide 3
Progress at August 31
13.4 miles of unprotected steel main and 1,510 steel services replaced, 61% and 63% of the 2026 targets.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 3
Notes: Crews moved to Bayou in September; weather risk in November and December.

## Slide 4
Why steel first
Non-excavation leaks found in 2025 per 100 miles of main: unprotected steel 243, protected steel 75, polyethylene 20. By material: protected steel 876, polyethylene 761, unprotected steel 204, other plastic 11.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 4

## Slide 5
Other plastic
4 miles of early-vintage plastic main. Few leaks in absolute terms, but the sample is too small to compare leak rates reliably.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 5

## Slide 6
2026 leaks to August
1,360 leaks found: 110 grade 1, 368 grade 2, 882 grade 3; 69 from excavation damage.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 6

## Slide 7
System inventory (year-end 2025)
4,980 miles of main: polyethylene 3,720, protected steel 1,172, unprotected steel 84, other plastic 4; 251,000 services.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 7

## Slide 8
System inventory (year-end 2025) · extract summary
Measure: main_miles
Unit: miles
Total: 4980.0
Mean: 41.5
Records: 120
Period: 2025-12-31 to 2025-12-31
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 8

## Slide 9
System inventory (year-end 2025) · extract summary
Measure: services
Unit: services
Total: 251000
Mean: 2091.6667
Records: 120
Period: 2025-12-31 to 2025-12-31
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 9

## Slide 10
System inventory (year-end 2025) · extract summary
Measure: leaks_repaired_2025
Unit: leaks
Total: 914
Mean: 7.6167
Records: 120
Period: 2025-12-31 to 2025-12-31
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 10

## Slide 11
Risk ranking and surveys
Corrosion on unprotected steel is the second-ranked DIMP threat after excavation damage. Outside business districts the federal minimum is one survey every five calendar years; we survey unprotected steel areas every three years until the steel is retired.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 11

## Slide 12
Funding
Gas pipe replacement is a $78 million capital program in 2026, recovered through annual interim rate adjustments.
Sedgewater Energy Holdings | Gas Engineering and Integrity | 2026-09-12 | 12