## Read me
Feeder Register and 2026 Pole Inspection Results
Sedgewater Energy Holdings
Effective date | 2026-09-08
Purpose | Provide the feeder register snapshot and all 2026 inspection batches to date.
Coverage | See each dataset dictionary and summary. Missing numeric values are excluded, not zero.
Summary interpretation | Descriptive statistics of selected records only. Totals of percentages and adjustment values are not operating KPIs.
Introduction | Workbook of the distribution feeder register at August 31, 2026 and the pole inspection batches closed from January to August 2026. Prepared by the Pole Program for asset planning and for the draft pole management plan.
Sheets | Data 1 - feeder register: one row per in-service feeder with district, substation code, customers, overhead and underground circuit miles, voltage class, decade in service, automation, resiliency scope, last cycle trim, 2025 worst-feeder flag and pole count.
Sheets | Data 2 - pole inspection batches: one row per feeder section inspected by one contractor in one month, with outcomes and the number of poles installed before 1980.
Sheets | Summary - formula totals of each numeric column.
Feeder register | The register lists 436 feeders from 102 substations with 8,860 overhead and 5,400 underground circuit miles (38% underground). Automation: 162 feeders with reclosers only, 134 with none, 102 with IGSD loops and 38 with full automation. The 2025 worst-feeder flag marks the 32 feeders on the 2025 list.
Feeder register | Sedgewater owns about 290,400 distribution poles, about 94% of them wood. Last cycle trim dates follow the four-year vegetation cycle.
2026 pole inspections | Poles are inspected on a ten-year cycle, about 29,000 a year; the 2026 plan calls for 29,500 inspections. The 2026 cycle area is mainly Bayou, plus hardening-scope feeders in Harbor and Prairie.
2026 pole inspections | January to August: 19,650 poles inspected, 18,392 passed (93.6%), 413 restorable by bracing or reinforcement, 177 priority rejects and 668 standard rejects (4.3% rejected). 83% of the poles inspected were installed before 1980.
By district | Harbor 2,785 inspected, 4.3% rejected; Crossroads 292 inspected, 6.8% rejected; Bayou 14,056 inspected, 4.1% rejected; Prairie 2,517 inspected, 5.2% rejected.
Outcome codes | Pass; restorable (bracing or reinforcement); priority reject (replace within 90 days); standard reject (replace within 12 months). Batches record counts only; pole identifiers and locations are held in GIS.
Notes | Last cycle trim is blank for the four all-underground feeders.

## Summary
Dataset | Measure | Unit | Total | Mean | Records | Period start | Period end
Distribution feeder register (snapshot) | customers | delivery points | 684892 | 1570.8532 | 436 | 2026-08-31 | 2026-08-31
Distribution feeder register (snapshot) | oh_miles | miles | 8860 | 20.3211 | 436 | 2026-08-31 | 2026-08-31
Distribution feeder register (snapshot) | ug_miles | miles | 5400 | 12.3853 | 436 | 2026-08-31 | 2026-08-31
Distribution feeder register (snapshot) | poles | poles | 290400 | 666.055 | 436 | 2026-08-31 | 2026-08-31
Pole inspection batches, Jan-Aug 2026 | poles_inspected | poles | 19650 | 13.3764 | 1469 | 2026-01-01 | 2026-08-31
Pole inspection batches, Jan-Aug 2026 | poles_pass | poles | 18392 | 12.5201 | 1469 | 2026-01-01 | 2026-08-31
Pole inspection batches, Jan-Aug 2026 | poles_restorable | poles | 413 | 0.28114 | 1469 | 2026-01-01 | 2026-08-31
Pole inspection batches, Jan-Aug 2026 | poles_reject_priority | poles | 177 | 0.12049 | 1469 | 2026-01-01 | 2026-08-31
Pole inspection batches, Jan-Aug 2026 | poles_reject_standard | poles | 668 | 0.45473 | 1469 | 2026-01-01 | 2026-08-31
Pole inspection batches, Jan-Aug 2026 | poles_pre_1980 | poles | 16363 | 11.1389 | 1469 | 2026-01-01 | 2026-08-31

## Dictionary
Dataset | Field | Definition | Unit | Type | Reference
Distribution feeder register (snapshot) | feeder_code | Fictional feeder code, e.g., CR-S14-03 |  | id
Distribution feeder register (snapshot) | district | District |  | category
Distribution feeder register (snapshot) | substation_code | Fictional substation code (102 codes) |  | category
Distribution feeder register (snapshot) | customers | Delivery points served | delivery points | integer
Distribution feeder register (snapshot) | oh_miles | Overhead circuit miles | miles | number
Distribution feeder register (snapshot) | ug_miles | Underground circuit miles | miles | number
Distribution feeder register (snapshot) | voltage_class | Nominal voltage |  | category
Distribution feeder register (snapshot) | in_service_decade | Decade first energized |  | category
Distribution feeder register (snapshot) | automation | Sectionalizing automation |  | category
Distribution feeder register (snapshot) | resiliency_scope | 2026-2028 plan scope |  | category
Distribution feeder register (snapshot) | last_cycle_trim | Completion of last cyclic vegetation trim (ISO date) |  | category
Distribution feeder register (snapshot) | worst_feeder_2025 | On 2025 worst-performing list |  | category
Distribution feeder register (snapshot) | poles | Distribution poles on the feeder | poles | integer
Pole inspection batches, Jan-Aug 2026 | batch_id | Batch identifier PIB-000001 |  | id
Pole inspection batches, Jan-Aug 2026 | poles_inspected | Poles inspected in batch | poles | integer
Pole inspection batches, Jan-Aug 2026 | feeder_code | Feeder (FK feeders) |  | category
Pole inspection batches, Jan-Aug 2026 | district | District (copied) |  | category
Pole inspection batches, Jan-Aug 2026 | contractor_code | Inspection contractor (FK contractors) |  | category
Pole inspection batches, Jan-Aug 2026 | inspection_month | Month batch closed |  | date
Pole inspection batches, Jan-Aug 2026 | poles_pass | Passed | poles | integer
Pole inspection batches, Jan-Aug 2026 | poles_restorable | Reinforce or restore | poles | integer
Pole inspection batches, Jan-Aug 2026 | poles_reject_priority | Reject, priority replacement | poles | integer
Pole inspection batches, Jan-Aug 2026 | poles_reject_standard | Reject, standard replacement | poles | integer
Pole inspection batches, Jan-Aug 2026 | poles_pre_1980 | Poles installed before 1980 | poles | integer

## Data 1
feeder_code | district | substation_code | customers | oh_miles | ug_miles | voltage_class | in_service_decade | automation | resiliency_scope | last_cycle_trim | worst_feeder_2025 | poles
HB-S01-01 | Harbor | HB-S01 | 2056 | 26.6 | 11.5 | 12.47 kV | 1980s | IGSD loop | Pole hardening | 2026-08-15 | No | 872
HB-S01-02 | Harbor | HB-S01 | 594 | 10.4 | 5.8 | 12.47 kV | 1990s | Full automation | None | 2024-03-04 | No | 341
HB-S01-03 | Harbor | HB-S01 | 2914 | 20.7 | 17 | 12.47 kV | 1990s | Recloser only | Pole hardening | 2023-08-06 | No | 679
HB-S01-04 | Harbor | HB-S01 | 47 | 8.7 | 5 | 12.47 kV | 1990s | IGSD loop | None | 2024-05-02 | No | 285
HB-S01-05 | Harbor | HB-S01 | 3419 | 44.1 | 15.5 | 12.47 kV | 2000s | Full automation | None | 2023-04-27 | No | 1445
HB-S02-01 | Harbor | HB-S02 | 3150 | 25.9 | 16.6 | 12.47 kV | 1980s | IGSD loop | None | 2023-09-13 | No | 849
HB-S02-02 | Harbor | HB-S02 | 1304 | 45.4 | 6.6 | 12.47 kV | 1970s | Recloser only | None | 2025-11-28 | No | 1488
HB-S02-03 | Harbor | HB-S02 | 2433 | 11 | 9.3 | 12.47 kV | 2000s | None | None | 2023-02-07 | No | 361
HB-S03-01 | Harbor | HB-S03 | 1241 | 18.7 | 10.2 | 12.47 kV | 1980s | None | Multiple measures | 2026-07-26 | No | 613
HB-S03-02 | Harbor | HB-S03 | 1246 | 13.3 | 8.9 | 12.47 kV | 1980s | None | None | 2022-04-03 | No | 436
HB-S03-03 | Harbor | HB-S03 | 1708 | 10.1 | 8.5 | 12.47 kV | 1970s | Full automation | None | 2025-10-25 | No | 331
HB-S04-01 | Harbor | HB-S04 | 1465 | 12.8 | 11.7 | 12.47 kV | 1990s | None | None | 2026-07-21 | No | 420
HB-S04-02 | Harbor | HB-S04 | 863 | 10.3 | 20.5 | 12.47 kV | 1980s | Recloser only | Multiple measures | 2025-09-15 | No | 338
HB-S05-01 | Harbor | HB-S05 | 2319 | 22.8 | 11.4 | 12.47 kV | 1990s | IGSD loop | None | 2025-10-29 | No | 747
HB-S05-02 | Harbor | HB-S05 | 944 | 9.8 | 4.7 | 12.47 kV | 2020s | IGSD loop | None | 2023-07-27 | No | 321
HB-S05-03 | Harbor | HB-S05 | 1273 | 31.5 | 14.5 | 12.47 kV | 2010s | Recloser only | None | 2022-05-01 | No | 1032
HB-S05-04 | Harbor | HB-S05 | 979 | 15.7 | 6.3 | 12.47 kV | 1990s | Recloser only | None | 2025-02-25 | No | 515
HB-S05-05 | Harbor | HB-S05 | 1917 | 9.3 | 4.5 | 12.47 kV | 1980s | None | None | 2026-05-23 | No | 305
HB-S05-06 | Harbor | HB-S05 | 2796 | 10.1 | 5.5 | 12.47 kV | 1990s | None | Automation | 2025-05-10 | No | 331
HB-S06-01 | Harbor | HB-S06 | 1382 | 18.5 | 12 | 12.47 kV | 1980s | Recloser only | None | 2025-05-30 | No | 606
HB-S06-02 | Harbor | HB-S06 | 1873 | 26.7 | 4.7 | 12.47 kV | 1990s | Full automation | Pole hardening | 2024-02-21 | No | 875
HB-S06-03 | Harbor | HB-S06 | 58 | 15.1 | 8.1 | 12.47 kV | 1970s | Recloser only | None | 2026-08-19 | No | 495
HB-S06-04 | Harbor | HB-S06 | 1770 | 17.7 | 13.2 | 12.47 kV | 2010s | Recloser only | None | 2023-05-13 | No | 580
HB-S06-05 | Harbor | HB-S06 | 1173 | 5.4 | 9.9 | 12.47 kV | 1970s | Recloser only | None | 2024-03-10 | No | 177
HB-S07-01 | Harbor | HB-S07 | 33 | 9.6 | 4.9 | 12.47 kV | 2000s | None | Multiple measures | 2025-05-23 | No | 315
HB-S07-02 | Harbor | HB-S07 | 2362 | 25.5 | 11.7 | 12.47 kV | 1980s | Recloser only | None | 2026-08-02 | No | 836
HB-S07-03 | Harbor | HB-S07 | 1234 | 11.6 | 11.5 | 12.47 kV | 1970s | Recloser only | None | 2025-03-05 | No | 380
HB-S07-04 | Harbor | HB-S07 | 1177 | 13.6 | 6.1 | 12.47 kV | 2000s | Recloser only | Automation | 2026-07-03 | No | 446
HB-S07-05 | Harbor | HB-S07 | 1129 | 17.7 | 12.8 | 12.47 kV | 2000s | IGSD loop | Pole hardening | 2022-04-29 | No | 580
HB-S08-01 | Harbor | HB-S08 | 1426 | 12.5 | 9.2 | 12.47 kV | 1990s | Recloser only | Multiple measures | 2025-12-16 | No | 410
HB-S08-02 | Harbor | HB-S08 | 1062 | 7.6 | 9.2 | 12.47 kV | 1980s | IGSD loop | None | 2022-06-30 | No | 249
HB-S08-03 | Harbor | HB-S08 | 879 | 5.2 | 5.6 | 12.47 kV | 1970s | Full automation | None | 2023-09-23 | SAIFI | 170
HB-S08-04 | Harbor | HB-S08 | 2437 | 9.2 | 14.3 | 12.47 kV | 1990s | None | None | 2023-04-28 | No | 302
HB-S08-05 | Harbor | HB-S08 | 1342 | 9.4 | 7.2 | 12.47 kV | 2010s | IGSD loop | None | 2026-08-23 | No | 308
HB-S09-01 | Harbor | HB-S09 | 940 | 7.4 | 9.6 | 12.47 kV | 1990s | IGSD loop | None | 2024-05-04 | No | 243
HB-S09-02 | Harbor | HB-S09 | 3985 | 19.6 | 19.8 | 12.47 kV | 2010s | Recloser only | Pole hardening | 2023-04-07 | No | 642
HB-S09-03 | Harbor | HB-S09 | 1544 | 48.9 | 11.2 | 12.47 kV | 1980s | Full automation | None | 2025-07-21 | No | 1603
HB-S09-04 | Harbor | HB-S09 | 943 | 15 | 5.4 | 12.47 kV | 1980s | None | None | 2025-05-20 | No | 492
HB-S09-05 | Harbor | HB-S09 | 1248 | 19 | 6.3 | 12.47 kV | 1970s | None | None | 2024-09-21 | No | 623
HB-S10-01 | Harbor | HB-S10 | 1745 | 10.1 | 5.6 | 12.47 kV | 1970s | None | None | 2025-05-22 | No | 331
HB-S10-02 | Harbor | HB-S10 | 1582 | 26 | 9.7 | 12.47 kV | 1990s | IGSD loop | None | 2025-09-16 | No | 852
HB-S10-03 | Harbor | HB-S10 | 4704 | 19.8 | 15.7 | 12.47 kV | 1970s | IGSD loop | Partial undergrounding | 2023-03-14 | No | 649
HB-S11-01 | Harbor | HB-S11 | 1082 | 58.4 | 4.9 | 12.47 kV | 2000s | IGSD loop | Pole hardening | 2025-11-23 | No | 1914
HB-S11-02 | Harbor | HB-S11 | 32 | 4.5 | 3.3 | 12.47 kV | 2010s | Recloser only | Multiple measures | 2025-12-09 | No | 148
HB-S11-03 | Harbor | HB-S11 | 2320 | 25.3 | 10.6 | 12.47 kV | 2000s | None | Automation | 2022-03-26 | No | 829
HB-S12-01 | Harbor | HB-S12 | 2513 | 18.1 | 9.2 | 12.47 kV | 1990s | IGSD loop | Automation | 2025-08-15 | No | 593
HB-S12-02 | Harbor | HB-S12 | 4703 | 54.5 | 28.9 | 12.47 kV | 1960s | None | None | 2024-01-19 | No | 1786
HB-S12-03 | Harbor | HB-S12 | 1672 | 33.3 | 13 | 12.47 kV | 2000s | Recloser only | Automation | 2026-04-08 | No | 1091
HB-S13-01 | Harbor | HB-S13 | 1084 | 21.9 | 6.1 | 12.47 kV | 2000s | IGSD loop | None | 2026-08-17 | No | 718
HB-S13-02 | Harbor | HB-S13 | 2552 | 31.1 | 7.3 | 12.47 kV | 2010s | Recloser only | None | 2026-06-24 | No | 1019
HB-S14-01 | Harbor | HB-S14 | 1413 | 11.9 | 5.4 | 12.47 kV | 2000s | None | Partial undergrounding | 2022-09-07 | No | 390
HB-S14-02 | Harbor | HB-S14 | 543 | 12.7 | 5.3 | 12.47 kV | 1990s | None | Pole hardening | 2024-05-29 | No | 416
HB-S14-03 | Harbor | HB-S14 | 1301 | 20.7 | 4.9 | 12.47 kV | 1970s | IGSD loop | Pole hardening | 2023-01-23 | No | 679
HB-S14-04 | Harbor | HB-S14 | 2319 | 3.7 | 9.6 | 12.47 kV | 2010s | Recloser only | Pole hardening | 2022-04-12 | No | 121
HB-S15-01 | Harbor | HB-S15 | 972 | 4.9 | 3.3 | 12.47 kV | 2020s | Recloser only | None | 2025-11-07 | No | 161
HB-S15-02 | Harbor | HB-S15 | 1067 | 22.6 | 5.7 | 12.47 kV | 2020s | None | None | 2025-10-18 | No | 741
HB-S15-03 | Harbor | HB-S15 | 2148 | 16.4 | 8.8 | 12.47 kV | 1990s | Full automation | None | 2022-06-26 | No | 538
HB-S16-01 | Harbor | HB-S16 | 1839 | 18.7 | 9.8 | 12.47 kV | 1970s | Recloser only | Automation | 2026-06-15 | No | 613
HB-S16-02 | Harbor | HB-S16 | 41 | 12.9 | 7.2 | 12.47 kV | 2020s | IGSD loop | None | 2022-09-06 | No | 423
HB-S16-03 | Harbor | HB-S16 | 1014 | 9.5 | 10.6 | 12.47 kV | 2000s | Full automation | None | 2025-10-07 | No | 311
HB-S16-04 | Harbor | HB-S16 | 788 | 14.5 | 9.7 | 12.47 kV | 1970s | None | Multiple measures | 2023-09-09 | No | 475
HB-S16-05 | Harbor | HB-S16 | 894 | 7.7 | 9.8 | 12.47 kV | 1980s | Recloser only | None | 2023-01-28 | No | 252
HB-S17-01 | Harbor | HB-S17 | 1623 | 18.7 | 14.4 | 12.47 kV | 1970s | IGSD loop | None | 2022-07-06 | No | 613
HB-S17-02 | Harbor | HB-S17 | 4706 | 36.3 | 12.1 | 12.47 kV | 1980s | IGSD loop | Automation | 2026-06-16 | No | 1190
HB-S17-03 | Harbor | HB-S17 | 1953 | 16.1 | 14.6 | 12.47 kV | 1970s | Recloser only | None | 2026-05-27 | No | 528
HB-S18-01 | Harbor | HB-S18 | 2519 | 28.6 | 12.8 | 12.47 kV | 2000s | None | None | 2022-11-07 | No | 937
HB-S18-02 | Harbor | HB-S18 | 2030 | 18.3 | 9.7 | 12.47 kV | 1990s | Recloser only | None | 2025-06-07 | No | 600
HB-S18-03 | Harbor | HB-S18 | 2268 | 20.7 | 29.3 | 12.47 kV | 1970s | IGSD loop | Automation | 2026-05-26 | No | 678
HB-S18-04 | Harbor | HB-S18 | 58 | 12.4 | 4.8 | 12.47 kV | 2010s | Recloser only | Partial undergrounding | 2022-05-31 | No | 406
HB-S19-01 | Harbor | HB-S19 | 1425 | 27.3 | 10.4 | 12.47 kV | 1970s | IGSD loop | None | 2026-08-23 | No | 895
HB-S19-02 | Harbor | HB-S19 | 1761 | 21 | 8.1 | 12.47 kV | 1960s | IGSD loop | None | 2023-11-15 | No | 688
HB-S19-03 | Harbor | HB-S19 | 844 | 20.3 | 3.2 | 12.47 kV | 1970s | Recloser only | None | 2026-07-03 | No | 665
HB-S19-04 | Harbor | HB-S19 | 2053 | 15.2 | 13.1 | 12.47 kV | 1980s | None | None | 2026-05-13 | No | 498
HB-S20-01 | Harbor | HB-S20 | 1889 | 8.5 | 9.6 | 12.47 kV | 2000s | Full automation | Automation | 2025-07-17 | No | 279
HB-S20-02 | Harbor | HB-S20 | 1494 | 6.9 | 6.9 | 12.47 kV | 1960s | IGSD loop | Pole hardening | 2023-04-12 | No | 226
HB-S20-03 | Harbor | HB-S20 | 1771 | 13.6 | 2.3 | 12.47 kV | 1990s | Recloser only | Automation | 2026-05-10 | No | 446
HB-S20-04 | Harbor | HB-S20 | 1493 | 15 | 6 | 12.47 kV | 1990s | Recloser only | None | 2025-05-27 | No | 492
HB-S20-05 | Harbor | HB-S20 | 1726 | 9.5 | 11.6 | 12.47 kV | 1960s | Recloser only | None | 2025-11-11 | No | 311
CR-S01-01 | Crossroads | CR-S01 | 939 | 11.9 | 9.3 | 12.47 kV | 2010s | Recloser only | None | 2023-11-09 | No | 390
CR-S01-02 | Crossroads | CR-S01 | 911 | 9.1 | 21 | 12.47 kV | 2010s | IGSD loop | None | 2026-07-06 | No | 298
CR-S01-03 | Crossroads | CR-S01 | 2083 | 22.8 | 25.5 | 12.47 kV | 2010s | IGSD loop | Pole hardening | 2024-04-22 | No | 747
CR-S01-04 | Crossroads | CR-S01 | 868 | 7 | 18.2 | 12.47 kV | 2010s | Recloser only | None | 2026-03-11 | No | 229
CR-S02-01 | Crossroads | CR-S02 | 1526 | 14.8 | 13.8 | 12.47 kV | 2000s | IGSD loop | None | 2025-08-28 | No | 485
CR-S02-02 | Crossroads | CR-S02 | 726 | 12 | 8 | 12.47 kV | 2010s | Full automation | None | 2023-07-10 | No | 393
CR-S02-03 | Crossroads | CR-S02 | 2238 | 19.9 | 19 | 12.47 kV | 2000s | None | Pole hardening | 2025-08-02 | No | 652
CR-S02-04 | Crossroads | CR-S02 | 997 | 3 | 15.3 | 12.47 kV | 2010s | Recloser only | None | 2023-03-08 | No | 98
CR-S02-05 | Crossroads | CR-S02 | 1817 | 7.4 | 18.3 | 12.47 kV | 2010s | Recloser only | None | 2023-08-02 | No | 243
CR-S03-01 | Crossroads | CR-S03 | 1712 | 14.6 | 13.9 | 12.47 kV | 2010s | None | None | 2023-05-21 | No | 479
CR-S03-02 | Crossroads | CR-S03 | 1527 | 11.7 | 11.8 | 12.47 kV | 2000s | IGSD loop | Automation | 2026-03-08 | No | 384
CR-S03-03 | Crossroads | CR-S03 | 973 | 5.5 | 12.6 | 12.47 kV | 2000s | IGSD loop | None | 2023-06-02 | No | 180
CR-S04-01 | Crossroads | CR-S04 | 2031 | 12.5 | 17.5 | 12.47 kV | 2000s | None | Multiple measures | 2022-11-04 | No | 410
CR-S04-02 | Crossroads | CR-S04 | 1950 | 8.8 | 36.2 | 12.47 kV | 1990s | IGSD loop | Automation | 2024-09-30 | SAIFI | 288
CR-S04-03 | Crossroads | CR-S04 | 2150 | 15.9 | 32.9 | 12.47 kV | 1990s | None | None | 2025-05-05 | Both | 521
CR-S04-04 | Crossroads | CR-S04 | 1071 | 9 | 10 | 12.47 kV | 2000s | IGSD loop | None | 2024-03-13 | No | 295
CR-S04-05 | Crossroads | CR-S04 | 1188 | 15.2 | 23.6 | 12.47 kV | 2000s | IGSD loop | Multiple measures | 2025-04-05 | No | 498
CR-S04-06 | Crossroads | CR-S04 | 3486 | 18.7 | 31.3 | 12.47 kV | 2010s | Full automation | None | 2024-08-24 | No | 613
CR-S05-01 | Crossroads | CR-S05 | 1479 | 18.4 | 31.7 | 12.47 kV | 2020s | Recloser only | Multiple measures | 2022-06-08 | No | 603
CR-S05-02 | Crossroads | CR-S05 | 1376 | 11.2 | 17.6 | 12.47 kV | 1990s | Recloser only | Automation | 2026-07-21 | No | 367
CR-S05-03 | Crossroads | CR-S05 | 1470 | 17.4 | 10 | 12.47 kV | 2000s | IGSD loop | None | 2022-03-12 | No | 570
CR-S05-04 | Crossroads | CR-S05 | 805 | 12.7 | 8.4 | 12.47 kV | 2000s | IGSD loop | Automation | 2022-06-23 | No | 416
CR-S05-05 | Crossroads | CR-S05 | 888 | 7.6 | 27.9 | 12.47 kV | 2010s | IGSD loop | None | 2022-02-17 | No | 249
CR-S05-06 | Crossroads | CR-S05 | 820 | 4.3 | 18.1 | 12.47 kV | 1960s | Recloser only | Multiple measures | 2025-10-21 | No | 141
CR-S06-01 | Crossroads | CR-S06 | 806 | 12.7 | 11.5 | 12.47 kV | 1980s | None | Automation | 2026-07-05 | No | 416
CR-S06-02 | Crossroads | CR-S06 | 2385 | 18.3 | 56.8 | 12.47 kV | 1990s | IGSD loop | None | 2022-04-06 | No | 600
CR-S06-03 | Crossroads | CR-S06 | 1536 | 6.1 | 19.8 | 12.47 kV | 2020s | Full automation | None | 2026-08-11 | No | 200
CR-S07-01 | Crossroads | CR-S07 | 1727 | 14.7 | 23.4 | 12.47 kV | 2000s | IGSD loop | Partial undergrounding | 2026-02-06 | No | 482
CR-S07-02 | Crossroads | CR-S07 | 1835 | 7.6 | 33.2 | 12.47 kV | 1980s | Recloser only | Automation | 2024-07-21 | No | 249
CR-S07-03 | Crossroads | CR-S07 | 2534 | 18.8 | 23.7 | 12.47 kV | 2010s | Full automation | None | 2026-06-11 | No | 616
CR-S07-04 | Crossroads | CR-S07 | 652 | 8.3 | 7.2 | 12.47 kV | 2010s | IGSD loop | None | 2022-11-05 | No | 272
CR-S07-05 | Crossroads | CR-S07 | 2063 | 12.2 | 14.3 | 12.47 kV | 1990s | Full automation | None | 2025-08-05 | No | 400
CR-S07-06 | Crossroads | CR-S07 | 902 | 6.1 | 11 | 12.47 kV | 2020s | Recloser only | None | 2023-02-04 | No | 200
CR-S07-07 | Crossroads | CR-S07 | 2797 | 5.8 | 24.7 | 12.47 kV | 2010s | IGSD loop | Partial undergrounding | 2022-03-04 | No | 190
CR-S08-01 | Crossroads | CR-S08 | 1078 | 15.3 | 5.9 | 12.47 kV | 2000s | Full automation | Multiple measures | 2025-11-08 | No | 502
CR-S08-02 | Crossroads | CR-S08 | 1960 | 10.9 | 28.1 | 12.47 kV | 2010s | Recloser only | None | 2026-07-27 | No | 357
CR-S08-03 | Crossroads | CR-S08 | 1035 | 0 | 24.9 | 12.47 kV | 2020s | IGSD loop | None |  | No | 0
CR-S08-04 | Crossroads | CR-S08 | 884 | 12.7 | 9.6 | 12.47 kV | 2020s | Full automation | None | 2024-05-17 | No | 416
CR-S08-05 | Crossroads | CR-S08 | 856 | 12.7 | 15.1 | 12.47 kV | 2010s | None | None | 2025-03-23 | No | 416
CR-S08-06 | Crossroads | CR-S08 | 1989 | 23 | 31.4 | 12.47 kV | 2010s | None | None | 2026-05-02 | No | 754
CR-S09-01 | Crossroads | CR-S09 | 3140 | 13.7 | 34.9 | 12.47 kV | 2010s | IGSD loop | None | 2026-02-24 | SAIFI | 449
CR-S09-02 | Crossroads | CR-S09 | 918 | 11.5 | 15.6 | 12.47 kV | 2020s | None | None | 2022-10-27 | No | 377
CR-S09-03 | Crossroads | CR-S09 | 1489 | 28.9 | 10.2 | 12.47 kV | 2000s | Full automation | None | 2023-05-12 | No | 947
CR-S09-04 | Crossroads | CR-S09 | 1326 | 12.1 | 39.3 | 12.47 kV | 2000s | None | Automation | 2026-01-30 | No | 397
CR-S09-05 | Crossroads | CR-S09 | 871 | 6 | 16.9 | 12.47 kV | 2000s | Full automation | Pole hardening | 2026-04-02 | No | 197
CR-S10-01 | Crossroads | CR-S10 | 1282 | 16.6 | 13.4 | 12.47 kV | 1980s | Full automation | None | 2023-04-19 | No | 544
CR-S10-02 | Crossroads | CR-S10 | 1475 | 4.8 | 18.3 | 12.47 kV | 2000s | Full automation | Multiple measures | 2026-02-16 | No | 157
CR-S10-03 | Crossroads | CR-S10 | 1655 | 16.3 | 12.4 | 12.47 kV | 2020s | Recloser only | Automation | 2025-11-14 | No | 534
CR-S11-01 | Crossroads | CR-S11 | 2550 | 27.7 | 34.8 | 12.47 kV | 2000s | IGSD loop | Automation | 2026-07-06 | No | 908
CR-S11-02 | Crossroads | CR-S11 | 1074 | 5.6 | 9.2 | 12.47 kV | 2000s | IGSD loop | Pole hardening | 2025-09-06 | No | 184
CR-S12-01 | Crossroads | CR-S12 | 2117 | 18.5 | 23.5 | 12.47 kV | 2020s | None | None | 2022-08-27 | No | 606
CR-S12-02 | Crossroads | CR-S12 | 873 | 3.2 | 9 | 12.47 kV | 1990s | Recloser only | Multiple measures | 2022-03-10 | No | 105
CR-S12-03 | Crossroads | CR-S12 | 1129 | 15.8 | 6.1 | 12.47 kV | 1970s | Recloser only | Partial undergrounding | 2025-08-27 | No | 518
CR-S13-01 | Crossroads | CR-S13 | 1116 | 21 | 16 | 12.47 kV | 2000s | IGSD loop | None | 2026-07-08 | No | 688
CR-S13-02 | Crossroads | CR-S13 | 1299 | 6.5 | 22.7 | 12.47 kV | 2010s | None | None | 2025-03-12 | No | 213
CR-S13-03 | Crossroads | CR-S13 | 1830 | 3.6 | 24.9 | 12.47 kV | 1990s | Recloser only | None | 2026-05-07 | No | 118
CR-S13-04 | Crossroads | CR-S13 | 1565 | 6 | 13.6 | 12.47 kV | 2010s | Recloser only | None | 2025-11-05 | No | 197
CR-S13-05 | Crossroads | CR-S13 | 1678 | 10.5 | 16.2 | 12.47 kV | 2010s | None | Automation | 2026-08-18 | No | 344
CR-S13-06 | Crossroads | CR-S13 | 1542 | 15.4 | 14.6 | 12.47 kV | 2010s | Recloser only | Pole hardening | 2025-09-09 | No | 505
CR-S14-01 | Crossroads | CR-S14 | 1821 | 17.7 | 16.4 | 12.47 kV | 1990s | Recloser only | None | 2024-10-25 | No | 580
CR-S14-02 | Crossroads | CR-S14 | 3874 | 19.6 | 38.2 | 12.47 kV | 2000s | Full automation | None | 2026-06-11 | Both | 642
CR-S14-03 | Crossroads | CR-S14 | 2037 | 27.5 | 18.1 | 12.47 kV | 2010s | Recloser only | None | 2026-01-02 | No | 901
CR-S14-04 | Crossroads | CR-S14 | 1323 | 12.1 | 13.7 | 12.47 kV | 1980s | IGSD loop | None | 2026-04-06 | No | 397
CR-S14-05 | Crossroads | CR-S14 | 2062 | 16 | 24.5 | 12.47 kV | 2000s | IGSD loop | Multiple measures | 2024-08-18 | No | 524
CR-S14-06 | Crossroads | CR-S14 | 542 | 11.2 | 14.3 | 12.47 kV | 2000s | Recloser only | None | 2022-05-27 | No | 367
CR-S15-01 | Crossroads | CR-S15 | 2248 | 5.4 | 24.5 | 12.47 kV | 2000s | Recloser only | None | 2024-11-15 | No | 177
CR-S15-02 | Crossroads | CR-S15 | 1727 | 4.9 | 11.7 | 12.47 kV | 2020s | Recloser only | Multiple measures | 2025-10-29 | No | 161
CR-S15-03 | Crossroads | CR-S15 | 1853 | 7 | 12.2 | 12.47 kV | 1990s | Recloser only | None | 2026-07-13 | No | 229
CR-S16-01 | Crossroads | CR-S16 | 1283 | 3.4 | 22.2 | 12.47 kV | 2010s | IGSD loop | Pole hardening | 2022-02-28 | No | 111
CR-S16-02 | Crossroads | CR-S16 | 4175 | 11 | 12.9 | 12.47 kV | 2000s | IGSD loop | None | 2022-07-28 | No | 361
CR-S16-03 | Crossroads | CR-S16 | 1550 | 7.3 | 22 | 12.47 kV | 2000s | Recloser only | None | 2023-04-02 | No | 239
CR-S16-04 | Crossroads | CR-S16 | 2427 | 14.4 | 21 | 12.47 kV | 2020s | Recloser only | None | 2026-04-20 | No | 472
CR-S16-05 | Crossroads | CR-S16 | 1147 | 14.6 | 16.9 | 12.47 kV | 1990s | IGSD loop | Automation | 2026-04-26 | No | 479
CR-S16-06 | Crossroads | CR-S16 | 992 | 5.4 | 18 | 12.47 kV | 2000s | IGSD loop | None | 2023-08-02 | No | 177
CR-S17-01 | Crossroads | CR-S17 | 4716 | 16.7 | 44 | 12.47 kV | 2000s | IGSD loop | None | 2026-07-01 | No | 547
CR-S17-02 | Crossroads | CR-S17 | 738 | 14.2 | 10.7 | 12.47 kV | 2010s | Recloser only | Pole hardening | 2024-10-31 | No | 465
CR-S17-03 | Crossroads | CR-S17 | 2117 | 5.7 | 22.2 | 12.47 kV | 1990s | None | None | 2025-10-24 | No | 187
CR-S18-01 | Crossroads | CR-S18 | 1112 | 5.8 | 12.6 | 12.47 kV | 1980s | Full automation | None | 2026-08-04 | No | 190
CR-S18-02 | Crossroads | CR-S18 | 1024 | 3.3 | 7.4 | 12.47 kV | 1990s | Full automation | Pole hardening | 2025-08-27 | No | 108
CR-S18-03 | Crossroads | CR-S18 | 1782 | 8.9 | 14.6 | 12.47 kV | 1980s | Recloser only | None | 2024-04-22 | No | 292
CR-S18-04 | Crossroads | CR-S18 | 2559 | 16.5 | 15.5 | 12.47 kV | 1990s | Recloser only | None | 2025-11-02 | No | 541
CR-S18-05 | Crossroads | CR-S18 | 1049 | 14.4 | 9.4 | 12.47 kV | 1990s | Recloser only | None | 2023-09-17 | No | 472
CR-S18-06 | Crossroads | CR-S18 | 1168 | 8 | 8.1 | 12.47 kV | 2000s | IGSD loop | None | 2023-06-11 | No | 262
CR-S19-01 | Crossroads | CR-S19 | 966 | 12.5 | 9.6 | 12.47 kV | 2000s | Full automation | None | 2026-03-12 | No | 410
CR-S19-02 | Crossroads | CR-S19 | 1449 | 7.7 | 9.5 | 12.47 kV | 1990s | IGSD loop | Multiple measures | 2026-07-01 | No | 252
CR-S19-03 | Crossroads | CR-S19 | 3373 | 33.1 | 20.4 | 12.47 kV | 2000s | None | None | 2024-11-07 | No | 1085
CR-S19-04 | Crossroads | CR-S19 | 2852 | 14.9 | 30.3 | 12.47 kV | 2010s | None | None | 2025-08-29 | No | 488
CR-S20-01 | Crossroads | CR-S20 | 1528 | 12.1 | 13.7 | 12.47 kV | 1970s | Full automation | None | 2026-08-02 | No | 397
CR-S20-02 | Crossroads | CR-S20 | 4112 | 10.4 | 48.4 | 12.47 kV | 2010s | Full automation | Multiple measures | 2025-05-27 | SAIDI | 341
CR-S20-03 | Crossroads | CR-S20 | 1501 | 27.2 | 9.4 | 12.47 kV | 1970s | Recloser only | None | 2026-07-27 | No | 892
CR-S20-04 | Crossroads | CR-S20 | 1292 | 4.8 | 20.5 | 12.47 kV | 2020s | None | Automation | 2025-04-04 | No | 157
CR-S20-05 | Crossroads | CR-S20 | 1972 | 16.6 | 20.1 | 12.47 kV | 1990s | Full automation | None | 2023-11-03 | No | 544
CR-S21-01 | Crossroads | CR-S21 | 2285 | 14.1 | 27 | 12.47 kV | 2000s | Recloser only | Automation | 2025-08-25 | No | 462
CR-S21-02 | Crossroads | CR-S21 | 1712 | 5.8 | 19.6 | 12.47 kV | 1980s | IGSD loop | None | 2022-04-17 | No | 190
CR-S21-03 | Crossroads | CR-S21 | 4248 | 31.4 | 30.8 | 12.47 kV | 1990s | IGSD loop | None | 2025-10-16 | No | 1029
CR-S22-01 | Crossroads | CR-S22 | 2257 | 41.9 | 23.4 | 12.47 kV | 1990s | None | Multiple measures | 2026-07-02 | No | 1373
CR-S22-02 | Crossroads | CR-S22 | 1789 | 16.4 | 19.4 | 12.47 kV | 2010s | IGSD loop | Pole hardening | 2025-09-27 | No | 538
CR-S22-03 | Crossroads | CR-S22 | 3207 | 7 | 22.2 | 12.47 kV | 1990s | Recloser only | None | 2023-11-13 | No | 229
CR-S22-04 | Crossroads | CR-S22 | 1395 | 15.1 | 23.8 | 12.47 kV | 2020s | IGSD loop | None | 2022-09-07 | Both | 495
CR-S23-01 | Crossroads | CR-S23 | 1450 | 11.6 | 14.9 | 12.47 kV | 2010s | Recloser only | None | 2026-03-09 | No | 380
CR-S23-02 | Crossroads | CR-S23 | 2716 | 37.3 | 23.4 | 12.47 kV | 1970s | None | Multiple measures | 2023-03-15 | No | 1223
CR-S23-03 | Crossroads | CR-S23 | 1184 | 7.8 | 17 | 12.47 kV | 2010s | Full automation | None | 2023-01-29 | No | 256
CR-S23-04 | Crossroads | CR-S23 | 1279 | 8.2 | 13.2 | 12.47 kV | 1980s | None | None | 2026-05-14 | No | 269
CR-S23-05 | Crossroads | CR-S23 | 1861 | 10 | 14.7 | 12.47 kV | 1980s | Full automation | None | 2022-07-01 | No | 328
CR-S24-01 | Crossroads | CR-S24 | 1822 | 3.7 | 23.5 | 12.47 kV | 2000s | Full automation | None | 2026-05-20 | No | 121
CR-S24-02 | Crossroads | CR-S24 | 992 | 0 | 50.2 | 12.47 kV | 2020s | None | None |  | No | 0
CR-S24-03 | Crossroads | CR-S24 | 2059 | 25 | 14 | 12.47 kV | 2000s | None | Partial undergrounding | 2025-09-11 | No | 819
CR-S24-04 | Crossroads | CR-S24 | 1802 | 15.8 | 24 | 12.47 kV | 2000s | IGSD loop | None | 2023-05-14 | No | 518
CR-S25-01 | Crossroads | CR-S25 | 2020 | 17.6 | 26.6 | 12.47 kV | 2010s | Recloser only | None | 2022-07-30 | No | 577
CR-S25-02 | Crossroads | CR-S25 | 1216 | 12.8 | 7 | 12.47 kV | 2010s | None | None | 2026-05-17 | No | 420
CR-S25-03 | Crossroads | CR-S25 | 2077 | 5.1 | 33.2 | 12.47 kV | 2010s | Recloser only | None | 2022-04-09 | No | 167
CR-S25-04 | Crossroads | CR-S25 | 1092 | 14.3 | 16 | 12.47 kV | 1990s | None | Multiple measures | 2026-08-18 | No | 469
CR-S25-05 | Crossroads | CR-S25 | 1252 | 8.6 | 15.4 | 12.47 kV | 2000s | Recloser only | Pole hardening | 2025-11-27 | No | 282
CR-S25-06 | Crossroads | CR-S25 | 1090 | 14.8 | 16.2 | 12.47 kV | 1990s | None | Pole hardening | 2024-05-07 | No | 485
CR-S26-01 | Crossroads | CR-S26 | 903 | 8 | 6.6 | 12.47 kV | 2000s | Recloser only | None | 2024-03-12 | No | 262
CR-S26-02 | Crossroads | CR-S26 | 2385 | 20.8 | 23.9 | 12.47 kV | 1980s | None | None | 2025-10-19 | No | 682
CR-S26-03 | Crossroads | CR-S26 | 1516 | 9.8 | 24.3 | 12.47 kV | 2010s | Recloser only | None | 2026-03-27 | No | 321
CR-S26-04 | Crossroads | CR-S26 | 959 | 10.2 | 9.9 | 12.47 kV | 1970s | Recloser only | Partial undergrounding | 2022-03-14 | No | 334
CR-S26-05 | Crossroads | CR-S26 | 530 | 22.8 | 10.1 | 12.47 kV | 2010s | IGSD loop | Pole hardening | 2022-03-18 | No | 747
CR-S26-06 | Crossroads | CR-S26 | 1425 | 10.6 | 14 | 12.47 kV | 2010s | Recloser only | None | 2023-08-20 | No | 347
CR-S27-01 | Crossroads | CR-S27 | 989 | 8.2 | 7.6 | 12.47 kV | 2000s | Recloser only | Multiple measures | 2024-01-29 | No | 269
CR-S27-02 | Crossroads | CR-S27 | 2947 | 11.2 | 30.6 | 12.47 kV | 2020s | Recloser only | Partial undergrounding | 2023-02-19 | No | 367
CR-S27-03 | Crossroads | CR-S27 | 1485 | 0 | 58.3 | 12.47 kV | 1990s | Recloser only | None |  | No | 0
CR-S27-04 | Crossroads | CR-S27 | 3673 | 8.2 | 18.2 | 12.47 kV | 2020s | IGSD loop | Automation | 2026-07-06 | No | 269
CR-S28-01 | Crossroads | CR-S28 | 1966 | 0 | 58.1 | 12.47 kV | 2000s | Full automation | None |  | No | 0
CR-S28-02 | Crossroads | CR-S28 | 1427 | 9.2 | 10.5 | 12.47 kV | 2010s | Full automation | None | 2025-08-23 | No | 302
CR-S28-03 | Crossroads | CR-S28 | 3074 | 4.9 | 15.5 | 12.47 kV | 2020s | IGSD loop | Pole hardening | 2026-02-10 | No | 161
CR-S28-04 | Crossroads | CR-S28 | 1075 | 11.4 | 13.8 | 12.47 kV | 2010s | Recloser only | None | 2025-08-15 | No | 374
CR-S29-01 | Crossroads | CR-S29 | 1252 | 5.1 | 7.5 | 12.47 kV | 2010s | Recloser only | None | 2023-06-08 | No | 167
CR-S29-02 | Crossroads | CR-S29 | 1611 | 7.2 | 15.4 | 12.47 kV | 2010s | IGSD loop | Pole hardening | 2026-07-28 | No | 236
CR-S29-03 | Crossroads | CR-S29 | 1422 | 10.6 | 23.6 | 12.47 kV | 2000s | IGSD loop | None | 2024-11-08 | No | 347
CR-S30-01 | Crossroads | CR-S30 | 1461 | 7 | 14.1 | 12.47 kV | 2020s | IGSD loop | None | 2026-05-25 | No | 229
CR-S30-02 | Crossroads | CR-S30 | 1863 | 8.9 | 13.6 | 12.47 kV | 1960s | IGSD loop | Pole hardening | 2024-03-02 | No | 292
CR-S30-03 | Crossroads | CR-S30 | 1482 | 13.8 | 20.6 | 12.47 kV | 2000s | Full automation | Automation | 2023-11-07 | No | 452
CR-S30-04 | Crossroads | CR-S30 | 878 | 6.4 | 22.7 | 12.47 kV | 1990s | Full automation | None | 2022-08-23 | No | 210
CR-S30-05 | Crossroads | CR-S30 | 1304 | 12.6 | 15.2 | 12.47 kV | 2010s | IGSD loop | Pole hardening | 2026-06-30 | No | 413
CR-S30-06 | Crossroads | CR-S30 | 1279 | 3.9 | 25.4 | 12.47 kV | 2020s | Recloser only | None | 2022-07-29 | No | 128
CR-S30-07 | Crossroads | CR-S30 | 1620 | 16.9 | 15.2 | 12.47 kV | 1970s | Recloser only | None | 2025-02-28 | No | 554
CR-S31-01 | Crossroads | CR-S31 | 1968 | 10 | 16.1 | 12.47 kV | 2010s | IGSD loop | Pole hardening | 2025-11-01 | No | 328
CR-S31-02 | Crossroads | CR-S31 | 3068 | 18.2 | 9.1 | 12.47 kV | 2010s | Recloser only | None | 2026-05-27 | No | 597
CR-S31-03 | Crossroads | CR-S31 | 1089 | 17.1 | 18.2 | 12.47 kV | 2000s | None | None | 2024-04-28 | No | 561
CR-S32-01 | Crossroads | CR-S32 | 2814 | 6.9 | 29.6 | 12.47 kV | 2010s | Recloser only | Automation | 2023-03-30 | No | 226
CR-S32-02 | Crossroads | CR-S32 | 1341 | 18.5 | 24.2 | 12.47 kV | 2010s | IGSD loop | Automation | 2024-10-28 | No | 606
CR-S32-03 | Crossroads | CR-S32 | 2073 | 10.3 | 16.2 | 12.47 kV | 2000s | IGSD loop | None | 2025-07-15 | No | 338
CR-S32-04 | Crossroads | CR-S32 | 1031 | 10.5 | 28.4 | 12.47 kV | 2000s | Recloser only | None | 2023-04-07 | No | 344
CR-S32-05 | Crossroads | CR-S32 | 1225 | 5.9 | 10.9 | 12.47 kV | 2020s | IGSD loop | None | 2023-05-10 | No | 193
BY-S01-01 | Bayou | BY-S01 | 2033 | 35 | 10.2 | 12.47 kV | 1960s | Recloser only | Pole hardening | 2023-06-07 | No | 1147
BY-S01-02 | Bayou | BY-S01 | 945 | 14.5 | 13 | 12.47 kV | 1980s | IGSD loop | Pole hardening | 2026-05-11 | No | 475
BY-S02-01 | Bayou | BY-S02 | 1756 | 72.2 | 19.2 | 12.47 kV | 2000s | IGSD loop | Partial undergrounding | 2025-10-27 | No | 2366
BY-S02-02 | Bayou | BY-S02 | 656 | 18.1 | 5.3 | 12.47 kV | 1960s | Recloser only | None | 2022-04-23 | Both | 593
BY-S03-01 | Bayou | BY-S03 | 1172 | 16.5 | 8.2 | 12.47 kV | 1980s | IGSD loop | None | 2026-04-15 | No | 541
BY-S03-02 | Bayou | BY-S03 | 1869 | 42.9 | 16.3 | 12.47 kV | 1980s | Recloser only | Multiple measures | 2026-08-08 | No | 1406
BY-S03-03 | Bayou | BY-S03 | 661 | 25.8 | 7.8 | 12.47 kV | 1990s | Recloser only | None | 2025-09-30 | No | 846
BY-S04-01 | Bayou | BY-S04 | 1408 | 27.3 | 10.8 | 12.47 kV | 1960s | None | Multiple measures | 2025-09-19 | No | 895
BY-S04-02 | Bayou | BY-S04 | 2179 | 7.4 | 12.5 | 12.47 kV | 1960s | Recloser only | None | 2025-04-27 | No | 243
BY-S04-03 | Bayou | BY-S04 | 1237 | 18.7 | 6.4 | 12.47 kV | 1970s | Recloser only | Partial undergrounding | 2026-01-06 | No | 613
BY-S05-01 | Bayou | BY-S05 | 1100 | 47 | 7.4 | 12.47 kV | 1990s | Recloser only | None | 2022-05-08 | SAIDI | 1541
BY-S05-02 | Bayou | BY-S05 | 1858 | 22.2 | 6.5 | 12.47 kV | 2000s | None | None | 2025-08-05 | SAIDI | 728
BY-S05-03 | Bayou | BY-S05 | 1141 | 4.4 | 4.9 | 12.47 kV | 1970s | Recloser only | Pole hardening | 2024-04-18 | No | 144
BY-S06-01 | Bayou | BY-S06 | 1832 | 23.5 | 7.7 | 12.47 kV | 1960s | None | None | 2024-09-20 | No | 770
BY-S06-02 | Bayou | BY-S06 | 2374 | 34 | 17.6 | 12.47 kV | 1970s | IGSD loop | Multiple measures | 2026-04-13 | No | 1114
BY-S06-03 | Bayou | BY-S06 | 1309 | 18.6 | 9.8 | 12.47 kV | 1980s | None | None | 2026-08-24 | No | 610
BY-S07-01 | Bayou | BY-S07 | 1474 | 26.1 | 9.5 | 12.47 kV | 1960s | None | Pole hardening | 2023-09-24 | No | 855
BY-S07-02 | Bayou | BY-S07 | 2081 | 21.8 | 4.9 | 12.47 kV | 2010s | None | None | 2023-10-13 | SAIFI | 715
BY-S07-03 | Bayou | BY-S07 | 1806 | 17.8 | 11.9 | 12.47 kV | 1970s | Recloser only | Automation | 2025-10-29 | No | 583
BY-S07-04 | Bayou | BY-S07 | 571 | 10.6 | 3.2 | 12.47 kV | 1970s | None | None | 2022-02-05 | No | 347
BY-S07-05 | Bayou | BY-S07 | 981 | 5.7 | 7.9 | 12.47 kV | 1980s | Recloser only | None | 2023-10-20 | No | 187
BY-S07-06 | Bayou | BY-S07 | 1771 | 9.9 | 19.3 | 12.47 kV | 2010s | None | Multiple measures | 2022-06-03 | No | 325
BY-S08-01 | Bayou | BY-S08 | 2200 | 18.7 | 7.2 | 12.47 kV | 1960s | IGSD loop | Pole hardening | 2022-02-18 | No | 613
BY-S08-02 | Bayou | BY-S08 | 1154 | 14.7 | 5.1 | 12.47 kV | 1960s | None | Pole hardening | 2025-05-23 | SAIFI | 482
BY-S08-03 | Bayou | BY-S08 | 1737 | 12.5 | 8.4 | 12.47 kV | 1990s | Recloser only | Pole hardening | 2025-08-30 | No | 410
BY-S09-01 | Bayou | BY-S09 | 1247 | 16.9 | 6.3 | 12.47 kV | 1990s | None | Partial undergrounding | 2026-08-13 | No | 554
BY-S09-02 | Bayou | BY-S09 | 1177 | 25 | 17.1 | 12.47 kV | 1960s | Recloser only | None | 2025-11-21 | No | 819
BY-S09-03 | Bayou | BY-S09 | 1264 | 20.7 | 14 | 12.47 kV | 2000s | None | None | 2022-04-01 | No | 678
BY-S09-04 | Bayou | BY-S09 | 2640 | 12.8 | 10.8 | 12.47 kV | 1960s | Recloser only | Pole hardening | 2024-05-30 | No | 420
BY-S09-05 | Bayou | BY-S09 | 995 | 14.4 | 10.5 | 12.47 kV | 1970s | Recloser only | None | 2025-09-23 | No | 472
BY-S10-01 | Bayou | BY-S10 | 1762 | 21.8 | 11.2 | 12.47 kV | 2000s | IGSD loop | None | 2025-11-07 | No | 715
BY-S10-02 | Bayou | BY-S10 | 934 | 10 | 3.4 | 12.47 kV | 2000s | Recloser only | None | 2022-07-17 | No | 328
BY-S10-03 | Bayou | BY-S10 | 1067 | 25.5 | 20.2 | 12.47 kV | 1990s | Recloser only | None | 2022-01-19 | No | 836
BY-S10-04 | Bayou | BY-S10 | 1018 | 61.6 | 3.7 | 12.47 kV | 1960s | Full automation | Automation | 2026-08-06 | No | 2019
BY-S10-05 | Bayou | BY-S10 | 1197 | 17.6 | 11.3 | 12.47 kV | 2010s | IGSD loop | Partial undergrounding | 2026-02-18 | No | 577
BY-S11-01 | Bayou | BY-S11 | 2363 | 23.1 | 10 | 12.47 kV | 1970s | None | Automation | 2022-11-07 | No | 757
BY-S11-02 | Bayou | BY-S11 | 752 | 8.9 | 4.1 | 12.47 kV | 1980s | None | Automation | 2025-09-23 | No | 292
BY-S11-03 | Bayou | BY-S11 | 1218 | 13.2 | 5.4 | 12.47 kV | 1990s | IGSD loop | None | 2022-02-02 | No | 433
BY-S12-01 | Bayou | BY-S12 | 848 | 11.9 | 7.5 | 12.47 kV | 1990s | Recloser only | None | 2024-10-02 | No | 390
BY-S12-02 | Bayou | BY-S12 | 1082 | 9.7 | 16.1 | 12.47 kV | 1960s | IGSD loop | Partial undergrounding | 2025-03-07 | No | 318
BY-S12-03 | Bayou | BY-S12 | 1783 | 34.9 | 8.7 | 12.47 kV | 1960s | Recloser only | None | 2026-05-12 | No | 1144
BY-S12-04 | Bayou | BY-S12 | 1164 | 18.3 | 11.7 | 12.47 kV | 1960s | None | None | 2026-02-26 | No | 600
BY-S13-01 | Bayou | BY-S13 | 1453 | 9.4 | 17.3 | 12.47 kV | 1980s | Recloser only | None | 2022-07-13 | No | 308
BY-S13-02 | Bayou | BY-S13 | 886 | 22.5 | 8.3 | 12.47 kV | 1970s | Recloser only | Automation | 2022-05-31 | No | 737
BY-S13-03 | Bayou | BY-S13 | 1095 | 15.8 | 7.8 | 12.47 kV | 1970s | None | None | 2026-02-20 | No | 518
BY-S13-04 | Bayou | BY-S13 | 847 | 48.9 | 8.3 | 12.47 kV | 1970s | Recloser only | None | 2022-01-23 | No | 1603
BY-S13-05 | Bayou | BY-S13 | 2210 | 15 | 15.5 | 12.47 kV | 1970s | None | Partial undergrounding | 2026-07-19 | No | 492
BY-S13-06 | Bayou | BY-S13 | 2724 | 35.2 | 19.2 | 12.47 kV | 1990s | IGSD loop | None | 2026-07-08 | No | 1154
BY-S14-01 | Bayou | BY-S14 | 2780 | 15.2 | 6.5 | 12.47 kV | 1980s | None | None | 2026-05-02 | No | 498
BY-S14-02 | Bayou | BY-S14 | 1368 | 19.8 | 15.4 | 12.47 kV | 1960s | None | Pole hardening | 2026-05-12 | No | 649
BY-S14-03 | Bayou | BY-S14 | 929 | 22.3 | 10.9 | 12.47 kV | 1970s | None | Partial undergrounding | 2026-06-25 | No | 731
BY-S15-01 | Bayou | BY-S15 | 2159 | 4.8 | 9.7 | 12.47 kV | 1980s | None | Multiple measures | 2025-12-03 | No | 157
BY-S15-02 | Bayou | BY-S15 | 3364 | 28.3 | 38.6 | 12.47 kV | 1960s | Recloser only | None | 2023-03-05 | SAIFI | 928
BY-S15-03 | Bayou | BY-S15 | 1594 | 26.2 | 31.1 | 12.47 kV | 1960s | IGSD loop | None | 2025-11-09 | No | 859
BY-S15-04 | Bayou | BY-S15 | 1282 | 23.1 | 9.7 | 12.47 kV | 1970s | Recloser only | None | 2022-10-17 | No | 757
BY-S15-05 | Bayou | BY-S15 | 897 | 9 | 13.5 | 12.47 kV | 1990s | None | Multiple measures | 2023-11-10 | Both | 295
BY-S15-06 | Bayou | BY-S15 | 2182 | 31.9 | 11.3 | 12.47 kV | 2000s | IGSD loop | None | 2026-07-24 | No | 1046
BY-S16-01 | Bayou | BY-S16 | 3047 | 20.3 | 9.3 | 12.47 kV | 1970s | IGSD loop | Pole hardening | 2023-09-06 | No | 665
BY-S16-02 | Bayou | BY-S16 | 2008 | 17.3 | 11 | 12.47 kV | 1990s | IGSD loop | None | 2025-06-26 | No | 567
BY-S16-03 | Bayou | BY-S16 | 1279 | 25.4 | 7.8 | 12.47 kV | 1980s | Recloser only | None | 2022-02-22 | No | 833
BY-S16-04 | Bayou | BY-S16 | 1640 | 22.6 | 9.1 | 12.47 kV | 1970s | None | Automation | 2025-04-26 | No | 741
BY-S16-05 | Bayou | BY-S16 | 1474 | 16 | 6.5 | 12.47 kV | 1960s | Recloser only | None | 2026-03-22 | No | 524
BY-S16-06 | Bayou | BY-S16 | 3074 | 26.5 | 7.9 | 12.47 kV | 1980s | None | None | 2022-02-02 | No | 869
BY-S17-01 | Bayou | BY-S17 | 1868 | 40 | 5.6 | 12.47 kV | 2020s | None | None | 2025-12-12 | No | 1311
BY-S17-02 | Bayou | BY-S17 | 2526 | 15.7 | 7.9 | 12.47 kV | 1990s | None | None | 2025-09-18 | No | 515
BY-S17-03 | Bayou | BY-S17 | 903 | 14 | 5.6 | 12.47 kV | 2010s | Recloser only | Multiple measures | 2026-08-30 | No | 459
BY-S17-04 | Bayou | BY-S17 | 2458 | 24.6 | 15.1 | 12.47 kV | 1980s | None | Pole hardening | 2026-08-28 | SAIFI | 806
BY-S18-01 | Bayou | BY-S18 | 1136 | 22.4 | 12.1 | 12.47 kV | 1980s | Recloser only | None | 2025-02-24 | No | 734
BY-S18-02 | Bayou | BY-S18 | 1634 | 16.9 | 8.3 | 12.47 kV | 1970s | Recloser only | None | 2025-07-12 | No | 554
BY-S18-03 | Bayou | BY-S18 | 891 | 17.7 | 6.5 | 12.47 kV | 1980s | Recloser only | Multiple measures | 2025-09-16 | No | 580
BY-S18-04 | Bayou | BY-S18 | 2458 | 61.2 | 28.5 | 12.47 kV | 1990s | None | None | 2023-01-24 | No | 2006
BY-S18-05 | Bayou | BY-S18 | 1790 | 52.8 | 12.1 | 12.47 kV | 1960s | IGSD loop | None | 2026-08-28 | No | 1731
BY-S18-06 | Bayou | BY-S18 | 1170 | 21.2 | 5 | 12.47 kV | 1990s | None | None | 2022-03-26 | No | 695
BY-S18-07 | Bayou | BY-S18 | 1326 | 13.6 | 7.3 | 12.47 kV | 1970s | None | Pole hardening | 2025-09-24 | No | 446
BY-S19-01 | Bayou | BY-S19 | 2021 | 16.6 | 21.3 | 12.47 kV | 1970s | Recloser only | None | 2023-09-17 | No | 544
BY-S19-02 | Bayou | BY-S19 | 3169 | 41 | 13.9 | 12.47 kV | 1970s | Recloser only | Pole hardening | 2025-09-28 | No | 1344
BY-S19-03 | Bayou | BY-S19 | 2017 | 18.4 | 11.1 | 12.47 kV | 1980s | Recloser only | None | 2025-12-16 | No | 603
BY-S19-04 | Bayou | BY-S19 | 1613 | 15.9 | 5.3 | 12.47 kV | 1960s | Recloser only | None | 2026-04-14 | No | 521
BY-S20-01 | Bayou | BY-S20 | 1640 | 12.6 | 4.5 | 12.47 kV | 1990s | Recloser only | None | 2025-10-13 | No | 413
BY-S20-02 | Bayou | BY-S20 | 1422 | 5.5 | 11.2 | 12.47 kV | 1960s | Recloser only | Partial undergrounding | 2026-01-26 | No | 180
BY-S20-03 | Bayou | BY-S20 | 835 | 11 | 19.1 | 12.47 kV | 1970s | Recloser only | None | 2026-05-30 | No | 361
BY-S21-01 | Bayou | BY-S21 | 1819 | 18.5 | 6.6 | 12.47 kV | 1980s | Recloser only | Multiple measures | 2026-07-21 | No | 606
BY-S21-02 | Bayou | BY-S21 | 1223 | 33 | 5.3 | 12.47 kV | 1980s | Recloser only | None | 2023-08-22 | No | 1082
BY-S21-03 | Bayou | BY-S21 | 1519 | 22.7 | 8.2 | 12.47 kV | 1970s | Recloser only | None | 2023-08-30 | No | 744
BY-S21-04 | Bayou | BY-S21 | 1650 | 22.6 | 15.1 | 12.47 kV | 1990s | Recloser only | None | 2023-06-11 | No | 741
BY-S21-05 | Bayou | BY-S21 | 1403 | 42.9 | 13.7 | 12.47 kV | 1960s | IGSD loop | Partial undergrounding | 2026-03-27 | No | 1406
BY-S22-01 | Bayou | BY-S22 | 761 | 11.5 | 6.1 | 12.47 kV | 1990s | Recloser only | None | 2023-04-04 | No | 377
BY-S22-02 | Bayou | BY-S22 | 1133 | 6.2 | 4.9 | 12.47 kV | 1980s | Recloser only | Automation | 2025-09-03 | No | 203
BY-S22-03 | Bayou | BY-S22 | 1873 | 16.8 | 32.1 | 12.47 kV | 1970s | None | Automation | 2024-08-20 | No | 551
BY-S22-04 | Bayou | BY-S22 | 2128 | 20 | 14.8 | 12.47 kV | 1970s | None | Automation | 2022-10-29 | No | 656
BY-S23-01 | Bayou | BY-S23 | 1812 | 23.4 | 5.8 | 12.47 kV | 1980s | None | Automation | 2024-11-27 | No | 767
BY-S23-02 | Bayou | BY-S23 | 2696 | 38.5 | 18.8 | 12.47 kV | 1990s | Recloser only | Automation | 2024-02-06 | No | 1262
BY-S23-03 | Bayou | BY-S23 | 2340 | 17.8 | 13.1 | 12.47 kV | 1970s | None | Multiple measures | 2026-05-16 | No | 583
BY-S23-04 | Bayou | BY-S23 | 1927 | 20.5 | 8 | 12.47 kV | 1960s | IGSD loop | None | 2026-03-11 | No | 672
BY-S23-05 | Bayou | BY-S23 | 1185 | 28.3 | 6.2 | 12.47 kV | 1970s | IGSD loop | None | 2022-06-13 | No | 928
BY-S24-01 | Bayou | BY-S24 | 1253 | 17.1 | 6.6 | 12.47 kV | 1990s | None | None | 2024-02-01 | No | 561
BY-S24-02 | Bayou | BY-S24 | 887 | 7.5 | 9.8 | 12.47 kV | 1980s | None | None | 2022-08-27 | No | 246
BY-S24-03 | Bayou | BY-S24 | 894 | 14.2 | 7.9 | 12.47 kV | 1980s | IGSD loop | Multiple measures | 2026-08-25 | No | 465
BY-S24-04 | Bayou | BY-S24 | 1201 | 22.3 | 5.1 | 12.47 kV | 2000s | IGSD loop | Pole hardening | 2023-12-01 | SAIDI | 731
BY-S24-05 | Bayou | BY-S24 | 1485 | 18 | 3.3 | 12.47 kV | 2000s | None | Partial undergrounding | 2026-01-28 | No | 590
BY-S25-01 | Bayou | BY-S25 | 1251 | 10.8 | 4.7 | 12.47 kV | 1980s | IGSD loop | None | 2026-04-11 | No | 354
BY-S25-02 | Bayou | BY-S25 | 1757 | 29.5 | 9.3 | 12.47 kV | 1970s | Recloser only | None | 2025-07-02 | No | 967
BY-S25-03 | Bayou | BY-S25 | 1607 | 8.3 | 10.6 | 12.47 kV | 1960s | None | None | 2026-04-18 | No | 272
BY-S25-04 | Bayou | BY-S25 | 1534 | 25 | 7 | 12.47 kV | 1980s | Recloser only | Multiple measures | 2026-07-25 | SAIFI | 819
BY-S25-05 | Bayou | BY-S25 | 1240 | 12.4 | 6.4 | 12.47 kV | 1970s | Recloser only | None | 2024-06-18 | No | 406
BY-S26-01 | Bayou | BY-S26 | 1196 | 27.6 | 4.5 | 12.47 kV | 1980s | None | None | 2026-08-28 | No | 905
BY-S26-02 | Bayou | BY-S26 | 3714 | 24.1 | 20.8 | 12.47 kV | 1970s | Recloser only | None | 2026-04-21 | No | 790
BY-S26-03 | Bayou | BY-S26 | 1696 | 17.2 | 11.1 | 12.47 kV | 1980s | None | None | 2025-11-03 | No | 564
BY-S26-04 | Bayou | BY-S26 | 1437 | 5.4 | 16.5 | 12.47 kV | 1960s | IGSD loop | None | 2025-06-14 | No | 177
BY-S26-05 | Bayou | BY-S26 | 1316 | 6.4 | 11.9 | 12.47 kV | 1970s | None | None | 2025-02-24 | No | 210
BY-S26-06 | Bayou | BY-S26 | 1108 | 19.6 | 3.5 | 12.47 kV | 1970s | Recloser only | None | 2026-03-20 | No | 642
BY-S27-01 | Bayou | BY-S27 | 1207 | 11.3 | 3.4 | 12.47 kV | 1970s | Recloser only | None | 2025-05-20 | No | 370
BY-S27-02 | Bayou | BY-S27 | 689 | 16.1 | 4.8 | 12.47 kV | 1960s | None | None | 2024-05-06 | No | 528
BY-S27-03 | Bayou | BY-S27 | 1062 | 13.1 | 13.8 | 12.47 kV | 1960s | None | None | 2022-09-12 | No | 429
BY-S27-04 | Bayou | BY-S27 | 773 | 9 | 4.3 | 12.47 kV | 1980s | Recloser only | None | 2026-06-25 | SAIFI | 295
BY-S27-05 | Bayou | BY-S27 | 976 | 13.3 | 18.8 | 12.47 kV | 1970s | Recloser only | None | 2026-04-14 | No | 436
BY-S27-06 | Bayou | BY-S27 | 2434 | 23.2 | 7.1 | 12.47 kV | 1970s | None | None | 2023-08-10 | No | 760
BY-S28-01 | Bayou | BY-S28 | 1048 | 17 | 5.5 | 12.47 kV | 1980s | Recloser only | None | 2025-10-01 | No | 557
BY-S28-02 | Bayou | BY-S28 | 1740 | 16.6 | 8.7 | 12.47 kV | 1990s | Recloser only | None | 2024-03-14 | No | 544
BY-S28-03 | Bayou | BY-S28 | 1339 | 14.9 | 15.1 | 12.47 kV | 1970s | None | None | 2026-07-13 | SAIDI | 488
BY-S29-01 | Bayou | BY-S29 | 4666 | 99.6 | 13.2 | 12.47 kV | 1960s | Full automation | None | 2026-07-29 | No | 3265
BY-S29-02 | Bayou | BY-S29 | 2691 | 28.2 | 9 | 12.47 kV | 1960s | Recloser only | None | 2024-06-27 | SAIFI | 924
BY-S29-03 | Bayou | BY-S29 | 1608 | 16.2 | 4.7 | 12.47 kV | 1960s | Recloser only | Automation | 2022-11-04 | No | 531
BY-S29-04 | Bayou | BY-S29 | 2920 | 12 | 5.4 | 12.47 kV | 1980s | Recloser only | None | 2026-05-28 | No | 393
BY-S29-05 | Bayou | BY-S29 | 1135 | 21.8 | 7.2 | 12.47 kV | 1960s | Recloser only | None | 2023-09-27 | Both | 715
BY-S30-01 | Bayou | BY-S30 | 2519 | 33.1 | 20.2 | 12.47 kV | 1980s | None | None | 2025-08-28 | No | 1085
BY-S30-02 | Bayou | BY-S30 | 770 | 16 | 6.2 | 12.47 kV | 1970s | None | None | 2025-08-10 | No | 524
BY-S30-03 | Bayou | BY-S30 | 1153 | 21.7 | 6.8 | 12.47 kV | 1980s | Recloser only | None | 2026-06-12 | No | 711
PR-S01-01 | Prairie | PR-S01 | 1190 | 39.7 | 1.8 | 34.5 kV | 1970s | None | None | 2023-07-14 | No | 1301
PR-S01-02 | Prairie | PR-S01 | 1400 | 17.2 | 4.4 | 12.47 kV | 2010s | Recloser only | Partial undergrounding | 2026-03-17 | No | 564
PR-S01-03 | Prairie | PR-S01 | 1250 | 46.4 | 7.8 | 34.5 kV | 1960s | Recloser only | Automation | 2023-08-11 | No | 1521
PR-S01-04 | Prairie | PR-S01 | 369 | 31.7 | 4.1 | 12.47 kV | 1970s | Recloser only | None | 2026-08-25 | No | 1039
PR-S01-05 | Prairie | PR-S01 | 887 | 74.4 | 4.6 | 34.5 kV | 1980s | Recloser only | None | 2026-05-26 | No | 2439
PR-S01-06 | Prairie | PR-S01 | 1131 | 31 | 9.1 | 12.47 kV | 1970s | None | Multiple measures | 2024-11-25 | No | 1016
PR-S02-01 | Prairie | PR-S02 | 1061 | 28.9 | 8.1 | 12.47 kV | 1990s | None | None | 2023-06-21 | No | 947
PR-S02-02 | Prairie | PR-S02 | 1521 | 25.1 | 5 | 12.47 kV | 1980s | None | None | 2023-07-04 | Both | 823
PR-S02-03 | Prairie | PR-S02 | 866 | 18.7 | 4.1 | 12.47 kV | 1960s | None | Multiple measures | 2025-11-05 | No | 613
PR-S03-01 | Prairie | PR-S03 | 1088 | 19.8 | 6.6 | 12.47 kV | 2000s | None | None | 2023-05-04 | No | 649
PR-S03-02 | Prairie | PR-S03 | 1265 | 30.3 | 10.1 | 12.47 kV | 1990s | None | Pole hardening | 2025-09-01 | No | 993
PR-S03-03 | Prairie | PR-S03 | 743 | 22.2 | 2.9 | 12.47 kV | 1980s | None | Pole hardening | 2025-09-06 | No | 728
PR-S03-04 | Prairie | PR-S03 | 576 | 47.7 | 1.8 | 34.5 kV | 1990s | None | None | 2025-09-14 | SAIDI | 1563
PR-S03-05 | Prairie | PR-S03 | 1752 | 36.3 | 5 | 12.47 kV | 1980s | Recloser only | None | 2022-07-05 | No | 1190
PR-S03-06 | Prairie | PR-S03 | 902 | 24.2 | 2.7 | 12.47 kV | 2000s | Recloser only | Multiple measures | 2026-08-31 | No | 793
PR-S04-01 | Prairie | PR-S04 | 1481 | 42.3 | 5.6 | 34.5 kV | 2000s | None | Multiple measures | 2025-10-30 | No | 1386
PR-S04-02 | Prairie | PR-S04 | 1159 | 25.3 | 3.6 | 12.47 kV | 1990s | None | None | 2025-11-22 | No | 829
PR-S04-03 | Prairie | PR-S04 | 460 | 19.2 | 1.5 | 12.47 kV | 1960s | None | None | 2023-02-08 | No | 629
PR-S05-01 | Prairie | PR-S05 | 791 | 14.1 | 3 | 12.47 kV | 1960s | Recloser only | None | 2023-02-17 | No | 462
PR-S05-02 | Prairie | PR-S05 | 1225 | 29.3 | 3.8 | 12.47 kV | 1970s | None | None | 2026-04-29 | No | 960
PR-S05-03 | Prairie | PR-S05 | 833 | 45.7 | 3.6 | 34.5 kV | 1980s | Recloser only | None | 2023-03-02 | No | 1498
PR-S06-01 | Prairie | PR-S06 | 1800 | 98.4 | 5.1 | 34.5 kV | 1970s | IGSD loop | None | 2025-12-12 | No | 3225
PR-S06-02 | Prairie | PR-S06 | 951 | 38.3 | 5.3 | 34.5 kV | 2000s | None | None | 2022-09-05 | No | 1255
PR-S06-03 | Prairie | PR-S06 | 1431 | 18.4 | 1.9 | 12.47 kV | 1980s | IGSD loop | None | 2025-05-13 | No | 603
PR-S07-01 | Prairie | PR-S07 | 961 | 32.1 | 6.2 | 12.47 kV | 1980s | IGSD loop | None | 2023-02-18 | No | 1052
PR-S07-02 | Prairie | PR-S07 | 1233 | 41 | 4.3 | 34.5 kV | 1990s | None | None | 2026-08-15 | No | 1344
PR-S07-03 | Prairie | PR-S07 | 1639 | 24.9 | 4.4 | 12.47 kV | 1980s | None | Automation | 2022-09-14 | No | 816
PR-S07-04 | Prairie | PR-S07 | 1637 | 44.9 | 5.4 | 34.5 kV | 2020s | None | None | 2023-11-09 | No | 1472
PR-S07-05 | Prairie | PR-S07 | 1336 | 29.2 | 4.9 | 12.47 kV | 1970s | IGSD loop | None | 2026-07-13 | No | 957
PR-S07-06 | Prairie | PR-S07 | 2139 | 94.3 | 10.9 | 34.5 kV | 1990s | Recloser only | None | 2023-03-07 | No | 3091
PR-S08-01 | Prairie | PR-S08 | 2156 | 36.1 | 6 | 12.47 kV | 1980s | Recloser only | Multiple measures | 2024-01-25 | No | 1183
PR-S08-02 | Prairie | PR-S08 | 1865 | 42.1 | 5.9 | 34.5 kV | 2010s | None | Pole hardening | 2022-10-07 | No | 1380
PR-S08-03 | Prairie | PR-S08 | 1601 | 45.3 | 5.1 | 34.5 kV | 2000s | None | None | 2025-07-11 | No | 1485
PR-S09-01 | Prairie | PR-S09 | 2165 | 14.2 | 5.3 | 12.47 kV | 1990s | Recloser only | None | 2026-08-02 | No | 465
PR-S09-02 | Prairie | PR-S09 | 1022 | 16.1 | 5.6 | 12.47 kV | 1970s | Recloser only | None | 2025-08-19 | No | 528
PR-S09-03 | Prairie | PR-S09 | 1654 | 36.8 | 7.1 | 12.47 kV | 1980s | None | None | 2025-12-27 | No | 1206
PR-S09-04 | Prairie | PR-S09 | 716 | 37.3 | 4.5 | 34.5 kV | 2000s | Recloser only | None | 2024-03-05 | No | 1223
PR-S10-01 | Prairie | PR-S10 | 616 | 28.7 | 3.3 | 12.47 kV | 1970s | None | None | 2024-08-05 | No | 941
PR-S10-02 | Prairie | PR-S10 | 1016 | 41.3 | 4.2 | 34.5 kV | 1970s | None | Pole hardening | 2022-05-08 | No | 1354
PR-S10-03 | Prairie | PR-S10 | 2240 | 31.2 | 4.1 | 12.47 kV | 1980s | Recloser only | None | 2022-11-11 | No | 1023
PR-S11-01 | Prairie | PR-S11 | 976 | 32.6 | 3 | 12.47 kV | 1990s | None | None | 2023-09-25 | No | 1069
PR-S11-02 | Prairie | PR-S11 | 1818 | 37.7 | 7.5 | 34.5 kV | 2010s | Recloser only | Automation | 2023-07-01 | No | 1236
PR-S11-03 | Prairie | PR-S11 | 1585 | 31.1 | 4 | 12.47 kV | 2000s | IGSD loop | Pole hardening | 2026-06-15 | No | 1019
PR-S12-01 | Prairie | PR-S12 | 3421 | 60.4 | 4.5 | 34.5 kV | 2010s | Recloser only | None | 2022-04-21 | No | 1980
PR-S12-02 | Prairie | PR-S12 | 560 | 18.4 | 3.9 | 12.47 kV | 1980s | None | Pole hardening | 2022-08-18 | No | 603
PR-S12-03 | Prairie | PR-S12 | 1257 | 24.4 | 5.5 | 12.47 kV | 1970s | None | None | 2026-04-29 | No | 800
PR-S13-01 | Prairie | PR-S13 | 2584 | 28.8 | 5.9 | 12.47 kV | 2010s | Full automation | Automation | 2026-04-29 | No | 944
PR-S13-02 | Prairie | PR-S13 | 1241 | 24.3 | 3.1 | 12.47 kV | 1990s | IGSD loop | None | 2023-10-14 | No | 796
PR-S13-03 | Prairie | PR-S13 | 560 | 30.4 | 3.4 | 12.47 kV | 1960s | IGSD loop | None | 2026-07-05 | Both | 996
PR-S13-04 | Prairie | PR-S13 | 1024 | 20.6 | 4.3 | 12.47 kV | 2010s | None | Multiple measures | 2026-01-29 | No | 675
PR-S13-05 | Prairie | PR-S13 | 676 | 29.3 | 4.9 | 12.47 kV | 1970s | Recloser only | Pole hardening | 2025-08-09 | No | 960
PR-S13-06 | Prairie | PR-S13 | 1290 | 27.9 | 14.5 | 12.47 kV | 1980s | None | Pole hardening | 2025-06-06 | SAIDI | 914
PR-S14-01 | Prairie | PR-S14 | 947 | 23 | 2.2 | 12.47 kV | 1960s | IGSD loop | Partial undergrounding | 2024-02-09 | No | 754
PR-S14-02 | Prairie | PR-S14 | 628 | 9.4 | 2.1 | 12.47 kV | 1980s | None | None | 2022-03-15 | No | 308
PR-S14-03 | Prairie | PR-S14 | 1814 | 22.5 | 6.4 | 12.47 kV | 1990s | IGSD loop | Automation | 2022-09-28 | No | 737
PR-S14-04 | Prairie | PR-S14 | 2823 | 28.1 | 12 | 12.47 kV | 1990s | Recloser only | None | 2026-08-12 | Both | 921
PR-S15-01 | Prairie | PR-S15 | 1045 | 28.7 | 3 | 12.47 kV | 1970s | None | None | 2025-12-08 | No | 941
PR-S15-02 | Prairie | PR-S15 | 1274 | 18.4 | 6.9 | 12.47 kV | 2000s | IGSD loop | None | 2026-07-02 | No | 603
PR-S15-03 | Prairie | PR-S15 | 1679 | 37.1 | 6.1 | 34.5 kV | 1970s | None | None | 2024-05-04 | No | 1216
PR-S15-04 | Prairie | PR-S15 | 828 | 16.9 | 2.8 | 12.47 kV | 2000s | Recloser only | None | 2022-11-14 | No | 554
PR-S15-05 | Prairie | PR-S15 | 497 | 32.7 | 3.8 | 12.47 kV | 1970s | None | Automation | 2026-05-20 | No | 1072
PR-S15-06 | Prairie | PR-S15 | 1472 | 88.6 | 13.2 | 34.5 kV | 2000s | Recloser only | None | 2024-06-15 | Both | 2904
PR-S16-01 | Prairie | PR-S16 | 881 | 26.9 | 3.9 | 12.47 kV | 1990s | Recloser only | None | 2024-07-13 | No | 882
PR-S16-02 | Prairie | PR-S16 | 500 | 15.6 | 6 | 12.47 kV | 1980s | None | None | 2023-06-04 | No | 511
PR-S16-03 | Prairie | PR-S16 | 770 | 40.8 | 4.4 | 34.5 kV | 1970s | None | None | 2023-01-25 | No | 1337
PR-S16-04 | Prairie | PR-S16 | 808 | 45.9 | 4.6 | 34.5 kV | 1980s | Recloser only | Multiple measures | 2023-06-08 | No | 1504
PR-S16-05 | Prairie | PR-S16 | 1450 | 49.9 | 2.3 | 34.5 kV | 1990s | None | None | 2023-03-24 | Both | 1636
PR-S17-01 | Prairie | PR-S17 | 2222 | 48.3 | 7.2 | 34.5 kV | 1970s | Recloser only | None | 2026-04-25 | No | 1583
PR-S17-02 | Prairie | PR-S17 | 695 | 35.3 | 6.8 | 12.47 kV | 1980s | None | None | 2026-08-20 | SAIDI | 1157
PR-S18-01 | Prairie | PR-S18 | 600 | 35.7 | 4.8 | 12.47 kV | 1970s | None | None | 2026-07-27 | No | 1170
PR-S18-02 | Prairie | PR-S18 | 1027 | 48.1 | 4 | 34.5 kV | 2000s | Recloser only | Pole hardening | 2026-07-28 | No | 1577
PR-S18-03 | Prairie | PR-S18 | 1422 | 39.3 | 5 | 34.5 kV | 1990s | None | None | 2023-07-22 | No | 1288
PR-S18-04 | Prairie | PR-S18 | 1253 | 44.5 | 9.8 | 34.5 kV | 1970s | None | None | 2023-02-01 | SAIDI | 1459
PR-S18-05 | Prairie | PR-S18 | 2060 | 35.7 | 8.9 | 12.47 kV | 1990s | None | Pole hardening | 2022-05-06 | No | 1170
PR-S18-06 | Prairie | PR-S18 | 1435 | 24.6 | 5.8 | 12.47 kV | 1980s | IGSD loop | None | 2026-05-03 | No | 806
PR-S19-01 | Prairie | PR-S19 | 914 | 26.4 | 6.6 | 12.47 kV | 1990s | None | None | 2026-05-16 | Both | 865
PR-S19-02 | Prairie | PR-S19 | 849 | 23.5 | 7.3 | 12.47 kV | 1980s | Recloser only | None | 2026-02-19 | No | 770
PR-S19-03 | Prairie | PR-S19 | 1068 | 57.9 | 2.8 | 34.5 kV | 1970s | None | None | 2025-12-07 | No | 1898
PR-S19-04 | Prairie | PR-S19 | 1504 | 33.1 | 3.3 | 12.47 kV | 1980s | None | None | 2023-05-03 | No | 1085
PR-S19-05 | Prairie | PR-S19 | 1476 | 48.2 | 5.3 | 34.5 kV | 1990s | Recloser only | Multiple measures | 2025-11-02 | No | 1580
PR-S20-01 | Prairie | PR-S20 | 1016 | 17.7 | 5.9 | 12.47 kV | 1980s | None | Multiple measures | 2025-11-24 | No | 580
PR-S20-02 | Prairie | PR-S20 | 915 | 47.7 | 3.2 | 34.5 kV | 1980s | Recloser only | None | 2026-07-04 | No | 1563
PR-S20-03 | Prairie | PR-S20 | 790 | 39.4 | 4.3 | 34.5 kV | 2010s | IGSD loop | None | 2023-02-07 | No | 1291
PR-S20-04 | Prairie | PR-S20 | 434 | 24.1 | 6.1 | 12.47 kV | 1960s | Full automation | None | 2025-02-24 | SAIDI | 790

## Data 2
batch_id | poles_inspected | feeder_code | district | contractor_code | inspection_month | poles_pass | poles_restorable | poles_reject_priority | poles_reject_standard | poles_pre_1980
PIB-000001 | 14 | BY-S15-03 | Bayou | CT-11 | 2026-01-01 | 14 | 0 | 0 | 0 | 13
PIB-000002 | 11 | BY-S25-03 | Bayou | CT-11 | 2026-01-01 | 10 | 0 | 0 | 1 | 9
PIB-000003 | 17 | BY-S29-05 | Bayou | CT-11 | 2026-01-01 | 14 | 0 | 0 | 3 | 16
PIB-000004 | 10 | BY-S29-05 | Bayou | CT-11 | 2026-01-01 | 9 | 1 | 0 | 0 | 10
PIB-000005 | 6 | BY-S15-03 | Bayou | CT-11 | 2026-01-02 | 4 | 0 | 0 | 2 | 6
PIB-000006 | 21 | BY-S15-03 | Bayou | CT-11 | 2026-01-02 | 20 | 1 | 0 | 0 | 18
PIB-000007 | 6 | BY-S25-03 | Bayou | CT-11 | 2026-01-02 | 4 | 1 | 1 | 0 | 6
PIB-000008 | 6 | BY-S25-03 | Bayou | CT-11 | 2026-01-02 | 6 | 0 | 0 | 0 | 6
PIB-000009 | 17 | BY-S25-03 | Bayou | CT-11 | 2026-01-02 | 15 | 0 | 0 | 2 | 12
PIB-000010 | 20 | BY-S29-05 | Bayou | CT-11 | 2026-01-02 | 20 | 0 | 0 | 0 | 17
PIB-000011 | 6 | CR-S30-02 | Crossroads | CT-11 | 2026-01-02 | 6 | 0 | 0 | 0 | 5
PIB-000012 | 6 | BY-S15-03 | Bayou | CT-11 | 2026-01-05 | 5 | 1 | 0 | 0 | 6
PIB-000013 | 18 | BY-S15-03 | Bayou | CT-11 | 2026-01-05 | 17 | 0 | 1 | 0 | 14
PIB-000014 | 18 | BY-S15-03 | Bayou | CT-11 | 2026-01-05 | 17 | 1 | 0 | 0 | 17
PIB-000015 | 17 | BY-S15-03 | Bayou | CT-11 | 2026-01-05 | 16 | 1 | 0 | 0 | 17
PIB-000016 | 20 | BY-S29-05 | Bayou | CT-11 | 2026-01-05 | 18 | 0 | 0 | 2 | 17
PIB-000017 | 10 | BY-S29-05 | Bayou | CT-11 | 2026-01-05 | 10 | 0 | 0 | 0 | 8
PIB-000018 | 17 | CR-S30-02 | Crossroads | CT-11 | 2026-01-05 | 16 | 0 | 1 | 0 | 15
PIB-000019 | 15 | BY-S15-03 | Bayou | CT-11 | 2026-01-06 | 15 | 0 | 0 | 0 | 12
PIB-000020 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-06 | 9 | 0 | 0 | 1 | 9
PIB-000021 | 9 | BY-S15-03 | Bayou | CT-11 | 2026-01-06 | 9 | 0 | 0 | 0 | 8
PIB-000022 | 7 | BY-S15-03 | Bayou | CT-11 | 2026-01-06 | 7 | 0 | 0 | 0 | 7
PIB-000023 | 19 | BY-S19-04 | Bayou | CT-11 | 2026-01-06 | 17 | 0 | 0 | 2 | 18
PIB-000024 | 18 | BY-S25-03 | Bayou | CT-11 | 2026-01-06 | 18 | 0 | 0 | 0 | 15
PIB-000025 | 17 | BY-S25-03 | Bayou | CT-11 | 2026-01-06 | 17 | 0 | 0 | 0 | 16
PIB-000026 | 7 | BY-S29-05 | Bayou | CT-11 | 2026-01-06 | 6 | 0 | 1 | 0 | 5
PIB-000027 | 14 | BY-S29-05 | Bayou | CT-11 | 2026-01-06 | 12 | 0 | 0 | 2 | 13
PIB-000028 | 10 | BY-S29-05 | Bayou | CT-11 | 2026-01-06 | 9 | 0 | 1 | 0 | 8
PIB-000029 | 19 | BY-S29-05 | Bayou | CT-11 | 2026-01-06 | 19 | 0 | 0 | 0 | 13
PIB-000030 | 9 | CR-S30-02 | Crossroads | CT-11 | 2026-01-06 | 8 | 0 | 0 | 1 | 8
PIB-000031 | 16 | BY-S15-03 | Bayou | CT-11 | 2026-01-07 | 15 | 1 | 0 | 0 | 12
PIB-000032 | 14 | BY-S15-03 | Bayou | CT-11 | 2026-01-07 | 14 | 0 | 0 | 0 | 14
PIB-000033 | 12 | BY-S15-03 | Bayou | CT-11 | 2026-01-07 | 12 | 0 | 0 | 0 | 10
PIB-000034 | 6 | BY-S15-03 | Bayou | CT-11 | 2026-01-07 | 6 | 0 | 0 | 0 | 5
PIB-000035 | 19 | BY-S19-04 | Bayou | CT-11 | 2026-01-07 | 18 | 0 | 0 | 1 | 15
PIB-000036 | 13 | BY-S25-03 | Bayou | CT-11 | 2026-01-07 | 12 | 0 | 1 | 0 | 10
PIB-000037 | 8 | BY-S29-05 | Bayou | CT-11 | 2026-01-07 | 7 | 0 | 1 | 0 | 7
PIB-000038 | 15 | BY-S29-05 | Bayou | CT-11 | 2026-01-07 | 15 | 0 | 0 | 0 | 12
PIB-000039 | 17 | BY-S29-05 | Bayou | CT-11 | 2026-01-07 | 15 | 0 | 0 | 2 | 16
PIB-000040 | 6 | CR-S30-02 | Crossroads | CT-11 | 2026-01-07 | 6 | 0 | 0 | 0 | 5
PIB-000041 | 15 | BY-S15-03 | Bayou | CT-11 | 2026-01-08 | 13 | 2 | 0 | 0 | 14
PIB-000042 | 8 | BY-S25-03 | Bayou | CT-11 | 2026-01-08 | 5 | 2 | 0 | 1 | 6
PIB-000043 | 12 | BY-S29-05 | Bayou | CT-11 | 2026-01-08 | 12 | 0 | 0 | 0 | 12
PIB-000044 | 19 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 17 | 0 | 0 | 2 | 13
PIB-000045 | 7 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 7 | 0 | 0 | 0 | 6
PIB-000046 | 18 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 15 | 0 | 0 | 3 | 15
PIB-000047 | 20 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 19 | 1 | 0 | 0 | 17
PIB-000048 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 9 | 1 | 0 | 0 | 9
PIB-000049 | 18 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 18 | 0 | 0 | 0 | 17
PIB-000050 | 19 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 18 | 1 | 0 | 0 | 19
PIB-000051 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 9 | 0 | 0 | 1 | 8
PIB-000052 | 16 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 16 | 0 | 0 | 0 | 15
PIB-000053 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-09 | 10 | 0 | 0 | 0 | 9
PIB-000054 | 19 | BY-S25-03 | Bayou | CT-11 | 2026-01-09 | 18 | 0 | 0 | 1 | 14
PIB-000055 | 7 | BY-S25-03 | Bayou | CT-11 | 2026-01-09 | 7 | 0 | 0 | 0 | 6
PIB-000056 | 12 | BY-S29-05 | Bayou | CT-11 | 2026-01-09 | 12 | 0 | 0 | 0 | 11
PIB-000057 | 9 | BY-S29-05 | Bayou | CT-11 | 2026-01-09 | 9 | 0 | 0 | 0 | 8
PIB-000058 | 17 | BY-S29-05 | Bayou | CT-11 | 2026-01-09 | 15 | 0 | 0 | 2 | 15
PIB-000059 | 19 | BY-S29-05 | Bayou | CT-11 | 2026-01-09 | 19 | 0 | 0 | 0 | 17
PIB-000060 | 8 | CR-S30-02 | Crossroads | CT-11 | 2026-01-09 | 7 | 1 | 0 | 0 | 6
PIB-000061 | 11 | BY-S15-03 | Bayou | CT-11 | 2026-01-12 | 10 | 0 | 1 | 0 | 9
PIB-000062 | 14 | BY-S19-04 | Bayou | CT-11 | 2026-01-12 | 13 | 0 | 1 | 0 | 12
PIB-000063 | 21 | BY-S29-05 | Bayou | CT-11 | 2026-01-12 | 21 | 0 | 0 | 0 | 17
PIB-000064 | 21 | CR-S30-02 | Crossroads | CT-11 | 2026-01-12 | 19 | 2 | 0 | 0 | 19
PIB-000065 | 14 | CR-S30-02 | Crossroads | CT-11 | 2026-01-12 | 8 | 2 | 1 | 3 | 12
PIB-000066 | 12 | BY-S15-03 | Bayou | CT-11 | 2026-01-13 | 10 | 0 | 0 | 2 | 10
PIB-000067 | 20 | BY-S15-03 | Bayou | CT-11 | 2026-01-13 | 19 | 1 | 0 | 0 | 19
PIB-000068 | 18 | BY-S15-03 | Bayou | CT-11 | 2026-01-13 | 16 | 2 | 0 | 0 | 14
PIB-000069 | 7 | BY-S15-03 | Bayou | CT-11 | 2026-01-13 | 6 | 0 | 1 | 0 | 5
PIB-000070 | 12 | BY-S15-03 | Bayou | CT-11 | 2026-01-13 | 12 | 0 | 0 | 0 | 12
PIB-000071 | 19 | BY-S29-05 | Bayou | CT-11 | 2026-01-13 | 18 | 0 | 0 | 1 | 15
PIB-000072 | 12 | BY-S29-05 | Bayou | CT-11 | 2026-01-13 | 11 | 0 | 1 | 0 | 11
PIB-000073 | 7 | BY-S29-05 | Bayou | CT-11 | 2026-01-13 | 7 | 0 | 0 | 0 | 6
PIB-000074 | 11 | BY-S29-05 | Bayou | CT-11 | 2026-01-13 | 10 | 0 | 0 | 1 | 10
PIB-000075 | 17 | BY-S29-05 | Bayou | CT-11 | 2026-01-13 | 16 | 0 | 0 | 1 | 15
PIB-000076 | 13 | CR-S30-02 | Crossroads | CT-11 | 2026-01-13 | 11 | 2 | 0 | 0 | 12
PIB-000077 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-14 | 10 | 0 | 0 | 0 | 7
PIB-000078 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-14 | 8 | 0 | 0 | 2 | 10
PIB-000079 | 18 | BY-S15-03 | Bayou | CT-11 | 2026-01-14 | 16 | 0 | 0 | 2 | 16
PIB-000080 | 11 | BY-S19-04 | Bayou | CT-11 | 2026-01-14 | 10 | 0 | 0 | 1 | 11
PIB-000081 | 13 | BY-S25-03 | Bayou | CT-11 | 2026-01-14 | 12 | 1 | 0 | 0 | 12
PIB-000082 | 7 | BY-S29-05 | Bayou | CT-11 | 2026-01-14 | 7 | 0 | 0 | 0 | 6
PIB-000083 | 13 | BY-S29-05 | Bayou | CT-11 | 2026-01-14 | 13 | 0 | 0 | 0 | 11
PIB-000084 | 13 | BY-S29-05 | Bayou | CT-11 | 2026-01-14 | 12 | 0 | 0 | 1 | 10
PIB-000085 | 9 | BY-S29-05 | Bayou | CT-11 | 2026-01-14 | 9 | 0 | 0 | 0 | 7
PIB-000086 | 15 | BY-S15-03 | Bayou | CT-11 | 2026-01-15 | 12 | 1 | 0 | 2 | 13
PIB-000087 | 17 | BY-S15-03 | Bayou | CT-11 | 2026-01-15 | 14 | 1 | 0 | 2 | 14
PIB-000088 | 17 | BY-S25-03 | Bayou | CT-11 | 2026-01-15 | 17 | 0 | 0 | 0 | 14
PIB-000089 | 21 | BY-S25-03 | Bayou | CT-11 | 2026-01-15 | 20 | 0 | 0 | 1 | 17
PIB-000090 | 18 | BY-S29-05 | Bayou | CT-11 | 2026-01-15 | 17 | 1 | 0 | 0 | 15
PIB-000091 | 14 | CR-S30-02 | Crossroads | CT-11 | 2026-01-15 | 13 | 0 | 0 | 1 | 11
PIB-000092 | 17 | BY-S15-03 | Bayou | CT-11 | 2026-01-16 | 17 | 0 | 0 | 0 | 17
PIB-000093 | 7 | BY-S15-03 | Bayou | CT-11 | 2026-01-16 | 7 | 0 | 0 | 0 | 7
PIB-000094 | 7 | BY-S15-03 | Bayou | CT-11 | 2026-01-16 | 7 | 0 | 0 | 0 | 7
PIB-000095 | 19 | BY-S19-04 | Bayou | CT-11 | 2026-01-16 | 18 | 0 | 0 | 1 | 16
PIB-000096 | 6 | BY-S25-03 | Bayou | CT-11 | 2026-01-16 | 6 | 0 | 0 | 0 | 6
PIB-000097 | 15 | BY-S25-03 | Bayou | CT-11 | 2026-01-16 | 12 | 1 | 0 | 2 | 12
PIB-000098 | 10 | BY-S29-05 | Bayou | CT-11 | 2026-01-16 | 9 | 0 | 0 | 1 | 7
PIB-000099 | 21 | BY-S29-05 | Bayou | CT-11 | 2026-01-16 | 21 | 0 | 0 | 0 | 20
PIB-000100 | 11 | BY-S29-05 | Bayou | CT-11 | 2026-01-16 | 11 | 0 | 0 | 0 | 9
PIB-000101 | 9 | CR-S30-02 | Crossroads | CT-11 | 2026-01-16 | 8 | 0 | 0 | 1 | 7
PIB-000102 | 20 | BY-S15-03 | Bayou | CT-11 | 2026-01-19 | 20 | 0 | 0 | 0 | 14
PIB-000103 | 15 | BY-S15-03 | Bayou | CT-11 | 2026-01-19 | 15 | 0 | 0 | 0 | 13
PIB-000104 | 14 | BY-S15-03 | Bayou | CT-11 | 2026-01-19 | 13 | 1 | 0 | 0 | 10
PIB-000105 | 7 | BY-S15-03 | Bayou | CT-11 | 2026-01-19 | 7 | 0 | 0 | 0 | 6
PIB-000106 | 15 | BY-S25-03 | Bayou | CT-11 | 2026-01-19 | 13 | 1 | 0 | 1 | 12
PIB-000107 | 9 | BY-S29-05 | Bayou | CT-11 | 2026-01-19 | 7 | 0 | 0 | 2 | 9
PIB-000108 | 12 | BY-S15-03 | Bayou | CT-11 | 2026-01-20 | 11 | 0 | 0 | 1 | 10
PIB-000109 | 20 | BY-S15-03 | Bayou | CT-11 | 2026-01-20 | 19 | 0 | 0 | 1 | 18
PIB-000110 | 11 | BY-S15-03 | Bayou | CT-11 | 2026-01-20 | 10 | 0 | 0 | 1 | 9
PIB-000111 | 13 | BY-S19-04 | Bayou | CT-11 | 2026-01-20 | 12 | 1 | 0 | 0 | 12
PIB-000112 | 11 | BY-S25-03 | Bayou | CT-11 | 2026-01-20 | 10 | 0 | 0 | 1 | 9
PIB-000113 | 10 | BY-S25-03 | Bayou | CT-11 | 2026-01-20 | 10 | 0 | 0 | 0 | 8
PIB-000114 | 20 | BY-S29-05 | Bayou | CT-11 | 2026-01-20 | 17 | 2 | 0 | 1 | 18
PIB-000115 | 18 | BY-S29-05 | Bayou | CT-11 | 2026-01-20 | 18 | 0 | 0 | 0 | 15
PIB-000116 | 7 | CR-S30-02 | Crossroads | CT-11 | 2026-01-20 | 7 | 0 | 0 | 0 | 5
PIB-000117 | 19 | BY-S15-03 | Bayou | CT-11 | 2026-01-21 | 18 | 0 | 0 | 1 | 17
PIB-000118 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-21 | 10 | 0 | 0 | 0 | 8
PIB-000119 | 4 | BY-S19-04 | Bayou | CT-11 | 2026-01-21 | 4 | 0 | 0 | 0 | 3
PIB-000120 | 12 | BY-S29-05 | Bayou | CT-11 | 2026-01-21 | 9 | 1 | 0 | 2 | 11
PIB-000121 | 17 | BY-S29-05 | Bayou | CT-11 | 2026-01-21 | 16 | 1 | 0 | 0 | 15
PIB-000122 | 12 | BY-S29-05 | Bayou | CT-11 | 2026-01-21 | 11 | 1 | 0 | 0 | 10
PIB-000123 | 15 | CR-S30-02 | Crossroads | CT-11 | 2026-01-21 | 14 | 0 | 1 | 0 | 14
PIB-000124 | 21 | BY-S15-03 | Bayou | CT-11 | 2026-01-22 | 20 | 0 | 0 | 1 | 17
PIB-000125 | 13 | BY-S15-03 | Bayou | CT-11 | 2026-01-22 | 13 | 0 | 0 | 0 | 11
PIB-000126 | 18 | BY-S29-05 | Bayou | CT-11 | 2026-01-22 | 17 | 0 | 1 | 0 | 17
PIB-000127 | 18 | BY-S29-05 | Bayou | CT-11 | 2026-01-22 | 17 | 0 | 0 | 1 | 15
PIB-000128 | 15 | BY-S29-05 | Bayou | CT-11 | 2026-01-22 | 14 | 0 | 0 | 1 | 12
PIB-000129 | 10 | BY-S29-05 | Bayou | CT-11 | 2026-01-22 | 10 | 0 | 0 | 0 | 9
PIB-000130 | 12 | BY-S29-05 | Bayou | CT-11 | 2026-01-22 | 11 | 1 | 0 | 0 | 10
PIB-000131 | 21 | CR-S30-02 | Crossroads | CT-11 | 2026-01-22 | 19 | 0 | 2 | 0 | 20
PIB-000132 | 9 | BY-S15-03 | Bayou | CT-11 | 2026-01-23 | 7 | 1 | 0 | 1 | 8
PIB-000133 | 14 | BY-S15-03 | Bayou | CT-11 | 2026-01-23 | 14 | 0 | 0 | 0 | 12
PIB-000134 | 13 | BY-S25-03 | Bayou | CT-11 | 2026-01-23 | 13 | 0 | 0 | 0 | 9
PIB-000135 | 7 | BY-S25-03 | Bayou | CT-11 | 2026-01-23 | 6 | 0 | 0 | 1 | 7
PIB-000136 | 8 | BY-S25-03 | Bayou | CT-11 | 2026-01-23 | 7 | 1 | 0 | 0 | 6
PIB-000137 | 20 | BY-S29-05 | Bayou | CT-11 | 2026-01-23 | 18 | 0 | 0 | 2 | 17
PIB-000138 | 18 | CR-S30-02 | Crossroads | CT-11 | 2026-01-23 | 14 | 1 | 1 | 2 | 16
PIB-000139 | 12 | BY-S15-03 | Bayou | CT-11 | 2026-01-26 | 12 | 0 | 0 | 0 | 10
PIB-000140 | 16 | BY-S19-04 | Bayou | CT-11 | 2026-01-26 | 14 | 0 | 0 | 2 | 15
PIB-000141 | 10 | CR-S30-02 | Crossroads | CT-11 | 2026-01-26 | 10 | 0 | 0 | 0 | 9
PIB-000142 | 16 | BY-S15-03 | Bayou | CT-11 | 2026-01-27 | 15 | 0 | 0 | 1 | 13
PIB-000143 | 15 | BY-S19-04 | Bayou | CT-11 | 2026-01-27 | 15 | 0 | 0 | 0 | 12
PIB-000144 | 10 | BY-S29-05 | Bayou | CT-11 | 2026-01-27 | 9 | 1 | 0 | 0 | 9
PIB-000145 | 15 | BY-S29-05 | Bayou | CT-11 | 2026-01-27 | 13 | 1 | 0 | 1 | 13
PIB-000146 | 8 | CR-S30-02 | Crossroads | CT-11 | 2026-01-27 | 8 | 0 | 0 | 0 | 7
PIB-000147 | 12 | BY-S15-03 | Bayou | CT-11 | 2026-01-28 | 12 | 0 | 0 | 0 | 12
PIB-000148 | 14 | BY-S25-03 | Bayou | CT-11 | 2026-01-28 | 13 | 0 | 0 | 1 | 12
PIB-000149 | 9 | BY-S29-05 | Bayou | CT-11 | 2026-01-28 | 9 | 0 | 0 | 0 | 6
PIB-000150 | 21 | CR-S30-02 | Crossroads | CT-11 | 2026-01-28 | 21 | 0 | 0 | 0 | 17
PIB-000151 | 16 | CR-S30-02 | Crossroads | CT-11 | 2026-01-28 | 14 | 2 | 0 | 0 | 13
PIB-000152 | 21 | CR-S30-02 | Crossroads | CT-11 | 2026-01-28 | 15 | 1 | 2 | 3 | 18
PIB-000153 | 19 | BY-S15-03 | Bayou | CT-11 | 2026-01-29 | 18 | 0 | 0 | 1 | 14
PIB-000154 | 18 | BY-S15-03 | Bayou | CT-11 | 2026-01-29 | 18 | 0 | 0 | 0 | 18
PIB-000155 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-29 | 9 | 1 | 0 | 0 | 9
PIB-000156 | 10 | BY-S15-03 | Bayou | CT-11 | 2026-01-29 | 10 | 0 | 0 | 0 | 8
PIB-000157 | 17 | BY-S15-03 | Bayou | CT-11 | 2026-01-29 | 16 | 0 | 0 | 1 | 14
PIB-000158 | 14 | BY-S19-04 | Bayou | CT-11 | 2026-01-29 | 12 | 1 | 0 | 1 | 13
PIB-000159 | 18 | BY-S19-04 | Bayou | CT-11 | 2026-01-29 | 17 | 0 | 1 | 0 | 18
PIB-000160 | 14 | BY-S29-05 | Bayou | CT-11 | 2026-01-29 | 14 | 0 | 0 | 0 | 12
PIB-000161 | 13 | BY-S29-05 | Bayou | CT-11 | 2026-01-29 | 13 | 0 | 0 | 0 | 11
PIB-000162 | 18 | BY-S29-05 | Bayou | CT-11 | 2026-01-29 | 18 | 0 | 0 | 0 | 15
PIB-000163 | 4 | BY-S29-05 | Bayou | CT-11 | 2026-01-29 | 4 | 0 | 0 | 0 | 3
PIB-000164 | 11 | CR-S30-02 | Crossroads | CT-11 | 2026-01-29 | 11 | 0 | 0 | 0 | 11
PIB-000165 | 10 | CR-S30-02 | Crossroads | CT-11 | 2026-01-29 | 10 | 0 | 0 | 0 | 9
PIB-000166 | 8 | CR-S30-02 | Crossroads | CT-11 | 2026-01-29 | 8 | 0 | 0 | 0 | 5
PIB-000167 | 13 | BY-S15-03 | Bayou | CT-11 | 2026-01-30 | 13 | 0 | 0 | 0 | 12
PIB-000168 | 15 | BY-S15-03 | Bayou | CT-11 | 2026-01-30 | 14 | 1 | 0 | 0 | 13
PIB-000169 | 6 | BY-S29-05 | Bayou | CT-11 | 2026-01-30 | 4 | 0 | 2 | 0 | 6
PIB-000170 | 20 | BY-S29-05 | Bayou | CT-11 | 2026-01-30 | 19 | 0 | 1 | 0 | 19
PIB-000171 | 9 | CR-S30-02 | Crossroads | CT-11 | 2026-01-30 | 8 | 0 | 0 | 1 | 8
PIB-000172 | 17 | BY-S16-05 | Bayou | CT-11 | 2026-02-02 | 16 | 0 | 0 | 1 | 13
PIB-000173 | 14 | BY-S19-04 | Bayou | CT-11 | 2026-02-02 | 13 | 0 | 0 | 1 | 11
PIB-000174 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-02 | 11 | 0 | 0 | 0 | 10
PIB-000175 | 18 | HB-S12-02 | Harbor | CT-11 | 2026-02-02 | 17 | 0 | 1 | 0 | 15
PIB-000176 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-02 | 8 | 1 | 0 | 1 | 10
PIB-000177 | 19 | HB-S12-02 | Harbor | CT-11 | 2026-02-02 | 16 | 2 | 0 | 1 | 18
PIB-000178 | 19 | HB-S12-02 | Harbor | CT-11 | 2026-02-02 | 17 | 0 | 0 | 2 | 18
PIB-000179 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-02 | 7 | 0 | 0 | 0 | 6
PIB-000180 | 13 | BY-S04-02 | Bayou | CT-11 | 2026-02-03 | 13 | 0 | 0 | 0 | 12
PIB-000181 | 11 | BY-S19-04 | Bayou | CT-11 | 2026-02-03 | 11 | 0 | 0 | 0 | 10
PIB-000182 | 21 | BY-S19-04 | Bayou | CT-11 | 2026-02-03 | 20 | 0 | 0 | 1 | 19
PIB-000183 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-03 | 12 | 0 | 0 | 0 | 12
PIB-000184 | 18 | HB-S12-02 | Harbor | CT-11 | 2026-02-03 | 18 | 0 | 0 | 0 | 15
PIB-000185 | 13 | HB-S12-02 | Harbor | CT-11 | 2026-02-03 | 12 | 1 | 0 | 0 | 10
PIB-000186 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-03 | 19 | 1 | 0 | 0 | 16
PIB-000187 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-03 | 11 | 0 | 0 | 0 | 11
PIB-000188 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-03 | 9 | 1 | 0 | 0 | 9
PIB-000189 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-03 | 9 | 1 | 0 | 0 | 5
PIB-000190 | 11 | BY-S04-02 | Bayou | CT-11 | 2026-02-04 | 10 | 0 | 1 | 0 | 8
PIB-000191 | 19 | BY-S19-04 | Bayou | CT-11 | 2026-02-04 | 17 | 0 | 0 | 2 | 17
PIB-000192 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-04 | 10 | 0 | 0 | 0 | 10
PIB-000193 | 15 | HB-S12-02 | Harbor | CT-11 | 2026-02-04 | 15 | 0 | 0 | 0 | 12
PIB-000194 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-04 | 9 | 2 | 0 | 0 | 11
PIB-000195 | 9 | BY-S04-02 | Bayou | CT-11 | 2026-02-05 | 9 | 0 | 0 | 0 | 7
PIB-000196 | 9 | BY-S04-02 | Bayou | CT-11 | 2026-02-05 | 8 | 1 | 0 | 0 | 9
PIB-000197 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-05 | 13 | 0 | 1 | 0 | 13
PIB-000198 | 8 | HB-S12-02 | Harbor | CT-11 | 2026-02-05 | 8 | 0 | 0 | 0 | 8
PIB-000199 | 6 | HB-S12-02 | Harbor | CT-11 | 2026-02-05 | 6 | 0 | 0 | 0 | 4
PIB-000200 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-05 | 19 | 0 | 0 | 1 | 16
PIB-000201 | 13 | BY-S04-02 | Bayou | CT-11 | 2026-02-06 | 12 | 0 | 0 | 1 | 9
PIB-000202 | 10 | BY-S19-04 | Bayou | CT-11 | 2026-02-06 | 10 | 0 | 0 | 0 | 7
PIB-000203 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 10 | 1 | 0 | 0 | 9
PIB-000204 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 12 | 0 | 0 | 0 | 10
PIB-000205 | 15 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 13 | 0 | 0 | 2 | 12
PIB-000206 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 10 | 0 | 0 | 0 | 9
PIB-000207 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 12 | 0 | 0 | 0 | 11
PIB-000208 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 7 | 0 | 0 | 0 | 5
PIB-000209 | 8 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 7 | 0 | 1 | 0 | 4
PIB-000210 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 14 | 0 | 2 | 1 | 15
PIB-000211 | 8 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 8 | 0 | 0 | 0 | 7
PIB-000212 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-06 | 15 | 0 | 1 | 0 | 14
PIB-000213 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 17 | 0 | 0 | 0 | 14
PIB-000214 | 9 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 9 | 0 | 0 | 0 | 8
PIB-000215 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 13 | 0 | 0 | 1 | 10
PIB-000216 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 13 | 1 | 0 | 0 | 12
PIB-000217 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 13 | 0 | 0 | 1 | 12
PIB-000218 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 7 | 0 | 0 | 0 | 7
PIB-000219 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 12 | 0 | 0 | 0 | 12
PIB-000220 | 15 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 13 | 2 | 0 | 0 | 13
PIB-000221 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 14 | 0 | 0 | 0 | 13
PIB-000222 | 18 | HB-S12-02 | Harbor | CT-11 | 2026-02-09 | 18 | 0 | 0 | 0 | 15
PIB-000223 | 21 | BY-S04-02 | Bayou | CT-11 | 2026-02-10 | 18 | 2 | 0 | 1 | 16
PIB-000224 | 8 | BY-S19-04 | Bayou | CT-11 | 2026-02-10 | 8 | 0 | 0 | 0 | 8
PIB-000225 | 7 | BY-S19-04 | Bayou | CT-11 | 2026-02-10 | 7 | 0 | 0 | 0 | 5
PIB-000226 | 16 | BY-S19-04 | Bayou | CT-11 | 2026-02-10 | 15 | 1 | 0 | 0 | 13
PIB-000227 | 19 | BY-S19-04 | Bayou | CT-11 | 2026-02-10 | 18 | 1 | 0 | 0 | 14
PIB-000228 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-10 | 15 | 0 | 0 | 2 | 14
PIB-000229 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-10 | 10 | 1 | 0 | 1 | 11
PIB-000230 | 8 | HB-S12-02 | Harbor | CT-11 | 2026-02-10 | 8 | 0 | 0 | 0 | 6
PIB-000231 | 9 | HB-S12-02 | Harbor | CT-11 | 2026-02-10 | 7 | 2 | 0 | 0 | 8
PIB-000232 | 18 | BY-S04-02 | Bayou | CT-11 | 2026-02-11 | 17 | 1 | 0 | 0 | 17
PIB-000233 | 16 | BY-S16-05 | Bayou | CT-11 | 2026-02-11 | 16 | 0 | 0 | 0 | 12
PIB-000234 | 18 | BY-S19-04 | Bayou | CT-11 | 2026-02-11 | 16 | 0 | 0 | 2 | 16
PIB-000235 | 4 | BY-S19-04 | Bayou | CT-11 | 2026-02-11 | 3 | 1 | 0 | 0 | 4
PIB-000236 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-11 | 14 | 0 | 0 | 0 | 13
PIB-000237 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-11 | 12 | 0 | 0 | 0 | 12
PIB-000238 | 20 | BY-S04-02 | Bayou | CT-11 | 2026-02-12 | 19 | 0 | 0 | 1 | 19
PIB-000239 | 20 | BY-S19-04 | Bayou | CT-11 | 2026-02-12 | 19 | 0 | 0 | 1 | 19
PIB-000240 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-12 | 12 | 0 | 0 | 0 | 11
PIB-000241 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-12 | 13 | 0 | 0 | 3 | 14
PIB-000242 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-12 | 17 | 0 | 0 | 0 | 11
PIB-000243 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-12 | 10 | 1 | 0 | 0 | 8
PIB-000244 | 13 | HB-S12-02 | Harbor | CT-11 | 2026-02-12 | 12 | 0 | 0 | 1 | 11
PIB-000245 | 8 | HB-S12-02 | Harbor | CT-11 | 2026-02-12 | 8 | 0 | 0 | 0 | 7
PIB-000246 | 13 | BY-S04-02 | Bayou | CT-11 | 2026-02-13 | 13 | 0 | 0 | 0 | 12
PIB-000247 | 12 | BY-S04-02 | Bayou | CT-11 | 2026-02-13 | 12 | 0 | 0 | 0 | 11
PIB-000248 | 9 | BY-S19-04 | Bayou | CT-11 | 2026-02-13 | 9 | 0 | 0 | 0 | 9
PIB-000249 | 15 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 12 | 0 | 0 | 3 | 12
PIB-000250 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 14 | 1 | 0 | 1 | 16
PIB-000251 | 6 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 6 | 0 | 0 | 0 | 5
PIB-000252 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 19 | 0 | 1 | 0 | 18
PIB-000253 | 15 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 15 | 0 | 0 | 0 | 15
PIB-000254 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 15 | 1 | 1 | 0 | 14
PIB-000255 | 9 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 9 | 0 | 0 | 0 | 8
PIB-000256 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 12 | 0 | 0 | 0 | 10
PIB-000257 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-13 | 16 | 1 | 0 | 0 | 15
PIB-000258 | 3 | BY-S04-02 | Bayou | CT-11 | 2026-02-16 | 2 | 0 | 0 | 1 | 2
PIB-000259 | 17 | BY-S19-04 | Bayou | CT-11 | 2026-02-16 | 16 | 0 | 0 | 1 | 16
PIB-000260 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 17 | 1 | 0 | 2 | 17
PIB-000261 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 12 | 1 | 1 | 3 | 17
PIB-000262 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 16 | 0 | 0 | 0 | 13
PIB-000263 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 19 | 0 | 0 | 1 | 15
PIB-000264 | 13 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 12 | 0 | 0 | 1 | 12
PIB-000265 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 10 | 1 | 1 | 0 | 10
PIB-000266 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 11 | 0 | 0 | 1 | 10
PIB-000267 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 12 | 0 | 0 | 0 | 7
PIB-000268 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 12 | 2 | 0 | 0 | 8
PIB-000269 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 13 | 0 | 1 | 0 | 12
PIB-000270 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-16 | 12 | 0 | 0 | 0 | 11
PIB-000271 | 11 | BY-S19-04 | Bayou | CT-11 | 2026-02-17 | 11 | 0 | 0 | 0 | 11
PIB-000272 | 19 | BY-S19-04 | Bayou | CT-11 | 2026-02-17 | 18 | 1 | 0 | 0 | 16
PIB-000273 | 8 | BY-S19-04 | Bayou | CT-11 | 2026-02-17 | 8 | 0 | 0 | 0 | 7
PIB-000274 | 9 | HB-S12-02 | Harbor | CT-11 | 2026-02-17 | 9 | 0 | 0 | 0 | 8
PIB-000275 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-17 | 11 | 0 | 0 | 0 | 9
PIB-000276 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-17 | 12 | 1 | 0 | 1 | 11
PIB-000277 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-17 | 17 | 1 | 0 | 2 | 16
PIB-000278 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-17 | 9 | 1 | 0 | 0 | 10
PIB-000279 | 11 | BY-S19-04 | Bayou | CT-11 | 2026-02-18 | 11 | 0 | 0 | 0 | 11
PIB-000280 | 19 | HB-S12-02 | Harbor | CT-11 | 2026-02-18 | 15 | 0 | 0 | 4 | 16
PIB-000281 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-18 | 9 | 0 | 0 | 1 | 10
PIB-000282 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-18 | 14 | 1 | 1 | 0 | 16
PIB-000283 | 13 | HB-S12-02 | Harbor | CT-11 | 2026-02-18 | 13 | 0 | 0 | 0 | 13
PIB-000284 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-18 | 6 | 0 | 1 | 0 | 6
PIB-000285 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-18 | 11 | 3 | 0 | 0 | 12
PIB-000286 | 21 | HB-S12-02 | Harbor | CT-11 | 2026-02-18 | 16 | 4 | 0 | 1 | 16
PIB-000287 | 15 | BY-S04-02 | Bayou | CT-11 | 2026-02-19 | 15 | 0 | 0 | 0 | 12
PIB-000288 | 11 | BY-S16-05 | Bayou | CT-11 | 2026-02-19 | 11 | 0 | 0 | 0 | 8
PIB-000289 | 20 | BY-S19-04 | Bayou | CT-11 | 2026-02-19 | 20 | 0 | 0 | 0 | 15
PIB-000290 | 9 | HB-S12-02 | Harbor | CT-11 | 2026-02-19 | 9 | 0 | 0 | 0 | 8
PIB-000291 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-19 | 9 | 0 | 0 | 1 | 9
PIB-000292 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-19 | 15 | 0 | 0 | 2 | 14
PIB-000293 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-19 | 8 | 2 | 0 | 0 | 8
PIB-000294 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-19 | 9 | 1 | 0 | 1 | 9
PIB-000295 | 21 | HB-S12-02 | Harbor | CT-11 | 2026-02-19 | 20 | 1 | 0 | 0 | 17
PIB-000296 | 14 | HB-S12-02 | Harbor | CT-11 | 2026-02-20 | 13 | 0 | 0 | 1 | 11
PIB-000297 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-20 | 7 | 0 | 0 | 0 | 6
PIB-000298 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-20 | 6 | 0 | 1 | 0 | 5
PIB-000299 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-20 | 19 | 1 | 0 | 0 | 17
PIB-000300 | 6 | HB-S12-02 | Harbor | CT-11 | 2026-02-20 | 6 | 0 | 0 | 0 | 6
PIB-000301 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-20 | 9 | 0 | 1 | 0 | 9
PIB-000302 | 19 | HB-S12-02 | Harbor | CT-11 | 2026-02-20 | 18 | 1 | 0 | 0 | 16
PIB-000303 | 18 | HB-S12-02 | Harbor | CT-11 | 2026-02-20 | 17 | 0 | 0 | 1 | 17
PIB-000304 | 15 | BY-S04-02 | Bayou | CT-11 | 2026-02-23 | 15 | 0 | 0 | 0 | 10
PIB-000305 | 6 | BY-S04-02 | Bayou | CT-11 | 2026-02-23 | 5 | 0 | 0 | 1 | 6
PIB-000306 | 7 | BY-S04-02 | Bayou | CT-11 | 2026-02-23 | 7 | 0 | 0 | 0 | 6
PIB-000307 | 6 | BY-S16-05 | Bayou | CT-11 | 2026-02-23 | 5 | 0 | 0 | 1 | 5
PIB-000308 | 7 | BY-S19-04 | Bayou | CT-11 | 2026-02-23 | 5 | 0 | 0 | 2 | 4
PIB-000309 | 18 | HB-S12-02 | Harbor | CT-11 | 2026-02-23 | 18 | 0 | 0 | 0 | 14
PIB-000310 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-23 | 7 | 0 | 0 | 0 | 6
PIB-000311 | 21 | HB-S12-02 | Harbor | CT-11 | 2026-02-23 | 20 | 0 | 0 | 1 | 18
PIB-000312 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-23 | 16 | 0 | 0 | 0 | 14
PIB-000313 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-23 | 18 | 0 | 0 | 2 | 14
PIB-000314 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-23 | 10 | 0 | 1 | 0 | 10
PIB-000315 | 15 | HB-S12-02 | Harbor | CT-11 | 2026-02-23 | 13 | 0 | 0 | 2 | 12
PIB-000316 | 12 | BY-S04-02 | Bayou | CT-11 | 2026-02-24 | 12 | 0 | 0 | 0 | 7
PIB-000317 | 21 | BY-S04-02 | Bayou | CT-11 | 2026-02-24 | 20 | 0 | 1 | 0 | 17
PIB-000318 | 15 | BY-S04-02 | Bayou | CT-11 | 2026-02-24 | 15 | 0 | 0 | 0 | 14
PIB-000319 | 8 | BY-S16-05 | Bayou | CT-11 | 2026-02-24 | 8 | 0 | 0 | 0 | 7
PIB-000320 | 4 | BY-S16-05 | Bayou | CT-11 | 2026-02-24 | 4 | 0 | 0 | 0 | 4
PIB-000321 | 6 | BY-S19-04 | Bayou | CT-11 | 2026-02-24 | 5 | 0 | 0 | 1 | 4
PIB-000322 | 21 | BY-S19-04 | Bayou | CT-11 | 2026-02-24 | 18 | 0 | 0 | 3 | 20
PIB-000323 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-24 | 18 | 1 | 0 | 1 | 17
PIB-000324 | 13 | HB-S12-02 | Harbor | CT-11 | 2026-02-24 | 13 | 0 | 0 | 0 | 10
PIB-000325 | 18 | HB-S12-02 | Harbor | CT-11 | 2026-02-24 | 18 | 0 | 0 | 0 | 16
PIB-000326 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-24 | 7 | 0 | 0 | 0 | 5
PIB-000327 | 10 | BY-S19-04 | Bayou | CT-11 | 2026-02-25 | 10 | 0 | 0 | 0 | 10
PIB-000328 | 13 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 12 | 0 | 1 | 0 | 10
PIB-000329 | 11 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 11 | 0 | 0 | 0 | 8
PIB-000330 | 18 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 18 | 0 | 0 | 0 | 16
PIB-000331 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 15 | 0 | 0 | 1 | 14
PIB-000332 | 7 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 7 | 0 | 0 | 0 | 6
PIB-000333 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 19 | 0 | 1 | 0 | 17
PIB-000334 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 10 | 0 | 0 | 0 | 10
PIB-000335 | 19 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 19 | 0 | 0 | 0 | 18
PIB-000336 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-25 | 16 | 0 | 0 | 0 | 12
PIB-000337 | 10 | BY-S19-04 | Bayou | CT-11 | 2026-02-26 | 9 | 0 | 0 | 1 | 8
PIB-000338 | 12 | BY-S19-04 | Bayou | CT-11 | 2026-02-26 | 12 | 0 | 0 | 0 | 11
PIB-000339 | 17 | BY-S19-04 | Bayou | CT-11 | 2026-02-26 | 16 | 0 | 0 | 1 | 17
PIB-000340 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-26 | 15 | 1 | 0 | 0 | 14
PIB-000341 | 9 | HB-S12-02 | Harbor | CT-11 | 2026-02-26 | 9 | 0 | 0 | 0 | 9
PIB-000342 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-26 | 12 | 0 | 0 | 0 | 9
PIB-000343 | 10 | HB-S12-02 | Harbor | CT-11 | 2026-02-26 | 9 | 0 | 1 | 0 | 9
PIB-000344 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-26 | 15 | 0 | 0 | 1 | 14
PIB-000345 | 21 | HB-S12-02 | Harbor | CT-11 | 2026-02-26 | 18 | 0 | 0 | 3 | 16
PIB-000346 | 10 | BY-S04-02 | Bayou | CT-11 | 2026-02-27 | 8 | 0 | 0 | 2 | 8
PIB-000347 | 7 | BY-S19-04 | Bayou | CT-11 | 2026-02-27 | 6 | 0 | 0 | 1 | 4
PIB-000348 | 7 | BY-S19-04 | Bayou | CT-11 | 2026-02-27 | 7 | 0 | 0 | 0 | 5
PIB-000349 | 16 | HB-S12-02 | Harbor | CT-11 | 2026-02-27 | 16 | 0 | 0 | 0 | 12
PIB-000350 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-27 | 18 | 0 | 0 | 2 | 17
PIB-000351 | 19 | HB-S12-02 | Harbor | CT-11 | 2026-02-27 | 19 | 0 | 0 | 0 | 17
PIB-000352 | 20 | HB-S12-02 | Harbor | CT-11 | 2026-02-27 | 19 | 0 | 0 | 1 | 19
PIB-000353 | 12 | HB-S12-02 | Harbor | CT-11 | 2026-02-27 | 10 | 0 | 0 | 2 | 9
PIB-000354 | 17 | HB-S12-02 | Harbor | CT-11 | 2026-02-27 | 15 | 0 | 0 | 2 | 15
PIB-000355 | 9 | HB-S12-02 | Harbor | CT-11 | 2026-02-27 | 8 | 0 | 0 | 1 | 7
PIB-000356 | 6 | BY-S14-02 | Bayou | CT-11 | 2026-03-02 | 6 | 0 | 0 | 0 | 6
PIB-000357 | 20 | BY-S14-02 | Bayou | CT-11 | 2026-03-02 | 15 | 3 | 0 | 2 | 19
PIB-000358 | 10 | BY-S16-05 | Bayou | CT-11 | 2026-03-02 | 9 | 1 | 0 | 0 | 8
PIB-000359 | 9 | BY-S21-05 | Bayou | CT-11 | 2026-03-02 | 9 | 0 | 0 | 0 | 7
PIB-000360 | 13 | HB-S19-02 | Harbor | CT-11 | 2026-03-02 | 12 | 0 | 0 | 1 | 13
PIB-000361 | 9 | HB-S19-02 | Harbor | CT-11 | 2026-03-02 | 7 | 2 | 0 | 0 | 8
PIB-000362 | 12 | BY-S14-02 | Bayou | CT-11 | 2026-03-03 | 12 | 0 | 0 | 0 | 10
PIB-000363 | 6 | BY-S14-02 | Bayou | CT-11 | 2026-03-03 | 6 | 0 | 0 | 0 | 4
PIB-000364 | 11 | BY-S14-02 | Bayou | CT-11 | 2026-03-03 | 9 | 0 | 0 | 2 | 10
PIB-000365 | 19 | BY-S14-02 | Bayou | CT-11 | 2026-03-03 | 18 | 1 | 0 | 0 | 16
PIB-000366 | 10 | BY-S14-02 | Bayou | CT-11 | 2026-03-03 | 10 | 0 | 0 | 0 | 10
PIB-000367 | 18 | BY-S14-02 | Bayou | CT-11 | 2026-03-03 | 18 | 0 | 0 | 0 | 16
PIB-000368 | 17 | BY-S14-02 | Bayou | CT-11 | 2026-03-03 | 14 | 1 | 1 | 1 | 15
PIB-000369 | 6 | BY-S16-05 | Bayou | CT-11 | 2026-03-03 | 6 | 0 | 0 | 0 | 5
PIB-000370 | 9 | BY-S16-05 | Bayou | CT-11 | 2026-03-03 | 8 | 1 | 0 | 0 | 8
PIB-000371 | 11 | BY-S16-05 | Bayou | CT-11 | 2026-03-03 | 11 | 0 | 0 | 0 | 10
PIB-000372 | 8 | BY-S21-05 | Bayou | CT-11 | 2026-03-03 | 7 | 0 | 0 | 1 | 5
PIB-000373 | 9 | BY-S21-05 | Bayou | CT-11 | 2026-03-03 | 8 | 1 | 0 | 0 | 7
PIB-000374 | 15 | BY-S21-05 | Bayou | CT-11 | 2026-03-03 | 13 | 0 | 0 | 2 | 15
PIB-000375 | 14 | BY-S21-05 | Bayou | CT-11 | 2026-03-03 | 14 | 0 | 0 | 0 | 12
PIB-000376 | 10 | BY-S14-02 | Bayou | CT-11 | 2026-03-04 | 8 | 0 | 0 | 2 | 8
PIB-000377 | 16 | BY-S14-02 | Bayou | CT-11 | 2026-03-04 | 15 | 0 | 0 | 1 | 11
PIB-000378 | 8 | BY-S21-05 | Bayou | CT-11 | 2026-03-04 | 8 | 0 | 0 | 0 | 7
PIB-000379 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-03-04 | 18 | 0 | 0 | 1 | 18
PIB-000380 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-03-04 | 17 | 0 | 2 | 0 | 17
PIB-000381 | 12 | HB-S19-02 | Harbor | CT-11 | 2026-03-04 | 11 | 0 | 0 | 1 | 9
PIB-000382 | 9 | HB-S19-02 | Harbor | CT-11 | 2026-03-04 | 8 | 0 | 1 | 0 | 7
PIB-000383 | 21 | HB-S19-02 | Harbor | CT-11 | 2026-03-04 | 21 | 0 | 0 | 0 | 18
PIB-000384 | 15 | HB-S19-02 | Harbor | CT-11 | 2026-03-04 | 15 | 0 | 0 | 0 | 14
PIB-000385 | 8 | BY-S14-02 | Bayou | CT-11 | 2026-03-05 | 8 | 0 | 0 | 0 | 8
PIB-000386 | 18 | BY-S14-02 | Bayou | CT-11 | 2026-03-05 | 15 | 3 | 0 | 0 | 17
PIB-000387 | 16 | BY-S16-05 | Bayou | CT-11 | 2026-03-05 | 14 | 0 | 0 | 2 | 13
PIB-000388 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-05 | 9 | 0 | 0 | 1 | 8
PIB-000389 | 14 | BY-S21-05 | Bayou | CT-11 | 2026-03-05 | 14 | 0 | 0 | 0 | 10
PIB-000390 | 13 | BY-S21-05 | Bayou | CT-11 | 2026-03-05 | 13 | 0 | 0 | 0 | 12
PIB-000391 | 20 | HB-S19-02 | Harbor | CT-11 | 2026-03-05 | 19 | 0 | 1 | 0 | 15
PIB-000392 | 12 | HB-S19-02 | Harbor | CT-11 | 2026-03-05 | 12 | 0 | 0 | 0 | 10
PIB-000393 | 17 | BY-S14-02 | Bayou | CT-11 | 2026-03-06 | 16 | 1 | 0 | 0 | 16
PIB-000394 | 21 | BY-S14-02 | Bayou | CT-11 | 2026-03-06 | 17 | 3 | 0 | 1 | 20
PIB-000395 | 11 | BY-S21-05 | Bayou | CT-11 | 2026-03-06 | 11 | 0 | 0 | 0 | 11
PIB-000396 | 15 | BY-S21-05 | Bayou | CT-11 | 2026-03-06 | 15 | 0 | 0 | 0 | 14
PIB-000397 | 21 | HB-S19-02 | Harbor | CT-11 | 2026-03-06 | 20 | 0 | 0 | 1 | 18
PIB-000398 | 17 | BY-S14-02 | Bayou | CT-11 | 2026-03-09 | 15 | 0 | 1 | 1 | 13
PIB-000399 | 13 | BY-S14-02 | Bayou | CT-11 | 2026-03-09 | 12 | 1 | 0 | 0 | 12
PIB-000400 | 7 | BY-S16-05 | Bayou | CT-11 | 2026-03-09 | 7 | 0 | 0 | 0 | 6
PIB-000401 | 13 | BY-S16-05 | Bayou | CT-11 | 2026-03-09 | 10 | 2 | 0 | 1 | 11
PIB-000402 | 13 | BY-S21-05 | Bayou | CT-11 | 2026-03-09 | 13 | 0 | 0 | 0 | 11
PIB-000403 | 15 | BY-S21-05 | Bayou | CT-11 | 2026-03-09 | 15 | 0 | 0 | 0 | 13
PIB-000404 | 15 | HB-S19-02 | Harbor | CT-11 | 2026-03-09 | 15 | 0 | 0 | 0 | 14
PIB-000405 | 11 | BY-S14-02 | Bayou | CT-11 | 2026-03-10 | 10 | 0 | 0 | 1 | 11
PIB-000406 | 14 | BY-S14-02 | Bayou | CT-11 | 2026-03-10 | 14 | 0 | 0 | 0 | 10
PIB-000407 | 20 | BY-S16-05 | Bayou | CT-11 | 2026-03-10 | 19 | 1 | 0 | 0 | 20
PIB-000408 | 6 | BY-S21-05 | Bayou | CT-11 | 2026-03-10 | 6 | 0 | 0 | 0 | 6
PIB-000409 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-03-10 | 17 | 1 | 0 | 0 | 18
PIB-000410 | 15 | HB-S19-02 | Harbor | CT-11 | 2026-03-10 | 14 | 1 | 0 | 0 | 13
PIB-000411 | 11 | BY-S14-02 | Bayou | CT-11 | 2026-03-11 | 11 | 0 | 0 | 0 | 9
PIB-000412 | 6 | BY-S16-05 | Bayou | CT-11 | 2026-03-11 | 6 | 0 | 0 | 0 | 5
PIB-000413 | 8 | BY-S16-05 | Bayou | CT-11 | 2026-03-11 | 8 | 0 | 0 | 0 | 6
PIB-000414 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-03-11 | 20 | 0 | 0 | 0 | 18
PIB-000415 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-03-11 | 20 | 1 | 0 | 0 | 15
PIB-000416 | 9 | HB-S19-02 | Harbor | CT-11 | 2026-03-11 | 9 | 0 | 0 | 0 | 7
PIB-000417 | 18 | HB-S19-02 | Harbor | CT-11 | 2026-03-11 | 16 | 0 | 0 | 2 | 16
PIB-000418 | 8 | HB-S19-02 | Harbor | CT-11 | 2026-03-11 | 8 | 0 | 0 | 0 | 8
PIB-000419 | 12 | HB-S19-02 | Harbor | CT-11 | 2026-03-11 | 12 | 0 | 0 | 0 | 12
PIB-000420 | 13 | HB-S19-02 | Harbor | CT-11 | 2026-03-11 | 13 | 0 | 0 | 0 | 7
PIB-000421 | 16 | BY-S14-02 | Bayou | CT-11 | 2026-03-12 | 15 | 1 | 0 | 0 | 12
PIB-000422 | 7 | BY-S14-02 | Bayou | CT-11 | 2026-03-12 | 6 | 1 | 0 | 0 | 7
PIB-000423 | 21 | BY-S14-02 | Bayou | CT-11 | 2026-03-12 | 21 | 0 | 0 | 0 | 19
PIB-000424 | 10 | BY-S16-05 | Bayou | CT-11 | 2026-03-12 | 9 | 0 | 0 | 1 | 6
PIB-000425 | 6 | BY-S16-05 | Bayou | CT-11 | 2026-03-12 | 6 | 0 | 0 | 0 | 5
PIB-000426 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-03-12 | 18 | 0 | 0 | 0 | 17
PIB-000427 | 11 | HB-S19-02 | Harbor | CT-11 | 2026-03-12 | 11 | 0 | 0 | 0 | 7
PIB-000428 | 15 | HB-S19-02 | Harbor | CT-11 | 2026-03-12 | 12 | 3 | 0 | 0 | 11
PIB-000429 | 17 | BY-S16-05 | Bayou | CT-11 | 2026-03-13 | 16 | 0 | 1 | 0 | 14
PIB-000430 | 17 | BY-S16-05 | Bayou | CT-11 | 2026-03-13 | 15 | 1 | 0 | 1 | 17
PIB-000431 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-03-13 | 21 | 0 | 0 | 0 | 16
PIB-000432 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-13 | 10 | 0 | 0 | 0 | 10
PIB-000433 | 17 | HB-S19-02 | Harbor | CT-11 | 2026-03-13 | 17 | 0 | 0 | 0 | 15
PIB-000434 | 21 | HB-S19-02 | Harbor | CT-11 | 2026-03-13 | 21 | 0 | 0 | 0 | 19
PIB-000435 | 10 | HB-S19-02 | Harbor | CT-11 | 2026-03-13 | 10 | 0 | 0 | 0 | 9
PIB-000436 | 10 | HB-S19-02 | Harbor | CT-11 | 2026-03-13 | 9 | 0 | 0 | 1 | 7
PIB-000437 | 18 | BY-S14-02 | Bayou | CT-11 | 2026-03-16 | 17 | 0 | 0 | 1 | 17
PIB-000438 | 9 | BY-S14-02 | Bayou | CT-11 | 2026-03-16 | 9 | 0 | 0 | 0 | 7
PIB-000439 | 9 | BY-S16-05 | Bayou | CT-11 | 2026-03-16 | 9 | 0 | 0 | 0 | 7
PIB-000440 | 14 | BY-S16-05 | Bayou | CT-11 | 2026-03-16 | 12 | 0 | 0 | 2 | 12
PIB-000441 | 12 | BY-S21-05 | Bayou | CT-11 | 2026-03-16 | 12 | 0 | 0 | 0 | 9
PIB-000442 | 15 | HB-S19-02 | Harbor | CT-11 | 2026-03-16 | 15 | 0 | 0 | 0 | 12
PIB-000443 | 9 | BY-S14-02 | Bayou | CT-11 | 2026-03-17 | 8 | 1 | 0 | 0 | 6
PIB-000444 | 11 | BY-S14-02 | Bayou | CT-11 | 2026-03-17 | 10 | 0 | 1 | 0 | 10
PIB-000445 | 14 | BY-S14-02 | Bayou | CT-11 | 2026-03-17 | 13 | 1 | 0 | 0 | 11
PIB-000446 | 20 | BY-S14-02 | Bayou | CT-11 | 2026-03-17 | 20 | 0 | 0 | 0 | 18
PIB-000447 | 12 | BY-S21-05 | Bayou | CT-11 | 2026-03-17 | 12 | 0 | 0 | 0 | 12
PIB-000448 | 7 | BY-S21-05 | Bayou | CT-11 | 2026-03-17 | 7 | 0 | 0 | 0 | 4
PIB-000449 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-17 | 9 | 0 | 0 | 1 | 9
PIB-000450 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-03-17 | 17 | 1 | 0 | 0 | 14
PIB-000451 | 17 | HB-S19-02 | Harbor | CT-11 | 2026-03-17 | 15 | 0 | 0 | 2 | 13
PIB-000452 | 6 | HB-S19-02 | Harbor | CT-11 | 2026-03-17 | 4 | 1 | 0 | 1 | 5
PIB-000453 | 11 | BY-S14-02 | Bayou | CT-11 | 2026-03-18 | 11 | 0 | 0 | 0 | 10
PIB-000454 | 15 | BY-S14-02 | Bayou | CT-11 | 2026-03-18 | 14 | 0 | 0 | 1 | 13
PIB-000455 | 19 | BY-S14-02 | Bayou | CT-11 | 2026-03-18 | 16 | 2 | 0 | 1 | 15
PIB-000456 | 8 | BY-S16-05 | Bayou | CT-11 | 2026-03-18 | 8 | 0 | 0 | 0 | 7
PIB-000457 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-03-18 | 18 | 0 | 0 | 1 | 18
PIB-000458 | 8 | BY-S21-05 | Bayou | CT-11 | 2026-03-18 | 8 | 0 | 0 | 0 | 7
PIB-000459 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-03-18 | 20 | 0 | 0 | 1 | 20
PIB-000460 | 17 | HB-S19-02 | Harbor | CT-11 | 2026-03-18 | 15 | 0 | 0 | 2 | 15
PIB-000461 | 6 | BY-S16-05 | Bayou | CT-11 | 2026-03-19 | 5 | 0 | 0 | 1 | 5
PIB-000462 | 16 | BY-S16-05 | Bayou | CT-11 | 2026-03-19 | 15 | 0 | 1 | 0 | 15
PIB-000463 | 15 | BY-S16-05 | Bayou | CT-11 | 2026-03-19 | 11 | 2 | 0 | 2 | 13
PIB-000464 | 7 | BY-S16-05 | Bayou | CT-11 | 2026-03-19 | 7 | 0 | 0 | 0 | 6
PIB-000465 | 11 | BY-S16-05 | Bayou | CT-11 | 2026-03-19 | 11 | 0 | 0 | 0 | 10
PIB-000466 | 17 | BY-S16-05 | Bayou | CT-11 | 2026-03-19 | 15 | 2 | 0 | 0 | 15
PIB-000467 | 8 | BY-S21-05 | Bayou | CT-11 | 2026-03-19 | 8 | 0 | 0 | 0 | 4
PIB-000468 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-03-19 | 18 | 0 | 0 | 2 | 17
PIB-000469 | 6 | BY-S21-05 | Bayou | CT-11 | 2026-03-19 | 6 | 0 | 0 | 0 | 4
PIB-000470 | 8 | BY-S21-05 | Bayou | CT-11 | 2026-03-19 | 8 | 0 | 0 | 0 | 6
PIB-000471 | 6 | HB-S19-02 | Harbor | CT-11 | 2026-03-19 | 6 | 0 | 0 | 0 | 5
PIB-000472 | 21 | HB-S19-02 | Harbor | CT-11 | 2026-03-19 | 21 | 0 | 0 | 0 | 20
PIB-000473 | 9 | BY-S14-02 | Bayou | CT-11 | 2026-03-20 | 8 | 1 | 0 | 0 | 7
PIB-000474 | 8 | BY-S14-02 | Bayou | CT-11 | 2026-03-20 | 8 | 0 | 0 | 0 | 7
PIB-000475 | 6 | BY-S14-02 | Bayou | CT-11 | 2026-03-20 | 6 | 0 | 0 | 0 | 5
PIB-000476 | 20 | BY-S14-02 | Bayou | CT-11 | 2026-03-20 | 13 | 3 | 1 | 3 | 18
PIB-000477 | 6 | BY-S14-02 | Bayou | CT-11 | 2026-03-20 | 4 | 1 | 0 | 1 | 5
PIB-000478 | 7 | BY-S14-02 | Bayou | CT-11 | 2026-03-20 | 6 | 0 | 0 | 1 | 6
PIB-000479 | 16 | BY-S16-05 | Bayou | CT-11 | 2026-03-20 | 16 | 0 | 0 | 0 | 15
PIB-000480 | 7 | BY-S16-05 | Bayou | CT-11 | 2026-03-20 | 6 | 0 | 0 | 1 | 6
PIB-000481 | 19 | BY-S16-05 | Bayou | CT-11 | 2026-03-20 | 19 | 0 | 0 | 0 | 15
PIB-000482 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-03-20 | 14 | 4 | 0 | 2 | 17
PIB-000483 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-03-20 | 16 | 1 | 0 | 1 | 14
PIB-000484 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-20 | 10 | 0 | 0 | 0 | 9
PIB-000485 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-20 | 9 | 0 | 0 | 1 | 9
PIB-000486 | 17 | HB-S19-02 | Harbor | CT-11 | 2026-03-20 | 15 | 2 | 0 | 0 | 17
PIB-000487 | 18 | BY-S14-02 | Bayou | CT-11 | 2026-03-23 | 18 | 0 | 0 | 0 | 13
PIB-000488 | 10 | BY-S14-02 | Bayou | CT-11 | 2026-03-23 | 10 | 0 | 0 | 0 | 6
PIB-000489 | 18 | BY-S16-05 | Bayou | CT-11 | 2026-03-23 | 16 | 0 | 2 | 0 | 15
PIB-000490 | 21 | BY-S16-05 | Bayou | CT-11 | 2026-03-23 | 21 | 0 | 0 | 0 | 19
PIB-000491 | 9 | BY-S16-05 | Bayou | CT-11 | 2026-03-23 | 9 | 0 | 0 | 0 | 7
PIB-000492 | 14 | BY-S21-05 | Bayou | CT-11 | 2026-03-23 | 12 | 1 | 1 | 0 | 11
PIB-000493 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-23 | 9 | 1 | 0 | 0 | 9
PIB-000494 | 15 | BY-S21-05 | Bayou | CT-11 | 2026-03-23 | 15 | 0 | 0 | 0 | 13
PIB-000495 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-03-23 | 15 | 1 | 0 | 2 | 16
PIB-000496 | 8 | BY-S21-05 | Bayou | CT-11 | 2026-03-23 | 8 | 0 | 0 | 0 | 8
PIB-000497 | 18 | HB-S19-02 | Harbor | CT-11 | 2026-03-23 | 15 | 0 | 0 | 3 | 13
PIB-000498 | 15 | HB-S19-02 | Harbor | CT-11 | 2026-03-23 | 15 | 0 | 0 | 0 | 11
PIB-000499 | 18 | HB-S19-02 | Harbor | CT-11 | 2026-03-23 | 18 | 0 | 0 | 0 | 12
PIB-000500 | 10 | HB-S19-02 | Harbor | CT-11 | 2026-03-23 | 10 | 0 | 0 | 0 | 9
PIB-000501 | 19 | HB-S19-02 | Harbor | CT-11 | 2026-03-23 | 17 | 1 | 0 | 1 | 15
PIB-000502 | 12 | HB-S19-02 | Harbor | CT-11 | 2026-03-23 | 12 | 0 | 0 | 0 | 8
PIB-000503 | 18 | BY-S14-02 | Bayou | CT-11 | 2026-03-24 | 18 | 0 | 0 | 0 | 15
PIB-000504 | 13 | BY-S16-05 | Bayou | CT-11 | 2026-03-24 | 12 | 0 | 0 | 1 | 11
PIB-000505 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-03-24 | 18 | 0 | 0 | 1 | 18
PIB-000506 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-03-24 | 19 | 0 | 0 | 0 | 16
PIB-000507 | 9 | BY-S21-05 | Bayou | CT-11 | 2026-03-24 | 9 | 0 | 0 | 0 | 7
PIB-000508 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-03-24 | 17 | 0 | 0 | 1 | 15
PIB-000509 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-03-24 | 16 | 1 | 0 | 3 | 16
PIB-000510 | 20 | HB-S19-02 | Harbor | CT-11 | 2026-03-24 | 19 | 0 | 0 | 1 | 17
PIB-000511 | 19 | HB-S19-02 | Harbor | CT-11 | 2026-03-24 | 18 | 1 | 0 | 0 | 17
PIB-000512 | 6 | HB-S19-02 | Harbor | CT-11 | 2026-03-24 | 6 | 0 | 0 | 0 | 4
PIB-000513 | 12 | HB-S19-02 | Harbor | CT-11 | 2026-03-24 | 12 | 0 | 0 | 0 | 11
PIB-000514 | 20 | BY-S14-02 | Bayou | CT-11 | 2026-03-25 | 19 | 1 | 0 | 0 | 18
PIB-000515 | 9 | BY-S14-02 | Bayou | CT-11 | 2026-03-25 | 8 | 0 | 0 | 1 | 7
PIB-000516 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-25 | 10 | 0 | 0 | 0 | 8
PIB-000517 | 14 | BY-S21-05 | Bayou | CT-11 | 2026-03-25 | 10 | 0 | 0 | 4 | 12
PIB-000518 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-03-25 | 21 | 0 | 0 | 0 | 18
PIB-000519 | 15 | BY-S21-05 | Bayou | CT-11 | 2026-03-25 | 14 | 1 | 0 | 0 | 13
PIB-000520 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-03-25 | 18 | 0 | 0 | 2 | 13
PIB-000521 | 19 | HB-S19-02 | Harbor | CT-11 | 2026-03-25 | 19 | 0 | 0 | 0 | 17
PIB-000522 | 17 | BY-S14-02 | Bayou | CT-11 | 2026-03-26 | 14 | 1 | 2 | 0 | 10
PIB-000523 | 13 | BY-S14-02 | Bayou | CT-11 | 2026-03-26 | 12 | 0 | 0 | 1 | 12
PIB-000524 | 15 | BY-S16-05 | Bayou | CT-11 | 2026-03-26 | 14 | 0 | 0 | 1 | 10
PIB-000525 | 11 | BY-S16-05 | Bayou | CT-11 | 2026-03-26 | 10 | 0 | 0 | 1 | 10
PIB-000526 | 12 | BY-S16-05 | Bayou | CT-11 | 2026-03-26 | 12 | 0 | 0 | 0 | 12
PIB-000527 | 15 | BY-S16-05 | Bayou | CT-11 | 2026-03-26 | 15 | 0 | 0 | 0 | 13
PIB-000528 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-26 | 9 | 1 | 0 | 0 | 9
PIB-000529 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-26 | 10 | 0 | 0 | 0 | 8
PIB-000530 | 16 | BY-S21-05 | Bayou | CT-11 | 2026-03-26 | 16 | 0 | 0 | 0 | 13
PIB-000531 | 6 | HB-S19-02 | Harbor | CT-11 | 2026-03-26 | 6 | 0 | 0 | 0 | 4
PIB-000532 | 18 | HB-S19-02 | Harbor | CT-11 | 2026-03-26 | 13 | 1 | 0 | 4 | 13
PIB-000533 | 13 | HB-S19-02 | Harbor | CT-11 | 2026-03-26 | 12 | 0 | 0 | 1 | 12
PIB-000534 | 12 | HB-S19-02 | Harbor | CT-11 | 2026-03-26 | 12 | 0 | 0 | 0 | 8
PIB-000535 | 2 | HB-S19-02 | Harbor | CT-11 | 2026-03-26 | 2 | 0 | 0 | 0 | 0
PIB-000536 | 16 | BY-S14-02 | Bayou | CT-11 | 2026-03-27 | 16 | 0 | 0 | 0 | 14
PIB-000537 | 7 | BY-S16-05 | Bayou | CT-11 | 2026-03-27 | 7 | 0 | 0 | 0 | 6
PIB-000538 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-03-27 | 10 | 0 | 0 | 0 | 8
PIB-000539 | 13 | HB-S19-02 | Harbor | CT-11 | 2026-03-27 | 11 | 0 | 0 | 2 | 11
PIB-000540 | 16 | HB-S19-02 | Harbor | CT-11 | 2026-03-27 | 16 | 0 | 0 | 0 | 14
PIB-000541 | 11 | BY-S14-02 | Bayou | CT-11 | 2026-03-30 | 11 | 0 | 0 | 0 | 10
PIB-000542 | 19 | BY-S16-05 | Bayou | CT-11 | 2026-03-30 | 15 | 0 | 0 | 4 | 16
PIB-000543 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-03-30 | 18 | 1 | 1 | 0 | 16
PIB-000544 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-03-30 | 19 | 2 | 0 | 0 | 18
PIB-000545 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-03-30 | 18 | 0 | 0 | 0 | 16
PIB-000546 | 11 | BY-S21-05 | Bayou | CT-11 | 2026-03-30 | 11 | 0 | 0 | 0 | 10
PIB-000547 | 11 | HB-S19-02 | Harbor | CT-11 | 2026-03-30 | 8 | 0 | 0 | 3 | 10
PIB-000548 | 12 | HB-S19-02 | Harbor | CT-11 | 2026-03-30 | 12 | 0 | 0 | 0 | 12
PIB-000549 | 12 | HB-S19-02 | Harbor | CT-11 | 2026-03-30 | 11 | 1 | 0 | 0 | 10
PIB-000550 | 9 | BY-S14-02 | Bayou | CT-11 | 2026-03-31 | 8 | 0 | 1 | 0 | 9
PIB-000551 | 7 | BY-S14-02 | Bayou | CT-11 | 2026-03-31 | 7 | 0 | 0 | 0 | 7
PIB-000552 | 21 | BY-S16-05 | Bayou | CT-11 | 2026-03-31 | 20 | 1 | 0 | 0 | 20
PIB-000553 | 14 | BY-S21-05 | Bayou | CT-11 | 2026-03-31 | 13 | 1 | 0 | 0 | 13
PIB-000554 | 9 | BY-S21-05 | Bayou | CT-11 | 2026-03-31 | 8 | 1 | 0 | 0 | 7
PIB-000555 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-03-31 | 18 | 1 | 0 | 0 | 16
PIB-000556 | 14 | BY-S09-02 | Bayou | CT-11 | 2026-04-01 | 13 | 0 | 0 | 1 | 12
PIB-000557 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-04-01 | 18 | 0 | 0 | 2 | 18
PIB-000558 | 7 | BY-S29-02 | Bayou | CT-11 | 2026-04-01 | 7 | 0 | 0 | 0 | 6
PIB-000559 | 18 | BY-S29-02 | Bayou | CT-11 | 2026-04-01 | 18 | 0 | 0 | 0 | 15
PIB-000560 | 14 | BY-S21-05 | Bayou | CT-11 | 2026-04-02 | 14 | 0 | 0 | 0 | 11
PIB-000561 | 7 | BY-S29-02 | Bayou | CT-11 | 2026-04-02 | 7 | 0 | 0 | 0 | 5
PIB-000562 | 16 | BY-S29-02 | Bayou | CT-11 | 2026-04-02 | 16 | 0 | 0 | 0 | 14
PIB-000563 | 15 | BY-S29-02 | Bayou | CT-11 | 2026-04-02 | 15 | 0 | 0 | 0 | 14
PIB-000564 | 20 | BY-S29-02 | Bayou | CT-11 | 2026-04-02 | 20 | 0 | 0 | 0 | 16
PIB-000565 | 12 | BY-S29-02 | Bayou | CT-11 | 2026-04-02 | 10 | 1 | 0 | 1 | 10
PIB-000566 | 9 | HB-S20-05 | Harbor | CT-11 | 2026-04-02 | 8 | 0 | 0 | 1 | 8
PIB-000567 | 9 | PR-S13-03 | Prairie | CT-12 | 2026-04-02 | 9 | 0 | 0 | 0 | 8
PIB-000568 | 18 | PR-S13-03 | Prairie | CT-12 | 2026-04-02 | 17 | 1 | 0 | 0 | 17
PIB-000569 | 15 | PR-S13-03 | Prairie | CT-12 | 2026-04-02 | 13 | 2 | 0 | 0 | 10
PIB-000570 | 15 | HB-S20-05 | Harbor | CT-11 | 2026-04-03 | 15 | 0 | 0 | 0 | 13
PIB-000571 | 15 | HB-S20-05 | Harbor | CT-11 | 2026-04-03 | 15 | 0 | 0 | 0 | 13
PIB-000572 | 9 | PR-S13-03 | Prairie | CT-12 | 2026-04-03 | 9 | 0 | 0 | 0 | 6
PIB-000573 | 16 | PR-S13-03 | Prairie | CT-11 | 2026-04-03 | 15 | 1 | 0 | 0 | 12
PIB-000574 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-04-06 | 18 | 0 | 0 | 1 | 14
PIB-000575 | 14 | BY-S21-05 | Bayou | CT-11 | 2026-04-06 | 12 | 1 | 1 | 0 | 11
PIB-000576 | 11 | BY-S29-02 | Bayou | CT-11 | 2026-04-06 | 11 | 0 | 0 | 0 | 6
PIB-000577 | 21 | BY-S29-02 | Bayou | CT-11 | 2026-04-06 | 21 | 0 | 0 | 0 | 18
PIB-000578 | 14 | BY-S29-02 | Bayou | CT-11 | 2026-04-06 | 10 | 0 | 0 | 4 | 14
PIB-000579 | 9 | BY-S29-02 | Bayou | CT-11 | 2026-04-06 | 9 | 0 | 0 | 0 | 9
PIB-000580 | 7 | BY-S29-02 | Bayou | CT-11 | 2026-04-06 | 7 | 0 | 0 | 0 | 4
PIB-000581 | 7 | HB-S20-05 | Harbor | CT-11 | 2026-04-06 | 7 | 0 | 0 | 0 | 6
PIB-000582 | 17 | HB-S20-05 | Harbor | CT-11 | 2026-04-06 | 16 | 0 | 0 | 1 | 16
PIB-000583 | 18 | PR-S13-03 | Prairie | CT-12 | 2026-04-06 | 17 | 1 | 0 | 0 | 17
PIB-000584 | 13 | PR-S13-03 | Prairie | CT-12 | 2026-04-06 | 12 | 0 | 1 | 0 | 11
PIB-000585 | 18 | PR-S13-03 | Prairie | CT-11 | 2026-04-06 | 15 | 3 | 0 | 0 | 15
PIB-000586 | 16 | BY-S21-05 | Bayou | CT-11 | 2026-04-07 | 14 | 0 | 1 | 1 | 13
PIB-000587 | 6 | BY-S21-05 | Bayou | CT-11 | 2026-04-07 | 5 | 1 | 0 | 0 | 3
PIB-000588 | 12 | BY-S29-02 | Bayou | CT-11 | 2026-04-07 | 10 | 1 | 1 | 0 | 9
PIB-000589 | 14 | BY-S29-02 | Bayou | CT-11 | 2026-04-07 | 14 | 0 | 0 | 0 | 11
PIB-000590 | 21 | BY-S29-02 | Bayou | CT-11 | 2026-04-07 | 17 | 1 | 1 | 2 | 18
PIB-000591 | 13 | BY-S29-02 | Bayou | CT-11 | 2026-04-07 | 12 | 0 | 0 | 1 | 11
PIB-000592 | 4 | HB-S20-05 | Harbor | CT-11 | 2026-04-07 | 4 | 0 | 0 | 0 | 2
PIB-000593 | 6 | PR-S13-03 | Prairie | CT-11 | 2026-04-07 | 6 | 0 | 0 | 0 | 6
PIB-000594 | 17 | PR-S13-03 | Prairie | CT-12 | 2026-04-07 | 13 | 1 | 0 | 3 | 17
PIB-000595 | 20 | PR-S13-03 | Prairie | CT-12 | 2026-04-07 | 20 | 0 | 0 | 0 | 16
PIB-000596 | 13 | PR-S13-03 | Prairie | CT-11 | 2026-04-07 | 12 | 0 | 1 | 0 | 12
PIB-000597 | 16 | BY-S21-05 | Bayou | CT-11 | 2026-04-08 | 15 | 0 | 0 | 1 | 14
PIB-000598 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-04-08 | 15 | 2 | 1 | 0 | 17
PIB-000599 | 13 | BY-S21-05 | Bayou | CT-11 | 2026-04-08 | 12 | 0 | 0 | 1 | 10
PIB-000600 | 9 | BY-S29-02 | Bayou | CT-11 | 2026-04-08 | 8 | 1 | 0 | 0 | 8
PIB-000601 | 18 | PR-S13-03 | Prairie | CT-11 | 2026-04-08 | 17 | 0 | 0 | 1 | 17
PIB-000602 | 19 | PR-S13-03 | Prairie | CT-11 | 2026-04-08 | 16 | 2 | 0 | 1 | 16
PIB-000603 | 15 | PR-S13-03 | Prairie | CT-12 | 2026-04-08 | 11 | 0 | 1 | 3 | 13
PIB-000604 | 18 | PR-S13-03 | Prairie | CT-12 | 2026-04-08 | 17 | 1 | 0 | 0 | 17
PIB-000605 | 9 | PR-S13-03 | Prairie | CT-11 | 2026-04-08 | 9 | 0 | 0 | 0 | 7
PIB-000606 | 8 | BY-S21-05 | Bayou | CT-11 | 2026-04-09 | 8 | 0 | 0 | 0 | 7
PIB-000607 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-04-09 | 10 | 0 | 0 | 0 | 9
PIB-000608 | 13 | BY-S21-05 | Bayou | CT-11 | 2026-04-09 | 12 | 0 | 1 | 0 | 13
PIB-000609 | 17 | BY-S21-05 | Bayou | CT-11 | 2026-04-09 | 16 | 1 | 0 | 0 | 14
PIB-000610 | 6 | BY-S21-05 | Bayou | CT-11 | 2026-04-09 | 6 | 0 | 0 | 0 | 6
PIB-000611 | 10 | BY-S29-02 | Bayou | CT-11 | 2026-04-09 | 10 | 0 | 0 | 0 | 9
PIB-000612 | 15 | BY-S29-02 | Bayou | CT-11 | 2026-04-09 | 15 | 0 | 0 | 0 | 13
PIB-000613 | 12 | PR-S13-03 | Prairie | CT-12 | 2026-04-09 | 12 | 0 | 0 | 0 | 10
PIB-000614 | 19 | PR-S13-03 | Prairie | CT-11 | 2026-04-09 | 19 | 0 | 0 | 0 | 15
PIB-000615 | 14 | PR-S13-03 | Prairie | CT-12 | 2026-04-09 | 14 | 0 | 0 | 0 | 13
PIB-000616 | 14 | PR-S13-03 | Prairie | CT-11 | 2026-04-09 | 13 | 1 | 0 | 0 | 11
PIB-000617 | 15 | BY-S21-05 | Bayou | CT-11 | 2026-04-10 | 13 | 0 | 0 | 2 | 13
PIB-000618 | 20 | BY-S29-02 | Bayou | CT-11 | 2026-04-10 | 20 | 0 | 0 | 0 | 18
PIB-000619 | 18 | BY-S29-02 | Bayou | CT-11 | 2026-04-10 | 16 | 0 | 1 | 1 | 17
PIB-000620 | 17 | PR-S13-03 | Prairie | CT-12 | 2026-04-10 | 16 | 0 | 0 | 1 | 14
PIB-000621 | 15 | BY-S29-02 | Bayou | CT-11 | 2026-04-13 | 15 | 0 | 0 | 0 | 12
PIB-000622 | 8 | BY-S29-02 | Bayou | CT-11 | 2026-04-13 | 8 | 0 | 0 | 0 | 5
PIB-000623 | 14 | BY-S29-02 | Bayou | CT-11 | 2026-04-13 | 12 | 1 | 0 | 1 | 12
PIB-000624 | 10 | BY-S29-02 | Bayou | CT-11 | 2026-04-13 | 10 | 0 | 0 | 0 | 9
PIB-000625 | 13 | BY-S29-02 | Bayou | CT-11 | 2026-04-13 | 11 | 0 | 1 | 1 | 9
PIB-000626 | 16 | HB-S20-05 | Harbor | CT-11 | 2026-04-13 | 14 | 2 | 0 | 0 | 14
PIB-000627 | 12 | HB-S20-05 | Harbor | CT-11 | 2026-04-13 | 11 | 0 | 0 | 1 | 9
PIB-000628 | 7 | HB-S20-05 | Harbor | CT-11 | 2026-04-13 | 7 | 0 | 0 | 0 | 6
PIB-000629 | 20 | HB-S20-05 | Harbor | CT-11 | 2026-04-13 | 20 | 0 | 0 | 0 | 12
PIB-000630 | 17 | PR-S13-03 | Prairie | CT-11 | 2026-04-13 | 16 | 1 | 0 | 0 | 15
PIB-000631 | 15 | PR-S13-03 | Prairie | CT-11 | 2026-04-13 | 15 | 0 | 0 | 0 | 10
PIB-000632 | 15 | PR-S13-03 | Prairie | CT-12 | 2026-04-13 | 15 | 0 | 0 | 0 | 11
PIB-000633 | 11 | PR-S13-03 | Prairie | CT-12 | 2026-04-13 | 11 | 0 | 0 | 0 | 10
PIB-000634 | 19 | PR-S13-03 | Prairie | CT-11 | 2026-04-13 | 18 | 0 | 1 | 0 | 18
PIB-000635 | 20 | PR-S13-03 | Prairie | CT-11 | 2026-04-13 | 18 | 1 | 1 | 0 | 18
PIB-000636 | 16 | PR-S13-03 | Prairie | CT-12 | 2026-04-13 | 15 | 0 | 0 | 1 | 14
PIB-000637 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-04-14 | 17 | 0 | 0 | 2 | 15
PIB-000638 | 21 | BY-S29-02 | Bayou | CT-11 | 2026-04-14 | 20 | 1 | 0 | 0 | 21
PIB-000639 | 10 | PR-S13-03 | Prairie | CT-12 | 2026-04-14 | 7 | 0 | 1 | 2 | 9
PIB-000640 | 10 | PR-S13-03 | Prairie | CT-11 | 2026-04-14 | 9 | 0 | 0 | 1 | 9
PIB-000641 | 7 | PR-S13-03 | Prairie | CT-12 | 2026-04-14 | 6 | 0 | 0 | 1 | 7
PIB-000642 | 13 | PR-S13-03 | Prairie | CT-12 | 2026-04-14 | 11 | 1 | 0 | 1 | 12
PIB-000643 | 6 | BY-S21-05 | Bayou | CT-11 | 2026-04-15 | 5 | 1 | 0 | 0 | 4
PIB-000644 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-04-15 | 20 | 0 | 0 | 1 | 17
PIB-000645 | 20 | BY-S29-02 | Bayou | CT-11 | 2026-04-15 | 20 | 0 | 0 | 0 | 19
PIB-000646 | 12 | BY-S29-02 | Bayou | CT-11 | 2026-04-15 | 10 | 2 | 0 | 0 | 9
PIB-000647 | 19 | BY-S29-02 | Bayou | CT-11 | 2026-04-15 | 18 | 1 | 0 | 0 | 14
PIB-000648 | 15 | BY-S29-02 | Bayou | CT-11 | 2026-04-15 | 14 | 1 | 0 | 0 | 13
PIB-000649 | 15 | HB-S20-05 | Harbor | CT-11 | 2026-04-15 | 13 | 0 | 0 | 2 | 13
PIB-000650 | 10 | PR-S13-03 | Prairie | CT-12 | 2026-04-15 | 10 | 0 | 0 | 0 | 7
PIB-000651 | 12 | PR-S13-03 | Prairie | CT-11 | 2026-04-15 | 10 | 0 | 0 | 2 | 10
PIB-000652 | 19 | PR-S13-03 | Prairie | CT-11 | 2026-04-15 | 19 | 0 | 0 | 0 | 19
PIB-000653 | 13 | PR-S13-03 | Prairie | CT-11 | 2026-04-15 | 10 | 3 | 0 | 0 | 11
PIB-000654 | 17 | BY-S29-02 | Bayou | CT-11 | 2026-04-16 | 17 | 0 | 0 | 0 | 14
PIB-000655 | 12 | BY-S29-02 | Bayou | CT-11 | 2026-04-16 | 10 | 1 | 0 | 1 | 11
PIB-000656 | 9 | BY-S29-02 | Bayou | CT-11 | 2026-04-16 | 8 | 0 | 0 | 1 | 9
PIB-000657 | 15 | HB-S20-05 | Harbor | CT-11 | 2026-04-16 | 14 | 1 | 0 | 0 | 13
PIB-000658 | 8 | HB-S20-05 | Harbor | CT-11 | 2026-04-16 | 8 | 0 | 0 | 0 | 8
PIB-000659 | 14 | HB-S20-05 | Harbor | CT-11 | 2026-04-16 | 14 | 0 | 0 | 0 | 12
PIB-000660 | 18 | PR-S13-03 | Prairie | CT-12 | 2026-04-16 | 16 | 0 | 0 | 2 | 14
PIB-000661 | 11 | PR-S13-03 | Prairie | CT-11 | 2026-04-16 | 8 | 0 | 0 | 3 | 9
PIB-000662 | 6 | PR-S13-03 | Prairie | CT-12 | 2026-04-16 | 6 | 0 | 0 | 0 | 6
PIB-000663 | 10 | BY-S21-05 | Bayou | CT-11 | 2026-04-17 | 10 | 0 | 0 | 0 | 8
PIB-000664 | 9 | BY-S29-02 | Bayou | CT-11 | 2026-04-17 | 8 | 0 | 0 | 1 | 7
PIB-000665 | 14 | BY-S29-02 | Bayou | CT-11 | 2026-04-17 | 13 | 0 | 0 | 1 | 12
PIB-000666 | 17 | BY-S29-02 | Bayou | CT-11 | 2026-04-17 | 17 | 0 | 0 | 0 | 14
PIB-000667 | 10 | PR-S13-03 | Prairie | CT-12 | 2026-04-17 | 10 | 0 | 0 | 0 | 9
PIB-000668 | 14 | PR-S13-03 | Prairie | CT-12 | 2026-04-17 | 12 | 0 | 0 | 2 | 11
PIB-000669 | 8 | PR-S13-03 | Prairie | CT-12 | 2026-04-17 | 8 | 0 | 0 | 0 | 4
PIB-000670 | 21 | PR-S13-03 | Prairie | CT-12 | 2026-04-17 | 21 | 0 | 0 | 0 | 15
PIB-000671 | 18 | PR-S13-03 | Prairie | CT-12 | 2026-04-17 | 18 | 0 | 0 | 0 | 14
PIB-000672 | 18 | BY-S29-02 | Bayou | CT-11 | 2026-04-20 | 15 | 1 | 0 | 2 | 16
PIB-000673 | 15 | BY-S29-02 | Bayou | CT-11 | 2026-04-20 | 13 | 0 | 0 | 2 | 14
PIB-000674 | 19 | BY-S29-02 | Bayou | CT-11 | 2026-04-20 | 18 | 1 | 0 | 0 | 16
PIB-000675 | 10 | HB-S20-05 | Harbor | CT-11 | 2026-04-20 | 9 | 0 | 0 | 1 | 9
PIB-000676 | 16 | HB-S20-05 | Harbor | CT-11 | 2026-04-20 | 16 | 0 | 0 | 0 | 13
PIB-000677 | 8 | HB-S20-05 | Harbor | CT-11 | 2026-04-20 | 6 | 0 | 1 | 1 | 8
PIB-000678 | 10 | HB-S20-05 | Harbor | CT-11 | 2026-04-20 | 10 | 0 | 0 | 0 | 9
PIB-000679 | 6 | PR-S13-03 | Prairie | CT-12 | 2026-04-20 | 6 | 0 | 0 | 0 | 6
PIB-000680 | 13 | PR-S13-03 | Prairie | CT-11 | 2026-04-20 | 13 | 0 | 0 | 0 | 11
PIB-000681 | 11 | PR-S13-03 | Prairie | CT-11 | 2026-04-20 | 11 | 0 | 0 | 0 | 9
PIB-000682 | 14 | PR-S13-03 | Prairie | CT-11 | 2026-04-20 | 14 | 0 | 0 | 0 | 14
PIB-000683 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-04-21 | 21 | 0 | 0 | 0 | 20
PIB-000684 | 7 | BY-S21-05 | Bayou | CT-11 | 2026-04-21 | 7 | 0 | 0 | 0 | 6
PIB-000685 | 19 | BY-S29-02 | Bayou | CT-11 | 2026-04-21 | 17 | 0 | 0 | 2 | 16
PIB-000686 | 21 | BY-S29-02 | Bayou | CT-11 | 2026-04-21 | 16 | 2 | 1 | 2 | 18
PIB-000687 | 14 | BY-S29-02 | Bayou | CT-11 | 2026-04-21 | 14 | 0 | 0 | 0 | 14
PIB-000688 | 17 | PR-S13-03 | Prairie | CT-12 | 2026-04-21 | 14 | 1 | 0 | 2 | 14
PIB-000689 | 11 | PR-S13-03 | Prairie | CT-11 | 2026-04-21 | 11 | 0 | 0 | 0 | 11
PIB-000690 | 6 | BY-S21-05 | Bayou | CT-11 | 2026-04-22 | 5 | 0 | 0 | 1 | 6
PIB-000691 | 6 | BY-S29-02 | Bayou | CT-11 | 2026-04-22 | 6 | 0 | 0 | 0 | 6
PIB-000692 | 11 | BY-S29-02 | Bayou | CT-11 | 2026-04-22 | 10 | 0 | 0 | 1 | 10
PIB-000693 | 7 | BY-S29-02 | Bayou | CT-11 | 2026-04-22 | 7 | 0 | 0 | 0 | 6
PIB-000694 | 15 | BY-S29-02 | Bayou | CT-11 | 2026-04-22 | 11 | 2 | 1 | 1 | 10
PIB-000695 | 9 | BY-S29-02 | Bayou | CT-11 | 2026-04-22 | 6 | 0 | 0 | 3 | 8
PIB-000696 | 21 | HB-S20-05 | Harbor | CT-11 | 2026-04-22 | 20 | 0 | 1 | 0 | 15
PIB-000697 | 19 | PR-S13-03 | Prairie | CT-12 | 2026-04-22 | 17 | 2 | 0 | 0 | 15
PIB-000698 | 9 | PR-S13-03 | Prairie | CT-12 | 2026-04-22 | 8 | 0 | 1 | 0 | 6
PIB-000699 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-04-23 | 20 | 0 | 0 | 1 | 18
PIB-000700 | 15 | BY-S29-02 | Bayou | CT-11 | 2026-04-23 | 13 | 0 | 0 | 2 | 13
PIB-000701 | 16 | BY-S29-02 | Bayou | CT-11 | 2026-04-23 | 15 | 0 | 1 | 0 | 13
PIB-000702 | 10 | BY-S29-02 | Bayou | CT-11 | 2026-04-23 | 8 | 1 | 0 | 1 | 8
PIB-000703 | 21 | BY-S29-02 | Bayou | CT-11 | 2026-04-23 | 20 | 1 | 0 | 0 | 17
PIB-000704 | 18 | HB-S20-05 | Harbor | CT-11 | 2026-04-23 | 17 | 0 | 0 | 1 | 16
PIB-000705 | 20 | PR-S13-03 | Prairie | CT-12 | 2026-04-23 | 20 | 0 | 0 | 0 | 19
PIB-000706 | 18 | PR-S13-03 | Prairie | CT-11 | 2026-04-23 | 16 | 0 | 1 | 1 | 16
PIB-000707 | 21 | PR-S13-03 | Prairie | CT-11 | 2026-04-23 | 19 | 0 | 0 | 2 | 17
PIB-000708 | 20 | PR-S13-03 | Prairie | CT-11 | 2026-04-23 | 19 | 0 | 0 | 1 | 17
PIB-000709 | 11 | BY-S21-05 | Bayou | CT-11 | 2026-04-24 | 8 | 0 | 1 | 2 | 8
PIB-000710 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-04-24 | 20 | 0 | 0 | 0 | 19
PIB-000711 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-04-24 | 17 | 0 | 0 | 1 | 14
PIB-000712 | 19 | BY-S21-05 | Bayou | CT-11 | 2026-04-24 | 18 | 0 | 0 | 1 | 18
PIB-000713 | 14 | BY-S29-02 | Bayou | CT-11 | 2026-04-24 | 10 | 0 | 0 | 4 | 12
PIB-000714 | 11 | HB-S20-05 | Harbor | CT-11 | 2026-04-24 | 11 | 0 | 0 | 0 | 10
PIB-000715 | 17 | PR-S13-03 | Prairie | CT-12 | 2026-04-24 | 15 | 1 | 0 | 1 | 14
PIB-000716 | 15 | PR-S13-03 | Prairie | CT-11 | 2026-04-24 | 15 | 0 | 0 | 0 | 11
PIB-000717 | 21 | BY-S21-05 | Bayou | CT-11 | 2026-04-27 | 19 | 1 | 0 | 1 | 18
PIB-000718 | 17 | BY-S21-05 | Bayou | CT-11 | 2026-04-27 | 12 | 1 | 0 | 4 | 15
PIB-000719 | 7 | BY-S29-02 | Bayou | CT-11 | 2026-04-27 | 7 | 0 | 0 | 0 | 5
PIB-000720 | 18 | BY-S29-02 | Bayou | CT-11 | 2026-04-27 | 16 | 0 | 1 | 1 | 15
PIB-000721 | 13 | BY-S29-02 | Bayou | CT-11 | 2026-04-27 | 11 | 0 | 0 | 2 | 11
PIB-000722 | 14 | BY-S29-02 | Bayou | CT-11 | 2026-04-27 | 13 | 0 | 0 | 1 | 14
PIB-000723 | 18 | HB-S20-05 | Harbor | CT-11 | 2026-04-27 | 17 | 1 | 0 | 0 | 16
PIB-000724 | 12 | PR-S13-03 | Prairie | CT-11 | 2026-04-27 | 12 | 0 | 0 | 0 | 12
PIB-000725 | 6 | PR-S13-03 | Prairie | CT-11 | 2026-04-27 | 6 | 0 | 0 | 0 | 6
PIB-000726 | 20 | BY-S21-05 | Bayou | CT-11 | 2026-04-28 | 18 | 2 | 0 | 0 | 16
PIB-000727 | 9 | BY-S21-05 | Bayou | CT-11 | 2026-04-28 | 8 | 0 | 0 | 1 | 8
PIB-000728 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-04-28 | 16 | 2 | 0 | 0 | 15
PIB-000729 | 7 | BY-S21-05 | Bayou | CT-11 | 2026-04-28 | 7 | 0 | 0 | 0 | 4
PIB-000730 | 7 | BY-S29-02 | Bayou | CT-11 | 2026-04-28 | 6 | 0 | 0 | 1 | 5
PIB-000731 | 19 | BY-S29-02 | Bayou | CT-11 | 2026-04-28 | 19 | 0 | 0 | 0 | 16
PIB-000732 | 19 | BY-S29-02 | Bayou | CT-11 | 2026-04-28 | 19 | 0 | 0 | 0 | 17
PIB-000733 | 8 | BY-S29-02 | Bayou | CT-11 | 2026-04-28 | 8 | 0 | 0 | 0 | 7
PIB-000734 | 21 | BY-S29-02 | Bayou | CT-11 | 2026-04-28 | 20 | 1 | 0 | 0 | 17
PIB-000735 | 19 | HB-S20-05 | Harbor | CT-11 | 2026-04-28 | 19 | 0 | 0 | 0 | 15
PIB-000736 | 15 | PR-S13-03 | Prairie | CT-12 | 2026-04-28 | 14 | 0 | 1 | 0 | 15
PIB-000737 | 18 | BY-S21-05 | Bayou | CT-11 | 2026-04-29 | 18 | 0 | 0 | 0 | 18
PIB-000738 | 11 | BY-S21-05 | Bayou | CT-11 | 2026-04-29 | 11 | 0 | 0 | 0 | 9
PIB-000739 | 15 | BY-S29-02 | Bayou | CT-11 | 2026-04-29 | 14 | 0 | 0 | 1 | 14
PIB-000740 | 10 | BY-S29-02 | Bayou | CT-11 | 2026-04-29 | 10 | 0 | 0 | 0 | 7
PIB-000741 | 6 | HB-S20-05 | Harbor | CT-11 | 2026-04-29 | 6 | 0 | 0 | 0 | 5
PIB-000742 | 17 | PR-S13-03 | Prairie | CT-11 | 2026-04-29 | 16 | 0 | 0 | 1 | 14
PIB-000743 | 16 | PR-S13-03 | Prairie | CT-12 | 2026-04-29 | 14 | 0 | 0 | 2 | 12
PIB-000744 | 7 | PR-S13-03 | Prairie | CT-12 | 2026-04-29 | 6 | 1 | 0 | 0 | 7
PIB-000745 | 10 | PR-S13-03 | Prairie | CT-11 | 2026-04-29 | 10 | 0 | 0 | 0 | 8
PIB-000746 | 11 | PR-S13-03 | Prairie | CT-11 | 2026-04-29 | 7 | 3 | 0 | 1 | 9
PIB-000747 | 7 | PR-S13-03 | Prairie | CT-11 | 2026-04-29 | 6 | 0 | 0 | 1 | 6
PIB-000748 | 19 | PR-S13-03 | Prairie | CT-12 | 2026-04-29 | 17 | 0 | 1 | 1 | 19
PIB-000749 | 13 | BY-S29-02 | Bayou | CT-11 | 2026-04-30 | 13 | 0 | 0 | 0 | 11
PIB-000750 | 16 | BY-S29-02 | Bayou | CT-11 | 2026-04-30 | 14 | 0 | 0 | 2 | 13
PIB-000751 | 16 | PR-S13-03 | Prairie | CT-11 | 2026-04-30 | 16 | 0 | 0 | 0 | 12
PIB-000752 | 9 | PR-S13-03 | Prairie | CT-12 | 2026-04-30 | 8 | 0 | 1 | 0 | 7
PIB-000753 | 9 | BY-S02-02 | Bayou | CT-11 | 2026-05-01 | 9 | 0 | 0 | 0 | 6
PIB-000754 | 7 | BY-S09-02 | Bayou | CT-11 | 2026-05-01 | 7 | 0 | 0 | 0 | 5
PIB-000755 | 8 | BY-S09-02 | Bayou | CT-11 | 2026-05-01 | 8 | 0 | 0 | 0 | 6
PIB-000756 | 14 | BY-S09-02 | Bayou | CT-11 | 2026-05-01 | 11 | 0 | 3 | 0 | 14
PIB-000757 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-05-01 | 18 | 0 | 0 | 0 | 16
PIB-000758 | 10 | BY-S20-02 | Bayou | CT-11 | 2026-05-01 | 9 | 0 | 0 | 1 | 7
PIB-000759 | 12 | BY-S02-02 | Bayou | CT-11 | 2026-05-04 | 11 | 1 | 0 | 0 | 12
PIB-000760 | 13 | BY-S02-02 | Bayou | CT-11 | 2026-05-04 | 13 | 0 | 0 | 0 | 10
PIB-000761 | 15 | BY-S02-02 | Bayou | CT-11 | 2026-05-04 | 14 | 0 | 0 | 1 | 12
PIB-000762 | 11 | BY-S09-02 | Bayou | CT-11 | 2026-05-04 | 10 | 0 | 0 | 1 | 9
PIB-000763 | 10 | BY-S09-02 | Bayou | CT-11 | 2026-05-04 | 9 | 0 | 1 | 0 | 10
PIB-000764 | 10 | BY-S09-02 | Bayou | CT-11 | 2026-05-04 | 10 | 0 | 0 | 0 | 8
PIB-000765 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-05-04 | 12 | 0 | 0 | 0 | 10
PIB-000766 | 20 | BY-S20-02 | Bayou | CT-11 | 2026-05-04 | 17 | 1 | 1 | 1 | 19
PIB-000767 | 7 | BY-S02-02 | Bayou | CT-11 | 2026-05-05 | 7 | 0 | 0 | 0 | 6
PIB-000768 | 19 | BY-S02-02 | Bayou | CT-11 | 2026-05-05 | 18 | 0 | 0 | 1 | 14
PIB-000769 | 18 | BY-S09-02 | Bayou | CT-11 | 2026-05-05 | 18 | 0 | 0 | 0 | 13
PIB-000770 | 17 | BY-S10-04 | Bayou | CT-11 | 2026-05-05 | 16 | 1 | 0 | 0 | 16
PIB-000771 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-05-05 | 18 | 0 | 1 | 0 | 17
PIB-000772 | 14 | BY-S09-02 | Bayou | CT-11 | 2026-05-06 | 14 | 0 | 0 | 0 | 9
PIB-000773 | 6 | BY-S02-02 | Bayou | CT-11 | 2026-05-07 | 6 | 0 | 0 | 0 | 3
PIB-000774 | 11 | BY-S02-02 | Bayou | CT-11 | 2026-05-07 | 10 | 1 | 0 | 0 | 9
PIB-000775 | 17 | BY-S02-02 | Bayou | CT-11 | 2026-05-07 | 15 | 1 | 1 | 0 | 15
PIB-000776 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-05-07 | 15 | 0 | 0 | 1 | 14
PIB-000777 | 21 | BY-S02-02 | Bayou | CT-11 | 2026-05-08 | 21 | 0 | 0 | 0 | 16
PIB-000778 | 9 | BY-S02-02 | Bayou | CT-11 | 2026-05-08 | 9 | 0 | 0 | 0 | 7
PIB-000779 | 11 | BY-S09-02 | Bayou | CT-11 | 2026-05-08 | 10 | 0 | 1 | 0 | 11
PIB-000780 | 14 | BY-S09-02 | Bayou | CT-11 | 2026-05-08 | 14 | 0 | 0 | 0 | 14
PIB-000781 | 13 | BY-S09-02 | Bayou | CT-11 | 2026-05-08 | 13 | 0 | 0 | 0 | 12
PIB-000782 | 18 | BY-S09-02 | Bayou | CT-11 | 2026-05-08 | 15 | 1 | 2 | 0 | 17
PIB-000783 | 14 | BY-S09-02 | Bayou | CT-11 | 2026-05-08 | 13 | 0 | 0 | 1 | 10
PIB-000784 | 20 | BY-S09-02 | Bayou | CT-11 | 2026-05-08 | 18 | 0 | 0 | 2 | 16
PIB-000785 | 21 | BY-S09-02 | Bayou | CT-11 | 2026-05-08 | 20 | 0 | 0 | 1 | 18
PIB-000786 | 13 | BY-S09-02 | Bayou | CT-11 | 2026-05-08 | 13 | 0 | 0 | 0 | 11
PIB-000787 | 10 | BY-S02-02 | Bayou | CT-11 | 2026-05-11 | 10 | 0 | 0 | 0 | 8
PIB-000788 | 11 | BY-S09-02 | Bayou | CT-11 | 2026-05-11 | 11 | 0 | 0 | 0 | 11
PIB-000789 | 8 | BY-S09-02 | Bayou | CT-11 | 2026-05-11 | 8 | 0 | 0 | 0 | 7
PIB-000790 | 17 | BY-S09-02 | Bayou | CT-11 | 2026-05-11 | 13 | 1 | 2 | 1 | 14
PIB-000791 | 14 | BY-S10-04 | Bayou | CT-11 | 2026-05-11 | 13 | 0 | 0 | 1 | 12
PIB-000792 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-05-11 | 8 | 0 | 0 | 0 | 8
PIB-000793 | 21 | BY-S20-02 | Bayou | CT-11 | 2026-05-11 | 20 | 1 | 0 | 0 | 20
PIB-000794 | 18 | BY-S02-02 | Bayou | CT-11 | 2026-05-12 | 18 | 0 | 0 | 0 | 15
PIB-000795 | 9 | BY-S20-02 | Bayou | CT-11 | 2026-05-12 | 9 | 0 | 0 | 0 | 6
PIB-000796 | 12 | BY-S20-02 | Bayou | CT-11 | 2026-05-12 | 10 | 1 | 1 | 0 | 9
PIB-000797 | 6 | BY-S02-02 | Bayou | CT-11 | 2026-05-13 | 6 | 0 | 0 | 0 | 6
PIB-000798 | 12 | BY-S02-02 | Bayou | CT-11 | 2026-05-13 | 11 | 0 | 0 | 1 | 11
PIB-000799 | 9 | BY-S02-02 | Bayou | CT-11 | 2026-05-13 | 9 | 0 | 0 | 0 | 8
PIB-000800 | 10 | BY-S09-02 | Bayou | CT-11 | 2026-05-13 | 10 | 0 | 0 | 0 | 8
PIB-000801 | 8 | BY-S09-02 | Bayou | CT-11 | 2026-05-13 | 8 | 0 | 0 | 0 | 6
PIB-000802 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-05-13 | 7 | 0 | 0 | 0 | 7
PIB-000803 | 18 | BY-S20-02 | Bayou | CT-11 | 2026-05-14 | 18 | 0 | 0 | 0 | 16
PIB-000804 | 11 | BY-S20-02 | Bayou | CT-11 | 2026-05-14 | 11 | 0 | 0 | 0 | 10
PIB-000805 | 10 | BY-S02-02 | Bayou | CT-11 | 2026-05-15 | 8 | 0 | 0 | 2 | 10
PIB-000806 | 16 | BY-S02-02 | Bayou | CT-11 | 2026-05-15 | 15 | 0 | 0 | 1 | 14
PIB-000807 | 6 | BY-S09-02 | Bayou | CT-11 | 2026-05-15 | 5 | 0 | 0 | 1 | 5
PIB-000808 | 21 | BY-S09-02 | Bayou | CT-11 | 2026-05-15 | 17 | 2 | 2 | 0 | 18
PIB-000809 | 6 | BY-S09-02 | Bayou | CT-11 | 2026-05-15 | 6 | 0 | 0 | 0 | 6
PIB-000810 | 10 | BY-S09-02 | Bayou | CT-11 | 2026-05-15 | 10 | 0 | 0 | 0 | 10
PIB-000811 | 17 | BY-S09-02 | Bayou | CT-11 | 2026-05-15 | 17 | 0 | 0 | 0 | 15
PIB-000812 | 14 | BY-S09-02 | Bayou | CT-11 | 2026-05-15 | 13 | 0 | 0 | 1 | 11
PIB-000813 | 12 | BY-S09-02 | Bayou | CT-11 | 2026-05-15 | 12 | 0 | 0 | 0 | 12
PIB-000814 | 16 | BY-S02-02 | Bayou | CT-11 | 2026-05-18 | 16 | 0 | 0 | 0 | 13
PIB-000815 | 12 | BY-S09-02 | Bayou | CT-11 | 2026-05-18 | 12 | 0 | 0 | 0 | 10
PIB-000816 | 7 | BY-S09-02 | Bayou | CT-11 | 2026-05-18 | 7 | 0 | 0 | 0 | 5
PIB-000817 | 13 | BY-S09-02 | Bayou | CT-11 | 2026-05-18 | 13 | 0 | 0 | 0 | 11
PIB-000818 | 17 | BY-S09-02 | Bayou | CT-11 | 2026-05-18 | 17 | 0 | 0 | 0 | 16
PIB-000819 | 6 | BY-S09-02 | Bayou | CT-11 | 2026-05-18 | 6 | 0 | 0 | 0 | 5
PIB-000820 | 6 | BY-S09-02 | Bayou | CT-11 | 2026-05-18 | 5 | 0 | 0 | 1 | 4
PIB-000821 | 11 | BY-S09-02 | Bayou | CT-11 | 2026-05-18 | 11 | 0 | 0 | 0 | 9
PIB-000822 | 21 | BY-S02-02 | Bayou | CT-11 | 2026-05-19 | 20 | 0 | 0 | 1 | 21
PIB-000823 | 21 | BY-S02-02 | Bayou | CT-11 | 2026-05-19 | 21 | 0 | 0 | 0 | 12
PIB-000824 | 17 | BY-S09-02 | Bayou | CT-11 | 2026-05-19 | 14 | 1 | 1 | 1 | 16
PIB-000825 | 10 | BY-S20-02 | Bayou | CT-11 | 2026-05-19 | 9 | 1 | 0 | 0 | 9
PIB-000826 | 21 | BY-S02-02 | Bayou | CT-11 | 2026-05-20 | 20 | 0 | 0 | 1 | 19
PIB-000827 | 9 | BY-S02-02 | Bayou | CT-11 | 2026-05-20 | 8 | 0 | 0 | 1 | 9
PIB-000828 | 12 | BY-S09-02 | Bayou | CT-11 | 2026-05-20 | 11 | 0 | 0 | 1 | 11
PIB-000829 | 10 | BY-S09-02 | Bayou | CT-11 | 2026-05-20 | 8 | 1 | 0 | 1 | 9
PIB-000830 | 16 | BY-S02-02 | Bayou | CT-11 | 2026-05-21 | 16 | 0 | 0 | 0 | 14
PIB-000831 | 16 | BY-S09-02 | Bayou | CT-11 | 2026-05-21 | 16 | 0 | 0 | 0 | 15
PIB-000832 | 6 | BY-S09-02 | Bayou | CT-11 | 2026-05-21 | 5 | 1 | 0 | 0 | 4
PIB-000833 | 6 | BY-S09-02 | Bayou | CT-11 | 2026-05-21 | 6 | 0 | 0 | 0 | 4
PIB-000834 | 17 | BY-S09-02 | Bayou | CT-11 | 2026-05-21 | 17 | 0 | 0 | 0 | 12
PIB-000835 | 20 | BY-S02-02 | Bayou | CT-11 | 2026-05-22 | 19 | 0 | 0 | 1 | 17
PIB-000836 | 11 | BY-S20-02 | Bayou | CT-11 | 2026-05-22 | 11 | 0 | 0 | 0 | 9
PIB-000837 | 19 | BY-S20-02 | Bayou | CT-11 | 2026-05-22 | 18 | 1 | 0 | 0 | 16
PIB-000838 | 19 | BY-S02-02 | Bayou | CT-11 | 2026-05-25 | 17 | 0 | 0 | 2 | 14
PIB-000839 | 15 | BY-S09-02 | Bayou | CT-11 | 2026-05-25 | 15 | 0 | 0 | 0 | 13
PIB-000840 | 17 | BY-S09-02 | Bayou | CT-11 | 2026-05-25 | 17 | 0 | 0 | 0 | 15
PIB-000841 | 21 | BY-S20-02 | Bayou | CT-11 | 2026-05-25 | 21 | 0 | 0 | 0 | 20
PIB-000842 | 10 | BY-S02-02 | Bayou | CT-11 | 2026-05-26 | 10 | 0 | 0 | 0 | 7
PIB-000843 | 16 | BY-S02-02 | Bayou | CT-11 | 2026-05-26 | 16 | 0 | 0 | 0 | 10
PIB-000844 | 8 | BY-S02-02 | Bayou | CT-11 | 2026-05-26 | 8 | 0 | 0 | 0 | 7
PIB-000845 | 7 | BY-S02-02 | Bayou | CT-11 | 2026-05-26 | 5 | 1 | 0 | 1 | 6
PIB-000846 | 19 | BY-S02-02 | Bayou | CT-11 | 2026-05-26 | 19 | 0 | 0 | 0 | 16
PIB-000847 | 9 | BY-S09-02 | Bayou | CT-11 | 2026-05-26 | 8 | 1 | 0 | 0 | 9
PIB-000848 | 8 | BY-S09-02 | Bayou | CT-11 | 2026-05-26 | 8 | 0 | 0 | 0 | 5
PIB-000849 | 14 | BY-S09-02 | Bayou | CT-11 | 2026-05-26 | 14 | 0 | 0 | 0 | 13
PIB-000850 | 6 | BY-S09-02 | Bayou | CT-11 | 2026-05-26 | 6 | 0 | 0 | 0 | 6
PIB-000851 | 19 | BY-S09-02 | Bayou | CT-11 | 2026-05-26 | 19 | 0 | 0 | 0 | 17
PIB-000852 | 12 | BY-S02-02 | Bayou | CT-11 | 2026-05-27 | 12 | 0 | 0 | 0 | 12
PIB-000853 | 13 | BY-S02-02 | Bayou | CT-11 | 2026-05-27 | 11 | 2 | 0 | 0 | 11
PIB-000854 | 20 | BY-S02-02 | Bayou | CT-11 | 2026-05-27 | 20 | 0 | 0 | 0 | 18
PIB-000855 | 19 | BY-S09-02 | Bayou | CT-11 | 2026-05-27 | 15 | 1 | 0 | 3 | 16
PIB-000856 | 7 | BY-S09-02 | Bayou | CT-11 | 2026-05-27 | 6 | 0 | 1 | 0 | 6
PIB-000857 | 10 | BY-S09-02 | Bayou | CT-11 | 2026-05-27 | 10 | 0 | 0 | 0 | 7
PIB-000858 | 18 | BY-S20-02 | Bayou | CT-11 | 2026-05-27 | 18 | 0 | 0 | 0 | 18
PIB-000859 | 14 | BY-S02-02 | Bayou | CT-11 | 2026-05-28 | 14 | 0 | 0 | 0 | 13
PIB-000860 | 14 | BY-S02-02 | Bayou | CT-11 | 2026-05-28 | 12 | 2 | 0 | 0 | 12
PIB-000861 | 21 | BY-S02-02 | Bayou | CT-11 | 2026-05-28 | 18 | 0 | 0 | 3 | 19
PIB-000862 | 15 | BY-S02-02 | Bayou | CT-11 | 2026-05-28 | 15 | 0 | 0 | 0 | 13
PIB-000863 | 17 | BY-S02-02 | Bayou | CT-11 | 2026-05-28 | 17 | 0 | 0 | 0 | 14
PIB-000864 | 21 | BY-S09-02 | Bayou | CT-11 | 2026-05-28 | 21 | 0 | 0 | 0 | 19
PIB-000865 | 12 | BY-S09-02 | Bayou | CT-11 | 2026-05-28 | 12 | 0 | 0 | 0 | 10
PIB-000866 | 6 | BY-S09-02 | Bayou | CT-11 | 2026-05-28 | 6 | 0 | 0 | 0 | 6
PIB-000867 | 10 | BY-S09-02 | Bayou | CT-11 | 2026-05-28 | 10 | 0 | 0 | 0 | 7
PIB-000868 | 13 | BY-S09-02 | Bayou | CT-11 | 2026-05-28 | 13 | 0 | 0 | 0 | 9
PIB-000869 | 8 | BY-S02-02 | Bayou | CT-11 | 2026-05-29 | 8 | 0 | 0 | 0 | 6
PIB-000870 | 11 | BY-S02-02 | Bayou | CT-11 | 2026-05-29 | 10 | 0 | 0 | 1 | 9
PIB-000871 | 21 | BY-S02-02 | Bayou | CT-11 | 2026-05-29 | 21 | 0 | 0 | 0 | 20
PIB-000872 | 4 | BY-S02-02 | Bayou | CT-11 | 2026-05-29 | 3 | 0 | 0 | 1 | 3
PIB-000873 | 10 | BY-S09-02 | Bayou | CT-11 | 2026-05-29 | 10 | 0 | 0 | 0 | 9
PIB-000874 | 15 | BY-S09-02 | Bayou | CT-11 | 2026-05-29 | 15 | 0 | 0 | 0 | 13
PIB-000875 | 15 | BY-S09-02 | Bayou | CT-11 | 2026-05-29 | 15 | 0 | 0 | 0 | 14
PIB-000876 | 17 | BY-S09-02 | Bayou | CT-11 | 2026-05-29 | 17 | 0 | 0 | 0 | 14
PIB-000877 | 16 | BY-S09-02 | Bayou | CT-11 | 2026-05-29 | 15 | 0 | 0 | 1 | 15
PIB-000878 | 16 | BY-S09-02 | Bayou | CT-11 | 2026-05-29 | 16 | 0 | 0 | 0 | 15
PIB-000879 | 18 | BY-S09-02 | Bayou | CT-11 | 2026-05-29 | 18 | 0 | 0 | 0 | 16
PIB-000880 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-05-29 | 11 | 0 | 0 | 0 | 11
PIB-000881 | 17 | BY-S10-04 | Bayou | CT-11 | 2026-06-01 | 13 | 0 | 0 | 4 | 15
PIB-000882 | 6 | BY-S10-04 | Bayou | CT-11 | 2026-06-01 | 6 | 0 | 0 | 0 | 5
PIB-000883 | 14 | BY-S10-04 | Bayou | CT-11 | 2026-06-01 | 12 | 0 | 1 | 1 | 11
PIB-000884 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-01 | 12 | 0 | 0 | 0 | 11
PIB-000885 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-01 | 16 | 0 | 0 | 0 | 10
PIB-000886 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-01 | 11 | 0 | 0 | 0 | 10
PIB-000887 | 6 | BY-S10-04 | Bayou | CT-11 | 2026-06-01 | 6 | 0 | 0 | 0 | 5
PIB-000888 | 9 | BY-S16-04 | Bayou | CT-11 | 2026-06-01 | 9 | 0 | 0 | 0 | 8
PIB-000889 | 18 | BY-S09-04 | Bayou | CT-11 | 2026-06-02 | 18 | 0 | 0 | 0 | 18
PIB-000890 | 19 | BY-S09-04 | Bayou | CT-11 | 2026-06-02 | 16 | 0 | 0 | 3 | 17
PIB-000891 | 7 | BY-S09-04 | Bayou | CT-11 | 2026-06-02 | 7 | 0 | 0 | 0 | 7
PIB-000892 | 10 | BY-S09-04 | Bayou | CT-11 | 2026-06-02 | 9 | 0 | 0 | 1 | 7
PIB-000893 | 10 | BY-S10-04 | Bayou | CT-11 | 2026-06-02 | 10 | 0 | 0 | 0 | 9
PIB-000894 | 10 | BY-S10-04 | Bayou | CT-11 | 2026-06-02 | 10 | 0 | 0 | 0 | 10
PIB-000895 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-02 | 9 | 0 | 0 | 0 | 7
PIB-000896 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-02 | 11 | 0 | 0 | 0 | 11
PIB-000897 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-02 | 14 | 0 | 1 | 1 | 15
PIB-000898 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-02 | 19 | 0 | 0 | 0 | 14
PIB-000899 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-02 | 15 | 0 | 0 | 0 | 13
PIB-000900 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-02 | 10 | 2 | 0 | 0 | 10
PIB-000901 | 11 | BY-S16-04 | Bayou | CT-11 | 2026-06-02 | 11 | 0 | 0 | 0 | 9
PIB-000902 | 16 | BY-S09-04 | Bayou | CT-11 | 2026-06-03 | 16 | 0 | 0 | 0 | 13
PIB-000903 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 17 | 0 | 0 | 1 | 13
PIB-000904 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 8 | 0 | 0 | 1 | 8
PIB-000905 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 17 | 0 | 0 | 1 | 18
PIB-000906 | 6 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 6 | 0 | 0 | 0 | 5
PIB-000907 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 6 | 0 | 0 | 1 | 7
PIB-000908 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 7 | 0 | 0 | 1 | 8
PIB-000909 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 16 | 0 | 0 | 0 | 13
PIB-000910 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 7 | 1 | 0 | 0 | 7
PIB-000911 | 13 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 13 | 0 | 0 | 0 | 10
PIB-000912 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-03 | 15 | 0 | 0 | 1 | 14
PIB-000913 | 10 | BY-S10-04 | Bayou | CT-11 | 2026-06-04 | 9 | 0 | 1 | 0 | 8
PIB-000914 | 21 | BY-S10-04 | Bayou | CT-11 | 2026-06-04 | 19 | 1 | 0 | 1 | 19
PIB-000915 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-04 | 11 | 1 | 0 | 0 | 12
PIB-000916 | 10 | BY-S16-04 | Bayou | CT-11 | 2026-06-04 | 8 | 0 | 0 | 2 | 8
PIB-000917 | 14 | BY-S09-04 | Bayou | CT-11 | 2026-06-05 | 14 | 0 | 0 | 0 | 14
PIB-000918 | 17 | BY-S09-04 | Bayou | CT-11 | 2026-06-05 | 16 | 0 | 0 | 1 | 15
PIB-000919 | 19 | BY-S09-04 | Bayou | CT-11 | 2026-06-05 | 16 | 0 | 0 | 3 | 16
PIB-000920 | 6 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 6 | 0 | 0 | 0 | 6
PIB-000921 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 17 | 1 | 0 | 0 | 15
PIB-000922 | 13 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 13 | 0 | 0 | 0 | 12
PIB-000923 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 8 | 1 | 0 | 0 | 8
PIB-000924 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 16 | 0 | 0 | 0 | 13
PIB-000925 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 19 | 0 | 0 | 0 | 16
PIB-000926 | 13 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 12 | 0 | 0 | 1 | 12
PIB-000927 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 7 | 0 | 0 | 0 | 5
PIB-000928 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-05 | 12 | 0 | 0 | 0 | 10
PIB-000929 | 7 | BY-S09-04 | Bayou | CT-11 | 2026-06-08 | 6 | 0 | 0 | 1 | 7
PIB-000930 | 15 | BY-S09-04 | Bayou | CT-11 | 2026-06-08 | 12 | 2 | 0 | 1 | 11
PIB-000931 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-08 | 14 | 1 | 1 | 0 | 14
PIB-000932 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-08 | 14 | 0 | 1 | 0 | 14
PIB-000933 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-08 | 15 | 0 | 0 | 0 | 14
PIB-000934 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-08 | 14 | 2 | 0 | 0 | 13
PIB-000935 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-08 | 10 | 1 | 0 | 0 | 11
PIB-000936 | 9 | BY-S16-04 | Bayou | CT-11 | 2026-06-08 | 9 | 0 | 0 | 0 | 7
PIB-000937 | 16 | BY-S16-04 | Bayou | CT-11 | 2026-06-08 | 13 | 0 | 1 | 2 | 11
PIB-000938 | 11 | BY-S09-04 | Bayou | CT-11 | 2026-06-09 | 10 | 1 | 0 | 0 | 9
PIB-000939 | 20 | BY-S09-04 | Bayou | CT-11 | 2026-06-09 | 19 | 0 | 0 | 1 | 16
PIB-000940 | 15 | BY-S09-04 | Bayou | CT-11 | 2026-06-09 | 14 | 1 | 0 | 0 | 12
PIB-000941 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 13 | 1 | 0 | 1 | 15
PIB-000942 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 10 | 1 | 0 | 0 | 10
PIB-000943 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 19 | 0 | 0 | 0 | 17
PIB-000944 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 19 | 0 | 0 | 0 | 15
PIB-000945 | 6 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 4 | 0 | 0 | 2 | 6
PIB-000946 | 6 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 6 | 0 | 0 | 0 | 4
PIB-000947 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 18 | 0 | 1 | 0 | 16
PIB-000948 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 14 | 0 | 0 | 1 | 14
PIB-000949 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 17 | 0 | 0 | 1 | 14
PIB-000950 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-09 | 9 | 0 | 0 | 0 | 8
PIB-000951 | 15 | BY-S16-04 | Bayou | CT-11 | 2026-06-09 | 11 | 3 | 1 | 0 | 8
PIB-000952 | 8 | BY-S16-04 | Bayou | CT-11 | 2026-06-09 | 8 | 0 | 0 | 0 | 5
PIB-000953 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-06-10 | 7 | 0 | 0 | 0 | 6
PIB-000954 | 13 | BY-S10-04 | Bayou | CT-11 | 2026-06-10 | 13 | 0 | 0 | 0 | 9
PIB-000955 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-10 | 9 | 1 | 0 | 2 | 11
PIB-000956 | 10 | BY-S10-04 | Bayou | CT-11 | 2026-06-10 | 9 | 0 | 0 | 1 | 8
PIB-000957 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-10 | 18 | 0 | 0 | 0 | 16
PIB-000958 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-10 | 9 | 0 | 0 | 0 | 9
PIB-000959 | 6 | BY-S10-04 | Bayou | CT-11 | 2026-06-10 | 6 | 0 | 0 | 0 | 4
PIB-000960 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-10 | 11 | 0 | 0 | 0 | 10
PIB-000961 | 8 | BY-S16-04 | Bayou | CT-11 | 2026-06-10 | 8 | 0 | 0 | 0 | 6
PIB-000962 | 19 | BY-S16-04 | Bayou | CT-11 | 2026-06-10 | 14 | 2 | 0 | 3 | 12
PIB-000963 | 21 | BY-S10-04 | Bayou | CT-11 | 2026-06-11 | 19 | 1 | 0 | 1 | 18
PIB-000964 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-11 | 19 | 0 | 0 | 0 | 16
PIB-000965 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-06-11 | 8 | 0 | 0 | 0 | 6
PIB-000966 | 20 | BY-S10-04 | Bayou | CT-11 | 2026-06-11 | 19 | 0 | 0 | 1 | 18
PIB-000967 | 21 | BY-S10-04 | Bayou | CT-11 | 2026-06-11 | 21 | 0 | 0 | 0 | 18
PIB-000968 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-06-11 | 7 | 1 | 0 | 0 | 5
PIB-000969 | 10 | BY-S10-04 | Bayou | CT-11 | 2026-06-11 | 10 | 0 | 0 | 0 | 10
PIB-000970 | 10 | BY-S16-04 | Bayou | CT-11 | 2026-06-11 | 10 | 0 | 0 | 0 | 6
PIB-000971 | 13 | BY-S16-04 | Bayou | CT-11 | 2026-06-11 | 10 | 0 | 0 | 3 | 6
PIB-000972 | 15 | BY-S09-04 | Bayou | CT-11 | 2026-06-12 | 15 | 0 | 0 | 0 | 14
PIB-000973 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-12 | 11 | 0 | 0 | 1 | 11
PIB-000974 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-12 | 15 | 0 | 1 | 0 | 15
PIB-000975 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-12 | 10 | 1 | 0 | 0 | 8
PIB-000976 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-12 | 11 | 0 | 0 | 0 | 9
PIB-000977 | 14 | BY-S10-04 | Bayou | CT-11 | 2026-06-12 | 13 | 0 | 0 | 1 | 11
PIB-000978 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-12 | 13 | 0 | 1 | 1 | 8
PIB-000979 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-12 | 9 | 0 | 0 | 2 | 11
PIB-000980 | 12 | BY-S16-04 | Bayou | CT-11 | 2026-06-12 | 12 | 0 | 0 | 0 | 11
PIB-000981 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-15 | 14 | 1 | 0 | 0 | 10
PIB-000982 | 20 | BY-S10-04 | Bayou | CT-11 | 2026-06-15 | 17 | 2 | 1 | 0 | 18
PIB-000983 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-06-15 | 8 | 0 | 0 | 0 | 6
PIB-000984 | 13 | BY-S16-04 | Bayou | CT-11 | 2026-06-15 | 12 | 1 | 0 | 0 | 9
PIB-000985 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-16 | 13 | 0 | 0 | 2 | 13
PIB-000986 | 21 | BY-S10-04 | Bayou | CT-11 | 2026-06-16 | 18 | 2 | 1 | 0 | 17
PIB-000987 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-16 | 15 | 0 | 0 | 1 | 16
PIB-000988 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-16 | 18 | 0 | 0 | 0 | 12
PIB-000989 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-16 | 16 | 1 | 0 | 1 | 14
PIB-000990 | 21 | BY-S10-04 | Bayou | CT-11 | 2026-06-16 | 18 | 1 | 0 | 2 | 15
PIB-000991 | 18 | BY-S09-04 | Bayou | CT-11 | 2026-06-17 | 17 | 1 | 0 | 0 | 14
PIB-000992 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-17 | 18 | 1 | 0 | 0 | 16
PIB-000993 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-17 | 16 | 0 | 0 | 2 | 18
PIB-000994 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-17 | 16 | 2 | 0 | 1 | 14
PIB-000995 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-17 | 8 | 0 | 1 | 0 | 8
PIB-000996 | 10 | BY-S16-04 | Bayou | CT-11 | 2026-06-17 | 10 | 0 | 0 | 0 | 8
PIB-000997 | 20 | BY-S09-04 | Bayou | CT-11 | 2026-06-18 | 20 | 0 | 0 | 0 | 16
PIB-000998 | 19 | BY-S09-04 | Bayou | CT-11 | 2026-06-18 | 19 | 0 | 0 | 0 | 17
PIB-000999 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 7 | 0 | 1 | 0 | 7
PIB-001000 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 15 | 0 | 0 | 0 | 11
PIB-001001 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 15 | 0 | 0 | 0 | 14
PIB-001002 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 19 | 0 | 0 | 0 | 14
PIB-001003 | 14 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 12 | 1 | 0 | 1 | 13
PIB-001004 | 21 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 19 | 2 | 0 | 0 | 20
PIB-001005 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 11 | 1 | 0 | 0 | 12
PIB-001006 | 17 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 17 | 0 | 0 | 0 | 14
PIB-001007 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 11 | 0 | 0 | 0 | 10
PIB-001008 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 16 | 0 | 0 | 0 | 14
PIB-001009 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-06-18 | 8 | 0 | 0 | 0 | 7
PIB-001010 | 19 | BY-S16-04 | Bayou | CT-11 | 2026-06-18 | 18 | 0 | 0 | 1 | 15
PIB-001011 | 15 | BY-S16-04 | Bayou | CT-11 | 2026-06-18 | 15 | 0 | 0 | 0 | 9
PIB-001012 | 16 | BY-S16-04 | Bayou | CT-11 | 2026-06-18 | 16 | 0 | 0 | 0 | 10
PIB-001013 | 13 | BY-S16-04 | Bayou | CT-11 | 2026-06-18 | 10 | 2 | 0 | 1 | 9
PIB-001014 | 12 | BY-S09-04 | Bayou | CT-11 | 2026-06-19 | 12 | 0 | 0 | 0 | 9
PIB-001015 | 15 | BY-S09-04 | Bayou | CT-11 | 2026-06-19 | 13 | 0 | 0 | 2 | 12
PIB-001016 | 10 | BY-S09-04 | Bayou | CT-11 | 2026-06-19 | 10 | 0 | 0 | 0 | 10
PIB-001017 | 20 | BY-S09-04 | Bayou | CT-11 | 2026-06-19 | 19 | 0 | 1 | 0 | 14
PIB-001018 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-19 | 16 | 0 | 0 | 0 | 14
PIB-001019 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-06-19 | 6 | 0 | 1 | 0 | 7
PIB-001020 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-19 | 15 | 0 | 0 | 1 | 14
PIB-001021 | 13 | BY-S09-04 | Bayou | CT-11 | 2026-06-22 | 12 | 0 | 1 | 0 | 12
PIB-001022 | 19 | BY-S09-04 | Bayou | CT-11 | 2026-06-22 | 18 | 0 | 0 | 1 | 17
PIB-001023 | 14 | BY-S09-04 | Bayou | CT-11 | 2026-06-22 | 12 | 1 | 0 | 1 | 11
PIB-001024 | 14 | BY-S10-04 | Bayou | CT-11 | 2026-06-22 | 12 | 1 | 0 | 1 | 13
PIB-001025 | 17 | BY-S16-04 | Bayou | CT-11 | 2026-06-22 | 17 | 0 | 0 | 0 | 13
PIB-001026 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 10 | 1 | 0 | 0 | 11
PIB-001027 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 6 | 0 | 1 | 0 | 7
PIB-001028 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 9 | 0 | 0 | 0 | 9
PIB-001029 | 17 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 14 | 1 | 0 | 2 | 16
PIB-001030 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 12 | 0 | 0 | 0 | 10
PIB-001031 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 16 | 0 | 0 | 0 | 14
PIB-001032 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 5 | 1 | 0 | 1 | 6
PIB-001033 | 18 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 17 | 0 | 0 | 1 | 15
PIB-001034 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-23 | 9 | 0 | 0 | 0 | 8
PIB-001035 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-24 | 8 | 1 | 0 | 0 | 8
PIB-001036 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-24 | 9 | 0 | 0 | 0 | 8
PIB-001037 | 11 | BY-S10-04 | Bayou | CT-11 | 2026-06-24 | 9 | 0 | 1 | 1 | 10
PIB-001038 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-06-24 | 7 | 0 | 0 | 0 | 7
PIB-001039 | 13 | BY-S10-04 | Bayou | CT-11 | 2026-06-24 | 11 | 0 | 0 | 2 | 13
PIB-001040 | 6 | BY-S16-04 | Bayou | CT-11 | 2026-06-24 | 6 | 0 | 0 | 0 | 5
PIB-001041 | 16 | BY-S16-04 | Bayou | CT-11 | 2026-06-24 | 15 | 0 | 0 | 1 | 11
PIB-001042 | 14 | BY-S16-04 | Bayou | CT-11 | 2026-06-24 | 14 | 0 | 0 | 0 | 6
PIB-001043 | 1 | BY-S09-04 | Bayou | CT-11 | 2026-06-25 | 1 | 0 | 0 | 0 | 1
PIB-001044 | 12 | BY-S09-04 | Bayou | CT-11 | 2026-06-25 | 12 | 0 | 0 | 0 | 10
PIB-001045 | 12 | BY-S09-04 | Bayou | CT-11 | 2026-06-25 | 9 | 1 | 0 | 2 | 10
PIB-001046 | 13 | BY-S10-04 | Bayou | CT-11 | 2026-06-25 | 13 | 0 | 0 | 0 | 12
PIB-001047 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-25 | 15 | 0 | 0 | 1 | 13
PIB-001048 | 10 | BY-S10-04 | Bayou | CT-11 | 2026-06-25 | 9 | 1 | 0 | 0 | 9
PIB-001049 | 10 | BY-S10-04 | Bayou | CT-11 | 2026-06-25 | 8 | 2 | 0 | 0 | 8
PIB-001050 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-25 | 11 | 0 | 0 | 1 | 10
PIB-001051 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-25 | 14 | 0 | 0 | 2 | 13
PIB-001052 | 17 | BY-S10-04 | Bayou | CT-11 | 2026-06-25 | 17 | 0 | 0 | 0 | 15
PIB-001053 | 16 | BY-S10-04 | Bayou | CT-11 | 2026-06-25 | 15 | 0 | 0 | 1 | 11
PIB-001054 | 16 | BY-S16-04 | Bayou | CT-11 | 2026-06-25 | 16 | 0 | 0 | 0 | 12
PIB-001055 | 16 | BY-S16-04 | Bayou | CT-11 | 2026-06-25 | 15 | 1 | 0 | 0 | 13
PIB-001056 | 11 | BY-S16-04 | Bayou | CT-11 | 2026-06-25 | 10 | 0 | 0 | 1 | 9
PIB-001057 | 16 | BY-S09-04 | Bayou | CT-11 | 2026-06-26 | 16 | 0 | 0 | 0 | 14
PIB-001058 | 8 | BY-S10-04 | Bayou | CT-11 | 2026-06-26 | 7 | 0 | 1 | 0 | 7
PIB-001059 | 21 | BY-S10-04 | Bayou | CT-11 | 2026-06-26 | 20 | 0 | 1 | 0 | 19
PIB-001060 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-26 | 13 | 0 | 0 | 2 | 13
PIB-001061 | 21 | BY-S10-04 | Bayou | CT-11 | 2026-06-26 | 21 | 0 | 0 | 0 | 17
PIB-001062 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-26 | 9 | 0 | 0 | 0 | 6
PIB-001063 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-29 | 12 | 0 | 0 | 0 | 11
PIB-001064 | 19 | BY-S10-04 | Bayou | CT-11 | 2026-06-29 | 18 | 0 | 0 | 1 | 16
PIB-001065 | 20 | BY-S10-04 | Bayou | CT-11 | 2026-06-29 | 17 | 0 | 1 | 2 | 17
PIB-001066 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-29 | 11 | 0 | 0 | 1 | 10
PIB-001067 | 16 | BY-S09-04 | Bayou | CT-11 | 2026-06-30 | 15 | 0 | 0 | 1 | 14
PIB-001068 | 17 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 17 | 0 | 0 | 0 | 14
PIB-001069 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 11 | 0 | 0 | 1 | 10
PIB-001070 | 15 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 14 | 0 | 0 | 1 | 11
PIB-001071 | 14 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 13 | 1 | 0 | 0 | 11
PIB-001072 | 9 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 9 | 0 | 0 | 0 | 8
PIB-001073 | 13 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 13 | 0 | 0 | 0 | 12
PIB-001074 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 12 | 0 | 0 | 0 | 11
PIB-001075 | 12 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 12 | 0 | 0 | 0 | 11
PIB-001076 | 7 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 7 | 0 | 0 | 0 | 6
PIB-001077 | 6 | BY-S10-04 | Bayou | CT-11 | 2026-06-30 | 6 | 0 | 0 | 0 | 5
PIB-001078 | 11 | BY-S16-04 | Bayou | CT-11 | 2026-06-30 | 9 | 0 | 2 | 0 | 8
PIB-001079 | 15 | BY-S22-03 | Bayou | CT-11 | 2026-07-01 | 15 | 0 | 0 | 0 | 13
PIB-001080 | 6 | PR-S01-03 | Prairie | CT-12 | 2026-07-01 | 5 | 0 | 0 | 1 | 6
PIB-001081 | 9 | PR-S01-03 | Prairie | CT-12 | 2026-07-01 | 9 | 0 | 0 | 0 | 8
PIB-001082 | 6 | PR-S01-03 | Prairie | CT-11 | 2026-07-01 | 6 | 0 | 0 | 0 | 6
PIB-001083 | 7 | PR-S01-03 | Prairie | CT-12 | 2026-07-01 | 7 | 0 | 0 | 0 | 6
PIB-001084 | 16 | BY-S22-03 | Bayou | CT-11 | 2026-07-02 | 16 | 0 | 0 | 0 | 10
PIB-001085 | 9 | BY-S22-03 | Bayou | CT-11 | 2026-07-02 | 8 | 1 | 0 | 0 | 4
PIB-001086 | 18 | BY-S22-03 | Bayou | CT-11 | 2026-07-02 | 16 | 1 | 0 | 1 | 15
PIB-001087 | 21 | PR-S01-03 | Prairie | CT-11 | 2026-07-02 | 21 | 0 | 0 | 0 | 16
PIB-001088 | 16 | PR-S01-03 | Prairie | CT-12 | 2026-07-02 | 15 | 0 | 1 | 0 | 14
PIB-001089 | 13 | PR-S01-03 | Prairie | CT-12 | 2026-07-02 | 13 | 0 | 0 | 0 | 12
PIB-001090 | 16 | PR-S01-03 | Prairie | CT-11 | 2026-07-02 | 12 | 0 | 0 | 4 | 12
PIB-001091 | 19 | PR-S01-03 | Prairie | CT-12 | 2026-07-02 | 19 | 0 | 0 | 0 | 17
PIB-001092 | 12 | PR-S01-03 | Prairie | CT-11 | 2026-07-02 | 12 | 0 | 0 | 0 | 10
PIB-001093 | 9 | BY-S16-04 | Bayou | CT-11 | 2026-07-03 | 9 | 0 | 0 | 0 | 4
PIB-001094 | 13 | BY-S16-04 | Bayou | CT-11 | 2026-07-03 | 12 | 1 | 0 | 0 | 9
PIB-001095 | 8 | BY-S16-04 | Bayou | CT-11 | 2026-07-03 | 8 | 0 | 0 | 0 | 6
PIB-001096 | 10 | BY-S16-04 | Bayou | CT-11 | 2026-07-03 | 9 | 0 | 1 | 0 | 5
PIB-001097 | 20 | BY-S22-03 | Bayou | CT-11 | 2026-07-03 | 20 | 0 | 0 | 0 | 16
PIB-001098 | 20 | BY-S22-03 | Bayou | CT-11 | 2026-07-03 | 19 | 0 | 1 | 0 | 12
PIB-001099 | 8 | PR-S01-03 | Prairie | CT-11 | 2026-07-03 | 8 | 0 | 0 | 0 | 8
PIB-001100 | 7 | PR-S01-03 | Prairie | CT-12 | 2026-07-03 | 7 | 0 | 0 | 0 | 5
PIB-001101 | 20 | PR-S01-03 | Prairie | CT-12 | 2026-07-03 | 19 | 0 | 0 | 1 | 17
PIB-001102 | 11 | PR-S01-03 | Prairie | CT-12 | 2026-07-03 | 7 | 1 | 3 | 0 | 10
PIB-001103 | 11 | PR-S01-03 | Prairie | CT-12 | 2026-07-03 | 10 | 1 | 0 | 0 | 10
PIB-001104 | 9 | PR-S01-03 | Prairie | CT-11 | 2026-07-03 | 9 | 0 | 0 | 0 | 8
PIB-001105 | 17 | PR-S01-03 | Prairie | CT-12 | 2026-07-03 | 17 | 0 | 0 | 0 | 15
PIB-001106 | 7 | BY-S16-04 | Bayou | CT-11 | 2026-07-06 | 7 | 0 | 0 | 0 | 2
PIB-001107 | 16 | BY-S16-04 | Bayou | CT-11 | 2026-07-06 | 16 | 0 | 0 | 0 | 14
PIB-001108 | 7 | PR-S01-03 | Prairie | CT-11 | 2026-07-06 | 7 | 0 | 0 | 0 | 7
PIB-001109 | 6 | PR-S01-03 | Prairie | CT-11 | 2026-07-06 | 6 | 0 | 0 | 0 | 5
PIB-001110 | 11 | PR-S01-03 | Prairie | CT-12 | 2026-07-06 | 11 | 0 | 0 | 0 | 10
PIB-001111 | 13 | PR-S01-03 | Prairie | CT-12 | 2026-07-06 | 10 | 0 | 1 | 2 | 9
PIB-001112 | 16 | PR-S01-03 | Prairie | CT-12 | 2026-07-06 | 14 | 0 | 0 | 2 | 13
PIB-001113 | 9 | PR-S01-03 | Prairie | CT-12 | 2026-07-06 | 9 | 0 | 0 | 0 | 9
PIB-001114 | 10 | PR-S01-03 | Prairie | CT-11 | 2026-07-06 | 10 | 0 | 0 | 0 | 8
PIB-001115 | 13 | BY-S11-01 | Bayou | CT-11 | 2026-07-07 | 12 | 0 | 1 | 0 | 11
PIB-001116 | 7 | BY-S16-04 | Bayou | CT-11 | 2026-07-07 | 6 | 1 | 0 | 0 | 4
PIB-001117 | 11 | BY-S16-04 | Bayou | CT-11 | 2026-07-07 | 10 | 0 | 0 | 1 | 9
PIB-001118 | 9 | BY-S22-03 | Bayou | CT-11 | 2026-07-07 | 9 | 0 | 0 | 0 | 6
PIB-001119 | 11 | BY-S22-03 | Bayou | CT-11 | 2026-07-07 | 11 | 0 | 0 | 0 | 9
PIB-001120 | 8 | PR-S01-03 | Prairie | CT-12 | 2026-07-07 | 8 | 0 | 0 | 0 | 7
PIB-001121 | 15 | PR-S01-03 | Prairie | CT-12 | 2026-07-07 | 13 | 0 | 0 | 2 | 13
PIB-001122 | 9 | BY-S16-04 | Bayou | CT-11 | 2026-07-08 | 9 | 0 | 0 | 0 | 6
PIB-001123 | 13 | BY-S16-04 | Bayou | CT-11 | 2026-07-08 | 13 | 0 | 0 | 0 | 11
PIB-001124 | 13 | BY-S16-04 | Bayou | CT-11 | 2026-07-08 | 11 | 0 | 0 | 2 | 11
PIB-001125 | 15 | BY-S22-03 | Bayou | CT-11 | 2026-07-08 | 12 | 0 | 0 | 3 | 12
PIB-001126 | 15 | BY-S22-03 | Bayou | CT-11 | 2026-07-08 | 14 | 0 | 0 | 1 | 13
PIB-001127 | 11 | BY-S22-03 | Bayou | CT-11 | 2026-07-08 | 11 | 0 | 0 | 0 | 7
PIB-001128 | 18 | PR-S01-03 | Prairie | CT-12 | 2026-07-08 | 15 | 1 | 0 | 2 | 16
PIB-001129 | 11 | PR-S01-03 | Prairie | CT-11 | 2026-07-08 | 11 | 0 | 0 | 0 | 10
PIB-001130 | 19 | PR-S01-03 | Prairie | CT-12 | 2026-07-08 | 17 | 1 | 1 | 0 | 16
PIB-001131 | 18 | PR-S01-03 | Prairie | CT-12 | 2026-07-08 | 16 | 0 | 0 | 2 | 17
PIB-001132 | 6 | PR-S01-03 | Prairie | CT-12 | 2026-07-08 | 6 | 0 | 0 | 0 | 6
PIB-001133 | 8 | PR-S01-03 | Prairie | CT-12 | 2026-07-08 | 8 | 0 | 0 | 0 | 8
PIB-001134 | 14 | BY-S16-04 | Bayou | CT-11 | 2026-07-09 | 14 | 0 | 0 | 0 | 13
PIB-001135 | 7 | BY-S22-03 | Bayou | CT-11 | 2026-07-09 | 7 | 0 | 0 | 0 | 4
PIB-001136 | 12 | BY-S22-03 | Bayou | CT-11 | 2026-07-09 | 12 | 0 | 0 | 0 | 8
PIB-001137 | 14 | BY-S22-03 | Bayou | CT-11 | 2026-07-09 | 13 | 0 | 1 | 0 | 8
PIB-001138 | 17 | PR-S01-03 | Prairie | CT-12 | 2026-07-09 | 17 | 0 | 0 | 0 | 15
PIB-001139 | 20 | PR-S01-03 | Prairie | CT-11 | 2026-07-09 | 20 | 0 | 0 | 0 | 14
PIB-001140 | 10 | PR-S01-03 | Prairie | CT-12 | 2026-07-09 | 8 | 0 | 2 | 0 | 8
PIB-001141 | 11 | PR-S01-03 | Prairie | CT-11 | 2026-07-09 | 9 | 0 | 0 | 2 | 9
PIB-001142 | 6 | BY-S11-01 | Bayou | CT-11 | 2026-07-10 | 6 | 0 | 0 | 0 | 4
PIB-001143 | 1 | BY-S11-01 | Bayou | CT-11 | 2026-07-10 | 1 | 0 | 0 | 0 | 0
PIB-001144 | 13 | BY-S22-03 | Bayou | CT-11 | 2026-07-10 | 11 | 0 | 0 | 2 | 9
PIB-001145 | 16 | BY-S22-03 | Bayou | CT-11 | 2026-07-10 | 16 | 0 | 0 | 0 | 13
PIB-001146 | 18 | PR-S01-03 | Prairie | CT-12 | 2026-07-10 | 17 | 1 | 0 | 0 | 11
PIB-001147 | 15 | PR-S01-03 | Prairie | CT-12 | 2026-07-10 | 14 | 1 | 0 | 0 | 12
PIB-001148 | 18 | PR-S01-03 | Prairie | CT-11 | 2026-07-10 | 17 | 0 | 1 | 0 | 15
PIB-001149 | 12 | PR-S01-03 | Prairie | CT-11 | 2026-07-10 | 12 | 0 | 0 | 0 | 12
PIB-001150 | 20 | PR-S01-03 | Prairie | CT-12 | 2026-07-10 | 16 | 1 | 0 | 3 | 16
PIB-001151 | 12 | BY-S11-01 | Bayou | CT-11 | 2026-07-13 | 12 | 0 | 0 | 0 | 7
PIB-001152 | 18 | BY-S16-04 | Bayou | CT-11 | 2026-07-13 | 17 | 1 | 0 | 0 | 15
PIB-001153 | 9 | PR-S01-03 | Prairie | CT-12 | 2026-07-13 | 8 | 0 | 0 | 1 | 9
PIB-001154 | 14 | PR-S01-03 | Prairie | CT-12 | 2026-07-13 | 11 | 0 | 0 | 3 | 13
PIB-001155 | 6 | PR-S01-03 | Prairie | CT-12 | 2026-07-13 | 5 | 0 | 1 | 0 | 3
PIB-001156 | 14 | PR-S01-03 | Prairie | CT-12 | 2026-07-13 | 14 | 0 | 0 | 0 | 11
PIB-001157 | 8 | PR-S01-03 | Prairie | CT-11 | 2026-07-13 | 7 | 1 | 0 | 0 | 7
PIB-001158 | 15 | PR-S01-03 | Prairie | CT-12 | 2026-07-13 | 15 | 0 | 0 | 0 | 11
PIB-001159 | 16 | BY-S22-03 | Bayou | CT-11 | 2026-07-14 | 15 | 1 | 0 | 0 | 12
PIB-001160 | 20 | PR-S01-03 | Prairie | CT-12 | 2026-07-14 | 20 | 0 | 0 | 0 | 17
PIB-001161 | 14 | PR-S01-03 | Prairie | CT-12 | 2026-07-14 | 12 | 0 | 1 | 1 | 11
PIB-001162 | 10 | PR-S01-03 | Prairie | CT-11 | 2026-07-14 | 9 | 0 | 0 | 1 | 10
PIB-001163 | 18 | BY-S11-01 | Bayou | CT-11 | 2026-07-15 | 17 | 0 | 0 | 1 | 12
PIB-001164 | 10 | BY-S22-03 | Bayou | CT-11 | 2026-07-15 | 9 | 0 | 0 | 1 | 8
PIB-001165 | 15 | PR-S01-03 | Prairie | CT-12 | 2026-07-15 | 15 | 0 | 0 | 0 | 13
PIB-001166 | 11 | PR-S01-03 | Prairie | CT-12 | 2026-07-15 | 11 | 0 | 0 | 0 | 7
PIB-001167 | 12 | PR-S01-03 | Prairie | CT-12 | 2026-07-15 | 12 | 0 | 0 | 0 | 11
PIB-001168 | 7 | PR-S01-03 | Prairie | CT-11 | 2026-07-15 | 6 | 0 | 0 | 1 | 7
PIB-001169 | 17 | BY-S16-04 | Bayou | CT-11 | 2026-07-16 | 16 | 1 | 0 | 0 | 11
PIB-001170 | 13 | BY-S16-04 | Bayou | CT-11 | 2026-07-16 | 13 | 0 | 0 | 0 | 11
PIB-001171 | 19 | BY-S22-03 | Bayou | CT-11 | 2026-07-16 | 18 | 0 | 0 | 1 | 14
PIB-001172 | 15 | BY-S22-03 | Bayou | CT-11 | 2026-07-16 | 15 | 0 | 0 | 0 | 12
PIB-001173 | 10 | PR-S01-03 | Prairie | CT-11 | 2026-07-16 | 9 | 0 | 0 | 1 | 9
PIB-001174 | 7 | PR-S01-03 | Prairie | CT-12 | 2026-07-16 | 6 | 0 | 1 | 0 | 5
PIB-001175 | 21 | PR-S01-03 | Prairie | CT-12 | 2026-07-16 | 21 | 0 | 0 | 0 | 18
PIB-001176 | 21 | PR-S01-03 | Prairie | CT-12 | 2026-07-16 | 21 | 0 | 0 | 0 | 18
PIB-001177 | 13 | BY-S11-01 | Bayou | CT-11 | 2026-07-17 | 13 | 0 | 0 | 0 | 10
PIB-001178 | 12 | BY-S16-04 | Bayou | CT-11 | 2026-07-17 | 11 | 1 | 0 | 0 | 10
PIB-001179 | 19 | BY-S16-04 | Bayou | CT-11 | 2026-07-17 | 18 | 0 | 0 | 1 | 12
PIB-001180 | 20 | BY-S16-04 | Bayou | CT-11 | 2026-07-17 | 20 | 0 | 0 | 0 | 13
PIB-001181 | 11 | BY-S16-04 | Bayou | CT-11 | 2026-07-17 | 8 | 2 | 0 | 1 | 8
PIB-001182 | 9 | BY-S22-03 | Bayou | CT-11 | 2026-07-17 | 9 | 0 | 0 | 0 | 6
PIB-001183 | 9 | BY-S22-03 | Bayou | CT-11 | 2026-07-17 | 9 | 0 | 0 | 0 | 7
PIB-001184 | 16 | BY-S22-03 | Bayou | CT-11 | 2026-07-17 | 14 | 0 | 1 | 1 | 11
PIB-001185 | 7 | BY-S22-03 | Bayou | CT-11 | 2026-07-17 | 7 | 0 | 0 | 0 | 5
PIB-001186 | 15 | BY-S22-03 | Bayou | CT-11 | 2026-07-17 | 15 | 0 | 0 | 0 | 9
PIB-001187 | 8 | PR-S01-03 | Prairie | CT-12 | 2026-07-17 | 5 | 0 | 1 | 2 | 7
PIB-001188 | 17 | PR-S01-03 | Prairie | CT-12 | 2026-07-17 | 16 | 0 | 0 | 1 | 15
PIB-001189 | 10 | PR-S01-03 | Prairie | CT-12 | 2026-07-17 | 8 | 0 | 0 | 2 | 10
PIB-001190 | 6 | PR-S01-03 | Prairie | CT-11 | 2026-07-17 | 6 | 0 | 0 | 0 | 6
PIB-001191 | 10 | PR-S01-03 | Prairie | CT-11 | 2026-07-17 | 10 | 0 | 0 | 0 | 10
PIB-001192 | 11 | PR-S01-03 | Prairie | CT-11 | 2026-07-17 | 10 | 0 | 1 | 0 | 8
PIB-001193 | 6 | PR-S01-03 | Prairie | CT-11 | 2026-07-17 | 6 | 0 | 0 | 0 | 5
PIB-001194 | 6 | PR-S01-03 | Prairie | CT-12 | 2026-07-17 | 6 | 0 | 0 | 0 | 5
PIB-001195 | 21 | BY-S16-04 | Bayou | CT-11 | 2026-07-20 | 19 | 0 | 0 | 2 | 16
PIB-001196 | 11 | BY-S22-03 | Bayou | CT-11 | 2026-07-20 | 10 | 0 | 1 | 0 | 7
PIB-001197 | 21 | PR-S01-03 | Prairie | CT-12 | 2026-07-20 | 17 | 3 | 1 | 0 | 18
PIB-001198 | 7 | PR-S01-03 | Prairie | CT-12 | 2026-07-20 | 7 | 0 | 0 | 0 | 6
PIB-001199 | 9 | PR-S01-03 | Prairie | CT-11 | 2026-07-20 | 7 | 1 | 0 | 1 | 7
PIB-001200 | 10 | PR-S01-03 | Prairie | CT-11 | 2026-07-20 | 10 | 0 | 0 | 0 | 8
PIB-001201 | 7 | BY-S11-01 | Bayou | CT-11 | 2026-07-21 | 6 | 0 | 0 | 1 | 7
PIB-001202 | 15 | BY-S16-04 | Bayou | CT-11 | 2026-07-21 | 15 | 0 | 0 | 0 | 9
PIB-001203 | 15 | BY-S16-04 | Bayou | CT-11 | 2026-07-21 | 15 | 0 | 0 | 0 | 11
PIB-001204 | 14 | BY-S22-03 | Bayou | CT-11 | 2026-07-21 | 14 | 0 | 0 | 0 | 13
PIB-001205 | 15 | BY-S22-03 | Bayou | CT-11 | 2026-07-21 | 14 | 0 | 1 | 0 | 10
PIB-001206 | 20 | PR-S01-03 | Prairie | CT-12 | 2026-07-21 | 19 | 1 | 0 | 0 | 20
PIB-001207 | 10 | PR-S01-03 | Prairie | CT-12 | 2026-07-21 | 10 | 0 | 0 | 0 | 8
PIB-001208 | 12 | PR-S01-03 | Prairie | CT-11 | 2026-07-21 | 12 | 0 | 0 | 0 | 11
PIB-001209 | 9 | PR-S01-03 | Prairie | CT-12 | 2026-07-21 | 9 | 0 | 0 | 0 | 6
PIB-001210 | 17 | PR-S01-03 | Prairie | CT-12 | 2026-07-21 | 15 | 0 | 0 | 2 | 15
PIB-001211 | 19 | PR-S01-03 | Prairie | CT-11 | 2026-07-21 | 18 | 0 | 1 | 0 | 17
PIB-001212 | 20 | PR-S01-03 | Prairie | CT-11 | 2026-07-21 | 19 | 0 | 1 | 0 | 18
PIB-001213 | 14 | PR-S01-03 | Prairie | CT-11 | 2026-07-21 | 11 | 0 | 0 | 3 | 11
PIB-001214 | 1 | PR-S01-03 | Prairie | CT-12 | 2026-07-21 | 1 | 0 | 0 | 0 | 0
PIB-001215 | 13 | BY-S16-04 | Bayou | CT-11 | 2026-07-22 | 12 | 0 | 0 | 1 | 7
PIB-001216 | 12 | BY-S16-04 | Bayou | CT-11 | 2026-07-22 | 12 | 0 | 0 | 0 | 6
PIB-001217 | 11 | BY-S16-04 | Bayou | CT-11 | 2026-07-22 | 11 | 0 | 0 | 0 | 10
PIB-001218 | 14 | BY-S22-03 | Bayou | CT-11 | 2026-07-22 | 13 | 0 | 0 | 1 | 7
PIB-001219 | 15 | BY-S22-03 | Bayou | CT-11 | 2026-07-22 | 14 | 1 | 0 | 0 | 13
PIB-001220 | 14 | PR-S01-03 | Prairie | CT-12 | 2026-07-22 | 13 | 1 | 0 | 0 | 11
PIB-001221 | 10 | PR-S01-03 | Prairie | CT-12 | 2026-07-22 | 10 | 0 | 0 | 0 | 6
PIB-001222 | 18 | PR-S01-03 | Prairie | CT-12 | 2026-07-22 | 18 | 0 | 0 | 0 | 14
PIB-001223 | 20 | PR-S01-03 | Prairie | CT-12 | 2026-07-22 | 20 | 0 | 0 | 0 | 18
PIB-001224 | 12 | PR-S01-03 | Prairie | CT-12 | 2026-07-22 | 12 | 0 | 0 | 0 | 11
PIB-001225 | 8 | PR-S01-03 | Prairie | CT-12 | 2026-07-22 | 7 | 0 | 0 | 1 | 8
PIB-001226 | 16 | PR-S01-03 | Prairie | CT-12 | 2026-07-22 | 16 | 0 | 0 | 0 | 11
PIB-001227 | 9 | BY-S16-04 | Bayou | CT-11 | 2026-07-23 | 8 | 1 | 0 | 0 | 8
PIB-001228 | 18 | BY-S22-03 | Bayou | CT-11 | 2026-07-23 | 16 | 0 | 0 | 2 | 16
PIB-001229 | 8 | BY-S22-03 | Bayou | CT-11 | 2026-07-23 | 8 | 0 | 0 | 0 | 6
PIB-001230 | 7 | BY-S22-03 | Bayou | CT-11 | 2026-07-23 | 7 | 0 | 0 | 0 | 6
PIB-001231 | 15 | PR-S01-03 | Prairie | CT-11 | 2026-07-23 | 14 | 0 | 0 | 1 | 14
PIB-001232 | 19 | PR-S01-03 | Prairie | CT-12 | 2026-07-23 | 19 | 0 | 0 | 0 | 18
PIB-001233 | 6 | PR-S01-03 | Prairie | CT-12 | 2026-07-23 | 6 | 0 | 0 | 0 | 6
PIB-001234 | 14 | PR-S01-03 | Prairie | CT-11 | 2026-07-23 | 14 | 0 | 0 | 0 | 11
PIB-001235 | 9 | PR-S01-03 | Prairie | CT-12 | 2026-07-23 | 9 | 0 | 0 | 0 | 7
PIB-001236 | 7 | PR-S01-03 | Prairie | CT-12 | 2026-07-23 | 5 | 0 | 0 | 2 | 5
PIB-001237 | 17 | PR-S01-03 | Prairie | CT-12 | 2026-07-23 | 16 | 0 | 0 | 1 | 12
PIB-001238 | 10 | BY-S16-04 | Bayou | CT-11 | 2026-07-24 | 10 | 0 | 0 | 0 | 5
PIB-001239 | 6 | BY-S16-04 | Bayou | CT-11 | 2026-07-24 | 6 | 0 | 0 | 0 | 5
PIB-001240 | 11 | BY-S22-03 | Bayou | CT-11 | 2026-07-24 | 10 | 1 | 0 | 0 | 7
PIB-001241 | 14 | BY-S22-03 | Bayou | CT-11 | 2026-07-24 | 13 | 0 | 0 | 1 | 10
PIB-001242 | 19 | PR-S01-03 | Prairie | CT-12 | 2026-07-24 | 17 | 2 | 0 | 0 | 18
PIB-001243 | 6 | PR-S01-03 | Prairie | CT-11 | 2026-07-24 | 5 | 1 | 0 | 0 | 5
PIB-001244 | 13 | PR-S01-03 | Prairie | CT-12 | 2026-07-24 | 12 | 0 | 0 | 1 | 10
PIB-001245 | 14 | BY-S16-04 | Bayou | CT-11 | 2026-07-27 | 12 | 0 | 0 | 2 | 7
PIB-001246 | 18 | PR-S01-03 | Prairie | CT-12 | 2026-07-27 | 16 | 0 | 0 | 2 | 17
PIB-001247 | 15 | PR-S01-03 | Prairie | CT-12 | 2026-07-27 | 15 | 0 | 0 | 0 | 14
PIB-001248 | 10 | PR-S01-03 | Prairie | CT-11 | 2026-07-27 | 10 | 0 | 0 | 0 | 8
PIB-001249 | 19 | PR-S01-03 | Prairie | CT-11 | 2026-07-27 | 17 | 1 | 0 | 1 | 15
PIB-001250 | 18 | PR-S01-03 | Prairie | CT-12 | 2026-07-27 | 17 | 1 | 0 | 0 | 17
PIB-001251 | 12 | PR-S01-03 | Prairie | CT-11 | 2026-07-27 | 12 | 0 | 0 | 0 | 9
PIB-001252 | 16 | PR-S01-03 | Prairie | CT-12 | 2026-07-27 | 12 | 3 | 0 | 1 | 14
PIB-001253 | 15 | PR-S01-03 | Prairie | CT-12 | 2026-07-27 | 12 | 0 | 2 | 1 | 14
PIB-001254 | 16 | PR-S01-03 | Prairie | CT-12 | 2026-07-27 | 16 | 0 | 0 | 0 | 15
PIB-001255 | 11 | PR-S01-03 | Prairie | CT-12 | 2026-07-28 | 11 | 0 | 0 | 0 | 9
PIB-001256 | 21 | BY-S16-04 | Bayou | CT-11 | 2026-07-29 | 19 | 1 | 0 | 1 | 18
PIB-001257 | 20 | BY-S22-03 | Bayou | CT-11 | 2026-07-29 | 18 | 2 | 0 | 0 | 13
PIB-001258 | 18 | BY-S22-03 | Bayou | CT-11 | 2026-07-29 | 16 | 0 | 0 | 2 | 11
PIB-001259 | 19 | PR-S01-03 | Prairie | CT-11 | 2026-07-29 | 14 | 3 | 0 | 2 | 13
PIB-001260 | 11 | PR-S01-03 | Prairie | CT-12 | 2026-07-29 | 10 | 0 | 0 | 1 | 10
PIB-001261 | 17 | PR-S01-03 | Prairie | CT-11 | 2026-07-29 | 15 | 1 | 0 | 1 | 15
PIB-001262 | 15 | PR-S01-03 | Prairie | CT-12 | 2026-07-29 | 14 | 0 | 0 | 1 | 12
PIB-001263 | 10 | BY-S16-04 | Bayou | CT-11 | 2026-07-30 | 10 | 0 | 0 | 0 | 5
PIB-001264 | 11 | BY-S16-04 | Bayou | CT-11 | 2026-07-30 | 11 | 0 | 0 | 0 | 9
PIB-001265 | 12 | BY-S22-03 | Bayou | CT-11 | 2026-07-30 | 12 | 0 | 0 | 0 | 7
PIB-001266 | 16 | BY-S22-03 | Bayou | CT-11 | 2026-07-30 | 16 | 0 | 0 | 0 | 6
PIB-001267 | 12 | PR-S01-03 | Prairie | CT-12 | 2026-07-30 | 9 | 2 | 0 | 1 | 11
PIB-001268 | 13 | PR-S01-03 | Prairie | CT-11 | 2026-07-30 | 13 | 0 | 0 | 0 | 10
PIB-001269 | 10 | PR-S01-03 | Prairie | CT-12 | 2026-07-30 | 10 | 0 | 0 | 0 | 8
PIB-001270 | 7 | PR-S01-03 | Prairie | CT-11 | 2026-07-30 | 6 | 0 | 0 | 1 | 6
PIB-001271 | 20 | PR-S01-03 | Prairie | CT-12 | 2026-07-30 | 16 | 1 | 0 | 3 | 18
PIB-001272 | 7 | PR-S01-03 | Prairie | CT-12 | 2026-07-30 | 7 | 0 | 0 | 0 | 6
PIB-001273 | 21 | BY-S22-03 | Bayou | CT-11 | 2026-07-31 | 20 | 1 | 0 | 0 | 15
PIB-001274 | 21 | PR-S01-03 | Prairie | CT-12 | 2026-07-31 | 19 | 0 | 0 | 2 | 19
PIB-001275 | 15 | PR-S01-03 | Prairie | CT-12 | 2026-07-31 | 14 | 1 | 0 | 0 | 11
PIB-001276 | 18 | BY-S23-03 | Bayou | CT-11 | 2026-08-03 | 17 | 0 | 1 | 0 | 14
PIB-001277 | 13 | BY-S29-01 | Bayou | CT-11 | 2026-08-03 | 13 | 0 | 0 | 0 | 10
PIB-001278 | 12 | BY-S29-01 | Bayou | CT-11 | 2026-08-03 | 11 | 0 | 1 | 0 | 11
PIB-001279 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-03 | 5 | 2 | 0 | 0 | 7
PIB-001280 | 11 | BY-S29-01 | Bayou | CT-11 | 2026-08-03 | 10 | 1 | 0 | 0 | 10
PIB-001281 | 15 | BY-S11-01 | Bayou | CT-11 | 2026-08-04 | 14 | 0 | 0 | 1 | 8
PIB-001282 | 6 | BY-S11-01 | Bayou | CT-11 | 2026-08-04 | 6 | 0 | 0 | 0 | 5
PIB-001283 | 7 | BY-S23-03 | Bayou | CT-11 | 2026-08-04 | 6 | 0 | 0 | 1 | 6
PIB-001284 | 6 | BY-S23-03 | Bayou | CT-11 | 2026-08-04 | 6 | 0 | 0 | 0 | 6
PIB-001285 | 14 | BY-S29-01 | Bayou | CT-11 | 2026-08-04 | 14 | 0 | 0 | 0 | 12
PIB-001286 | 18 | BY-S29-01 | Bayou | CT-11 | 2026-08-04 | 17 | 0 | 1 | 0 | 15
PIB-001287 | 13 | BY-S29-01 | Bayou | CT-11 | 2026-08-04 | 13 | 0 | 0 | 0 | 11
PIB-001288 | 9 | BY-S11-01 | Bayou | CT-11 | 2026-08-05 | 9 | 0 | 0 | 0 | 6
PIB-001289 | 6 | BY-S23-03 | Bayou | CT-11 | 2026-08-05 | 6 | 0 | 0 | 0 | 3
PIB-001290 | 17 | BY-S23-03 | Bayou | CT-11 | 2026-08-05 | 17 | 0 | 0 | 0 | 8
PIB-001291 | 12 | BY-S23-03 | Bayou | CT-11 | 2026-08-05 | 12 | 0 | 0 | 0 | 8
PIB-001292 | 13 | BY-S29-01 | Bayou | CT-11 | 2026-08-05 | 11 | 0 | 0 | 2 | 10
PIB-001293 | 6 | BY-S29-01 | Bayou | CT-11 | 2026-08-05 | 4 | 2 | 0 | 0 | 5
PIB-001294 | 20 | BY-S29-01 | Bayou | CT-11 | 2026-08-05 | 20 | 0 | 0 | 0 | 17
PIB-001295 | 16 | BY-S29-01 | Bayou | CT-11 | 2026-08-05 | 14 | 2 | 0 | 0 | 14
PIB-001296 | 6 | BY-S29-01 | Bayou | CT-11 | 2026-08-05 | 5 | 0 | 0 | 1 | 5
PIB-001297 | 9 | BY-S11-01 | Bayou | CT-11 | 2026-08-06 | 8 | 1 | 0 | 0 | 5
PIB-001298 | 10 | BY-S11-01 | Bayou | CT-11 | 2026-08-06 | 10 | 0 | 0 | 0 | 5
PIB-001299 | 14 | BY-S23-03 | Bayou | CT-11 | 2026-08-06 | 14 | 0 | 0 | 0 | 13
PIB-001300 | 13 | BY-S23-03 | Bayou | CT-11 | 2026-08-06 | 12 | 0 | 1 | 0 | 8
PIB-001301 | 15 | BY-S23-03 | Bayou | CT-11 | 2026-08-06 | 13 | 2 | 0 | 0 | 10
PIB-001302 | 7 | BY-S23-03 | Bayou | CT-11 | 2026-08-06 | 6 | 0 | 1 | 0 | 4
PIB-001303 | 11 | BY-S29-01 | Bayou | CT-11 | 2026-08-06 | 8 | 2 | 0 | 1 | 9
PIB-001304 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-06 | 20 | 0 | 0 | 1 | 19
PIB-001305 | 11 | BY-S29-01 | Bayou | CT-11 | 2026-08-06 | 11 | 0 | 0 | 0 | 9
PIB-001306 | 17 | BY-S29-01 | Bayou | CT-11 | 2026-08-06 | 16 | 0 | 0 | 1 | 16
PIB-001307 | 10 | BY-S11-01 | Bayou | CT-11 | 2026-08-07 | 10 | 0 | 0 | 0 | 7
PIB-001308 | 20 | BY-S29-01 | Bayou | CT-11 | 2026-08-07 | 19 | 1 | 0 | 0 | 13
PIB-001309 | 17 | BY-S29-01 | Bayou | CT-11 | 2026-08-07 | 17 | 0 | 0 | 0 | 13
PIB-001310 | 10 | BY-S29-01 | Bayou | CT-11 | 2026-08-07 | 10 | 0 | 0 | 0 | 10
PIB-001311 | 6 | BY-S29-01 | Bayou | CT-11 | 2026-08-07 | 5 | 0 | 1 | 0 | 6
PIB-001312 | 20 | BY-S29-01 | Bayou | CT-11 | 2026-08-07 | 18 | 2 | 0 | 0 | 14
PIB-001313 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-07 | 6 | 1 | 0 | 0 | 6
PIB-001314 | 6 | BY-S29-01 | Bayou | CT-11 | 2026-08-07 | 6 | 0 | 0 | 0 | 6
PIB-001315 | 9 | BY-S11-01 | Bayou | CT-11 | 2026-08-10 | 9 | 0 | 0 | 0 | 6
PIB-001316 | 20 | BY-S11-01 | Bayou | CT-11 | 2026-08-10 | 18 | 1 | 0 | 1 | 11
PIB-001317 | 3 | BY-S11-01 | Bayou | CT-11 | 2026-08-10 | 3 | 0 | 0 | 0 | 3
PIB-001318 | 9 | BY-S29-01 | Bayou | CT-11 | 2026-08-10 | 9 | 0 | 0 | 0 | 8
PIB-001319 | 16 | BY-S29-01 | Bayou | CT-11 | 2026-08-10 | 13 | 1 | 0 | 2 | 14
PIB-001320 | 18 | BY-S11-01 | Bayou | CT-11 | 2026-08-11 | 18 | 0 | 0 | 0 | 12
PIB-001321 | 7 | BY-S11-01 | Bayou | CT-11 | 2026-08-11 | 7 | 0 | 0 | 0 | 1
PIB-001322 | 20 | BY-S11-01 | Bayou | CT-11 | 2026-08-11 | 20 | 0 | 0 | 0 | 17
PIB-001323 | 7 | BY-S23-03 | Bayou | CT-11 | 2026-08-11 | 7 | 0 | 0 | 0 | 6
PIB-001324 | 20 | BY-S23-03 | Bayou | CT-11 | 2026-08-11 | 20 | 0 | 0 | 0 | 15
PIB-001325 | 17 | BY-S29-01 | Bayou | CT-11 | 2026-08-11 | 15 | 1 | 0 | 1 | 11
PIB-001326 | 10 | BY-S29-01 | Bayou | CT-11 | 2026-08-11 | 9 | 0 | 0 | 1 | 9
PIB-001327 | 10 | BY-S29-01 | Bayou | CT-11 | 2026-08-11 | 10 | 0 | 0 | 0 | 9
PIB-001328 | 14 | BY-S29-01 | Bayou | CT-11 | 2026-08-11 | 13 | 0 | 0 | 1 | 13
PIB-001329 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-11 | 21 | 0 | 0 | 0 | 18
PIB-001330 | 12 | BY-S11-01 | Bayou | CT-11 | 2026-08-12 | 12 | 0 | 0 | 0 | 10
PIB-001331 | 6 | BY-S11-01 | Bayou | CT-11 | 2026-08-12 | 6 | 0 | 0 | 0 | 3
PIB-001332 | 16 | BY-S11-01 | Bayou | CT-11 | 2026-08-12 | 16 | 0 | 0 | 0 | 13
PIB-001333 | 8 | BY-S23-03 | Bayou | CT-11 | 2026-08-12 | 7 | 0 | 0 | 1 | 7
PIB-001334 | 7 | BY-S23-03 | Bayou | CT-11 | 2026-08-12 | 7 | 0 | 0 | 0 | 5
PIB-001335 | 6 | BY-S23-03 | Bayou | CT-11 | 2026-08-12 | 6 | 0 | 0 | 0 | 5
PIB-001336 | 21 | BY-S23-03 | Bayou | CT-11 | 2026-08-12 | 19 | 0 | 0 | 2 | 15
PIB-001337 | 17 | BY-S23-03 | Bayou | CT-11 | 2026-08-12 | 16 | 1 | 0 | 0 | 13
PIB-001338 | 17 | BY-S29-01 | Bayou | CT-11 | 2026-08-12 | 17 | 0 | 0 | 0 | 13
PIB-001339 | 16 | BY-S29-01 | Bayou | CT-11 | 2026-08-12 | 16 | 0 | 0 | 0 | 15
PIB-001340 | 6 | BY-S29-01 | Bayou | CT-11 | 2026-08-12 | 6 | 0 | 0 | 0 | 4
PIB-001341 | 21 | BY-S11-01 | Bayou | CT-11 | 2026-08-13 | 21 | 0 | 0 | 0 | 14
PIB-001342 | 8 | BY-S11-01 | Bayou | CT-11 | 2026-08-13 | 8 | 0 | 0 | 0 | 5
PIB-001343 | 15 | BY-S23-03 | Bayou | CT-11 | 2026-08-13 | 14 | 0 | 1 | 0 | 13
PIB-001344 | 15 | BY-S23-03 | Bayou | CT-11 | 2026-08-13 | 13 | 1 | 1 | 0 | 11
PIB-001345 | 9 | BY-S23-03 | Bayou | CT-11 | 2026-08-13 | 9 | 0 | 0 | 0 | 5
PIB-001346 | 9 | BY-S23-03 | Bayou | CT-11 | 2026-08-13 | 8 | 0 | 0 | 1 | 8
PIB-001347 | 9 | BY-S29-01 | Bayou | CT-11 | 2026-08-13 | 9 | 0 | 0 | 0 | 7
PIB-001348 | 12 | BY-S29-01 | Bayou | CT-11 | 2026-08-13 | 11 | 1 | 0 | 0 | 10
PIB-001349 | 19 | BY-S29-01 | Bayou | CT-11 | 2026-08-13 | 18 | 0 | 0 | 1 | 18
PIB-001350 | 10 | BY-S11-01 | Bayou | CT-11 | 2026-08-14 | 10 | 0 | 0 | 0 | 7
PIB-001351 | 14 | BY-S11-01 | Bayou | CT-11 | 2026-08-14 | 14 | 0 | 0 | 0 | 9
PIB-001352 | 17 | BY-S11-01 | Bayou | CT-11 | 2026-08-14 | 17 | 0 | 0 | 0 | 9
PIB-001353 | 7 | BY-S11-01 | Bayou | CT-11 | 2026-08-14 | 7 | 0 | 0 | 0 | 2
PIB-001354 | 14 | BY-S11-01 | Bayou | CT-11 | 2026-08-14 | 13 | 0 | 0 | 1 | 10
PIB-001355 | 20 | BY-S23-03 | Bayou | CT-11 | 2026-08-14 | 20 | 0 | 0 | 0 | 14
PIB-001356 | 14 | BY-S23-03 | Bayou | CT-11 | 2026-08-14 | 13 | 0 | 0 | 1 | 10
PIB-001357 | 11 | BY-S23-03 | Bayou | CT-11 | 2026-08-14 | 10 | 1 | 0 | 0 | 8
PIB-001358 | 18 | BY-S29-01 | Bayou | CT-11 | 2026-08-14 | 18 | 0 | 0 | 0 | 15
PIB-001359 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-14 | 20 | 1 | 0 | 0 | 19
PIB-001360 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-14 | 18 | 0 | 0 | 3 | 21
PIB-001361 | 9 | BY-S29-01 | Bayou | CT-11 | 2026-08-14 | 7 | 1 | 0 | 1 | 8
PIB-001362 | 10 | BY-S29-01 | Bayou | CT-11 | 2026-08-14 | 10 | 0 | 0 | 0 | 10
PIB-001363 | 20 | BY-S29-01 | Bayou | CT-11 | 2026-08-14 | 17 | 0 | 1 | 2 | 14
PIB-001364 | 20 | BY-S11-01 | Bayou | CT-11 | 2026-08-17 | 18 | 1 | 1 | 0 | 13
PIB-001365 | 15 | BY-S11-01 | Bayou | CT-11 | 2026-08-17 | 15 | 0 | 0 | 0 | 11
PIB-001366 | 10 | BY-S23-03 | Bayou | CT-11 | 2026-08-17 | 10 | 0 | 0 | 0 | 7
PIB-001367 | 7 | BY-S23-03 | Bayou | CT-11 | 2026-08-17 | 7 | 0 | 0 | 0 | 5
PIB-001368 | 6 | BY-S23-03 | Bayou | CT-11 | 2026-08-17 | 6 | 0 | 0 | 0 | 5
PIB-001369 | 9 | BY-S29-01 | Bayou | CT-11 | 2026-08-17 | 9 | 0 | 0 | 0 | 7
PIB-001370 | 17 | BY-S29-01 | Bayou | CT-11 | 2026-08-17 | 15 | 0 | 0 | 2 | 15
PIB-001371 | 16 | BY-S29-01 | Bayou | CT-11 | 2026-08-17 | 15 | 1 | 0 | 0 | 10
PIB-001372 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-17 | 20 | 1 | 0 | 0 | 17
PIB-001373 | 19 | BY-S11-01 | Bayou | CT-11 | 2026-08-18 | 17 | 0 | 0 | 2 | 15
PIB-001374 | 7 | BY-S11-01 | Bayou | CT-11 | 2026-08-18 | 7 | 0 | 0 | 0 | 4
PIB-001375 | 13 | BY-S23-03 | Bayou | CT-11 | 2026-08-18 | 13 | 0 | 0 | 0 | 9
PIB-001376 | 12 | BY-S23-03 | Bayou | CT-11 | 2026-08-18 | 12 | 0 | 0 | 0 | 7
PIB-001377 | 13 | BY-S23-03 | Bayou | CT-11 | 2026-08-18 | 12 | 0 | 1 | 0 | 10
PIB-001378 | 12 | BY-S23-03 | Bayou | CT-11 | 2026-08-18 | 12 | 0 | 0 | 0 | 6
PIB-001379 | 21 | BY-S23-03 | Bayou | CT-11 | 2026-08-18 | 21 | 0 | 0 | 0 | 16
PIB-001380 | 8 | BY-S23-03 | Bayou | CT-11 | 2026-08-18 | 8 | 0 | 0 | 0 | 7
PIB-001381 | 18 | BY-S23-03 | Bayou | CT-11 | 2026-08-18 | 17 | 0 | 0 | 1 | 13
PIB-001382 | 15 | BY-S29-01 | Bayou | CT-11 | 2026-08-18 | 13 | 0 | 0 | 2 | 11
PIB-001383 | 17 | BY-S29-01 | Bayou | CT-11 | 2026-08-18 | 17 | 0 | 0 | 0 | 13
PIB-001384 | 16 | BY-S29-01 | Bayou | CT-11 | 2026-08-18 | 15 | 1 | 0 | 0 | 15
PIB-001385 | 17 | BY-S29-01 | Bayou | CT-11 | 2026-08-18 | 17 | 0 | 0 | 0 | 13
PIB-001386 | 12 | BY-S29-01 | Bayou | CT-11 | 2026-08-18 | 11 | 0 | 1 | 0 | 10
PIB-001387 | 18 | BY-S11-01 | Bayou | CT-11 | 2026-08-19 | 17 | 0 | 0 | 1 | 11
PIB-001388 | 16 | BY-S11-01 | Bayou | CT-11 | 2026-08-19 | 15 | 0 | 0 | 1 | 11
PIB-001389 | 6 | BY-S23-03 | Bayou | CT-11 | 2026-08-19 | 6 | 0 | 0 | 0 | 2
PIB-001390 | 21 | BY-S23-03 | Bayou | CT-11 | 2026-08-19 | 20 | 1 | 0 | 0 | 12
PIB-001391 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-19 | 6 | 0 | 1 | 0 | 5
PIB-001392 | 11 | BY-S29-01 | Bayou | CT-11 | 2026-08-19 | 10 | 0 | 0 | 1 | 10
PIB-001393 | 15 | BY-S23-03 | Bayou | CT-11 | 2026-08-20 | 15 | 0 | 0 | 0 | 9
PIB-001394 | 15 | BY-S23-03 | Bayou | CT-11 | 2026-08-20 | 14 | 0 | 0 | 1 | 10
PIB-001395 | 10 | BY-S29-01 | Bayou | CT-11 | 2026-08-20 | 8 | 2 | 0 | 0 | 8
PIB-001396 | 9 | BY-S29-01 | Bayou | CT-11 | 2026-08-20 | 9 | 0 | 0 | 0 | 8
PIB-001397 | 20 | BY-S29-01 | Bayou | CT-11 | 2026-08-20 | 19 | 0 | 0 | 1 | 18
PIB-001398 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-20 | 7 | 0 | 0 | 0 | 5
PIB-001399 | 7 | BY-S11-01 | Bayou | CT-11 | 2026-08-21 | 6 | 1 | 0 | 0 | 4
PIB-001400 | 20 | BY-S11-01 | Bayou | CT-11 | 2026-08-21 | 20 | 0 | 0 | 0 | 13
PIB-001401 | 9 | BY-S29-01 | Bayou | CT-11 | 2026-08-21 | 8 | 0 | 0 | 1 | 8
PIB-001402 | 11 | BY-S29-01 | Bayou | CT-11 | 2026-08-21 | 11 | 0 | 0 | 0 | 10
PIB-001403 | 18 | BY-S29-01 | Bayou | CT-11 | 2026-08-21 | 16 | 0 | 0 | 2 | 16
PIB-001404 | 12 | BY-S29-01 | Bayou | CT-11 | 2026-08-21 | 10 | 0 | 0 | 2 | 9
PIB-001405 | 10 | BY-S29-01 | Bayou | CT-11 | 2026-08-21 | 10 | 0 | 0 | 0 | 7
PIB-001406 | 14 | BY-S11-01 | Bayou | CT-11 | 2026-08-24 | 12 | 0 | 2 | 0 | 10
PIB-001407 | 11 | BY-S11-01 | Bayou | CT-11 | 2026-08-24 | 11 | 0 | 0 | 0 | 5
PIB-001408 | 15 | BY-S23-03 | Bayou | CT-11 | 2026-08-24 | 14 | 0 | 0 | 1 | 8
PIB-001409 | 8 | BY-S23-03 | Bayou | CT-11 | 2026-08-24 | 8 | 0 | 0 | 0 | 8
PIB-001410 | 11 | BY-S23-03 | Bayou | CT-11 | 2026-08-24 | 10 | 0 | 0 | 1 | 10
PIB-001411 | 14 | BY-S29-01 | Bayou | CT-11 | 2026-08-24 | 14 | 0 | 0 | 0 | 13
PIB-001412 | 8 | BY-S29-01 | Bayou | CT-11 | 2026-08-24 | 7 | 1 | 0 | 0 | 8
PIB-001413 | 12 | BY-S11-01 | Bayou | CT-11 | 2026-08-25 | 8 | 2 | 2 | 0 | 7
PIB-001414 | 15 | BY-S11-01 | Bayou | CT-11 | 2026-08-25 | 15 | 0 | 0 | 0 | 14
PIB-001415 | 13 | BY-S11-01 | Bayou | CT-11 | 2026-08-25 | 11 | 0 | 1 | 1 | 11
PIB-001416 | 17 | BY-S11-01 | Bayou | CT-11 | 2026-08-25 | 15 | 0 | 0 | 2 | 15
PIB-001417 | 10 | BY-S23-03 | Bayou | CT-11 | 2026-08-25 | 10 | 0 | 0 | 0 | 5
PIB-001418 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-25 | 7 | 0 | 0 | 0 | 6
PIB-001419 | 8 | BY-S29-01 | Bayou | CT-11 | 2026-08-25 | 8 | 0 | 0 | 0 | 6
PIB-001420 | 10 | BY-S29-01 | Bayou | CT-11 | 2026-08-25 | 10 | 0 | 0 | 0 | 9
PIB-001421 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-25 | 6 | 1 | 0 | 0 | 7
PIB-001422 | 8 | BY-S11-01 | Bayou | CT-11 | 2026-08-26 | 8 | 0 | 0 | 0 | 7
PIB-001423 | 9 | BY-S11-01 | Bayou | CT-11 | 2026-08-26 | 8 | 0 | 0 | 1 | 5
PIB-001424 | 8 | BY-S11-01 | Bayou | CT-11 | 2026-08-26 | 8 | 0 | 0 | 0 | 7
PIB-001425 | 16 | BY-S11-01 | Bayou | CT-11 | 2026-08-26 | 16 | 0 | 0 | 0 | 14
PIB-001426 | 8 | BY-S11-01 | Bayou | CT-11 | 2026-08-26 | 8 | 0 | 0 | 0 | 4
PIB-001427 | 21 | BY-S11-01 | Bayou | CT-11 | 2026-08-26 | 21 | 0 | 0 | 0 | 16
PIB-001428 | 19 | BY-S11-01 | Bayou | CT-11 | 2026-08-26 | 19 | 0 | 0 | 0 | 14
PIB-001429 | 20 | BY-S11-01 | Bayou | CT-11 | 2026-08-26 | 19 | 1 | 0 | 0 | 16
PIB-001430 | 18 | BY-S23-03 | Bayou | CT-11 | 2026-08-26 | 18 | 0 | 0 | 0 | 16
PIB-001431 | 6 | BY-S29-01 | Bayou | CT-11 | 2026-08-26 | 6 | 0 | 0 | 0 | 6
PIB-001432 | 12 | BY-S29-01 | Bayou | CT-11 | 2026-08-26 | 10 | 0 | 0 | 2 | 9
PIB-001433 | 11 | BY-S29-01 | Bayou | CT-11 | 2026-08-26 | 10 | 1 | 0 | 0 | 9
PIB-001434 | 8 | BY-S29-01 | Bayou | CT-11 | 2026-08-26 | 8 | 0 | 0 | 0 | 6
PIB-001435 | 14 | BY-S29-01 | Bayou | CT-11 | 2026-08-26 | 13 | 0 | 0 | 1 | 14
PIB-001436 | 15 | BY-S29-01 | Bayou | CT-11 | 2026-08-26 | 13 | 0 | 2 | 0 | 11
PIB-001437 | 19 | BY-S29-01 | Bayou | CT-11 | 2026-08-26 | 18 | 1 | 0 | 0 | 17
PIB-001438 | 14 | BY-S29-01 | Bayou | CT-11 | 2026-08-26 | 13 | 0 | 0 | 1 | 12
PIB-001439 | 9 | BY-S11-01 | Bayou | CT-11 | 2026-08-27 | 8 | 1 | 0 | 0 | 6
PIB-001440 | 17 | BY-S11-01 | Bayou | CT-11 | 2026-08-27 | 17 | 0 | 0 | 0 | 12
PIB-001441 | 19 | BY-S11-01 | Bayou | CT-11 | 2026-08-27 | 18 | 1 | 0 | 0 | 8
PIB-001442 | 13 | BY-S11-01 | Bayou | CT-11 | 2026-08-27 | 13 | 0 | 0 | 0 | 10
PIB-001443 | 17 | BY-S23-03 | Bayou | CT-11 | 2026-08-27 | 14 | 0 | 0 | 3 | 12
PIB-001444 | 18 | BY-S29-01 | Bayou | CT-11 | 2026-08-27 | 18 | 0 | 0 | 0 | 18
PIB-001445 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-27 | 21 | 0 | 0 | 0 | 18
PIB-001446 | 18 | BY-S29-01 | Bayou | CT-11 | 2026-08-27 | 16 | 2 | 0 | 0 | 14
PIB-001447 | 9 | BY-S29-01 | Bayou | CT-11 | 2026-08-27 | 7 | 0 | 0 | 2 | 8
PIB-001448 | 21 | BY-S11-01 | Bayou | CT-11 | 2026-08-28 | 20 | 0 | 0 | 1 | 12
PIB-001449 | 9 | BY-S11-01 | Bayou | CT-11 | 2026-08-28 | 9 | 0 | 0 | 0 | 8
PIB-001450 | 16 | BY-S11-01 | Bayou | CT-11 | 2026-08-28 | 15 | 0 | 1 | 0 | 12
PIB-001451 | 10 | BY-S23-03 | Bayou | CT-11 | 2026-08-28 | 10 | 0 | 0 | 0 | 9
PIB-001452 | 15 | BY-S23-03 | Bayou | CT-11 | 2026-08-28 | 15 | 0 | 0 | 0 | 11
PIB-001453 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 7 | 0 | 0 | 0 | 6
PIB-001454 | 16 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 16 | 0 | 0 | 0 | 14
PIB-001455 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 20 | 1 | 0 | 0 | 14
PIB-001456 | 20 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 17 | 0 | 2 | 1 | 19
PIB-001457 | 15 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 14 | 1 | 0 | 0 | 12
PIB-001458 | 19 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 18 | 1 | 0 | 0 | 17
PIB-001459 | 9 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 9 | 0 | 0 | 0 | 9
PIB-001460 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 21 | 0 | 0 | 0 | 16
PIB-001461 | 19 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 17 | 1 | 0 | 1 | 18
PIB-001462 | 14 | BY-S29-01 | Bayou | CT-11 | 2026-08-28 | 13 | 1 | 0 | 0 | 12
PIB-001463 | 9 | BY-S11-01 | Bayou | CT-11 | 2026-08-31 | 9 | 0 | 0 | 0 | 7
PIB-001464 | 8 | BY-S23-03 | Bayou | CT-11 | 2026-08-31 | 8 | 0 | 0 | 0 | 7
PIB-001465 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-31 | 6 | 0 | 0 | 1 | 6
PIB-001466 | 11 | BY-S29-01 | Bayou | CT-11 | 2026-08-31 | 11 | 0 | 0 | 0 | 8
PIB-001467 | 21 | BY-S29-01 | Bayou | CT-11 | 2026-08-31 | 19 | 1 | 0 | 1 | 18
PIB-001468 | 20 | BY-S29-01 | Bayou | CT-11 | 2026-08-31 | 16 | 2 | 0 | 2 | 16
PIB-001469 | 7 | BY-S29-01 | Bayou | CT-11 | 2026-08-31 | 7 | 0 | 0 | 0 | 6